## Informations
MAKE SURE THAT ALL THE INFORMATION YOU SHARE CAN BE SHARED PUBLICLY
Please fill the PV_plant_setup file, the cases in yellow must be filled to have the code running.
If possible please fill additional informations to the plant set-up and/or refer to a relevant documentation
The measured powered time series contains three columns:
--> one with the raw measured PV data aggregated on the hourly level (faculative, for documentation purposes)
--> one with the normalized PV data: all values must be between 0 and 1 (facultative, for documentation purposes)
--> one normalized corrected file where missing values are replaced (must be filled to have the code running)
If possible, please explain how this has been done in the "PV plant set-up informations" in this file.
More columns can be added but the column name "Normalized PV power corrected" or "Time" should not be changed

## PV_plant_setup
Parameter | Value | Note
Location | Turin
Latitude | 45.065
Longitude | 7.659
Tilt | 26
Azimuth | 206 | 180° is south facing
System loss | 10
Building/free | building | See sheet "Options" for more informations
PV technology | crystSi | See sheet "Options" for more informations
Start year | 2019
End year | 2020
Fixed | 1
Bifacial panel | No
Measurement resolution (should be below 1min) | 1 min
Installed peak capacity (kWp)
Inverter nominal capacity (kW), inlet/outlet
Inverter model (facultative info)
Module manufacturer (facultative info)
Module model (facultative info)
Tracking | 0
Max capacity simulation | 1 | Value should be 1 to use normalized measured data
Additional informations regarding the plant set-up:
General informations
The experimental PV plant consists in photovoltaic panels installed with a fixed support that is coplanar with a rooftop of the university Politecnico di Torino in Turin, Italy. The plant has been installed in 2018 and data are recorded between 1st January 2019 and 31st December 2020.
Climate site description (check https://koppen.earth/ )
The climate in both Turin can be described as humid subtropical climate (Cfa) characterized by hot and humid summers, and cool and damp winters. Locations with the same climates classification can be observed for example in the Australian East-coast (Queensland), American gulf and lower East-coast states in the US, or in Southern Brazil, north Argentina and Uruguay.
Detailed description of the PV plant set-up
The plant has an inclination angle (tilt) of 26° as the rooftop and an azimuth of 206° (South-West exposed). The solar panels installed are Monocrystalline Benq (SunForte PM096B00) with an efficiency of 20.1% at STC. There are 27 inverters Sunny Tripower between 20 and 25 kW (20000TL / 25000TL) with an efficiency of 98%. The power of each module is 327 W, the overall installed power is 604 kW, with a net occupy area of 3,000 m2. The data analyzed consists of energy produced by the photovoltaic panels and recorded on the AC side of the inverters with 1 minute time-step in kWh per minute measured between 2019 and 2020. The capacity factor is therefore calculated by dividing the energy produced every minute by the installed power capacity and multiplying by 60 min/hour. The hourly capacity factor is calculated summing the energy produced every minute and dividing by the installed power capacity. The system losses are 10%.
Measurement errors and missing values
No data is missing in 2019. There was a case of a capacity factor exceeding 1 and preceded by zeros, indicating that this value represents energy produced in previous hours but not recorded. In such cases, the value exceeding 1 has been redistributed proportionally to the previous hours, using Renewables.ninja MERRA2 as a reference.

## Options description
| PVGIS name | Meaning
PV technology | crystSi | Crystalline silicon PV panels mono and polycrystalline
PV technology | CIS | Copper Indium Gallium Selenide (CIGS) or CIS thin-film solar panels
PV technology | CdTe | Cadmium Telluride thin-film solar panels
PV technology | Unknown | Unknown
Building integration | building | PV panels integrated in the rooftop
Building integration | free | PV panels free standing on the ground
Fixed / Tracking | 1 | PV panels fixed
Fixed / Tracking | 0 | PV panles with tracking system

## Turin2020
Time | Hour of the year | Raw PV power measurements (facultative) | Normalized PV power [0-1] (faculative) | Normalized PV power corrected
2020-01-01 | 1 |  |  | 0
2020-01-01 01:00 | 2 |  |  | 0
2020-01-01 02:00 | 3 |  |  | 0
2020-01-01 03:00 | 4 |  |  | 0
2020-01-01 04:00 | 5 |  |  | 0
2020-01-01 05:00 | 6 |  |  | 0
2020-01-01 06:00 | 7 |  |  | 0
2020-01-01 07:00 | 8 |  |  | 0
2020-01-01 08:00 | 9 |  |  | 0.014886
2020-01-01 09:00 | 10 |  |  | 0.1654
2020-01-01 10:00 | 11 |  |  | 0.32418
2020-01-01 11:00 | 12 |  |  | 0.39696
2020-01-01 12:00 | 13 |  |  | 0.42177
2020-01-01 13:00 | 14 |  |  | 0.42177
2020-01-01 14:00 | 15 |  |  | 0.29937
2020-01-01 15:00 | 16 |  |  | 0.14886
2020-01-01 16:00 | 17 |  |  | 0.013232
2020-01-01 17:00 | 18 |  |  | 0
2020-01-01 18:00 | 19 |  |  | 0
2020-01-01 19:00 | 20 |  |  | 0
2020-01-01 20:00 | 21 |  |  | 0
2020-01-01 21:00 | 22 |  |  | 0
2020-01-01 22:00 | 23 |  |  | 0
2020-01-01 23:00 | 24 |  |  | 0
2020-01-02 | 25 |  |  | 0
2020-01-02 01:00 | 26 |  |  | 0
2020-01-02 02:00 | 27 |  |  | 0
2020-01-02 03:00 | 28 |  |  | 0
2020-01-02 04:00 | 29 |  |  | 0
2020-01-02 05:00 | 30 |  |  | 0
2020-01-02 06:00 | 31 |  |  | 0
2020-01-02 07:00 | 32 |  |  | 0
2020-01-02 08:00 | 33 |  |  | 0.0082699
2020-01-02 09:00 | 34 |  |  | 0.15382
2020-01-02 10:00 | 35 |  |  | 0.30599
2020-01-02 11:00 | 36 |  |  | 0.4135
2020-01-02 12:00 | 37 |  |  | 0.42177
2020-01-02 13:00 | 38 |  |  | 0.41184
2020-01-02 14:00 | 39 |  |  | 0.29772
2020-01-02 15:00 | 40 |  |  | 0.15051
2020-01-02 16:00 | 41 |  |  | 0.013232
2020-01-02 17:00 | 42 |  |  | 0
2020-01-02 18:00 | 43 |  |  | 0
2020-01-02 19:00 | 44 |  |  | 0
2020-01-02 20:00 | 45 |  |  | 0
2020-01-02 21:00 | 46 |  |  | 0
2020-01-02 22:00 | 47 |  |  | 0
2020-01-02 23:00 | 48 |  |  | 0
2020-01-03 | 49 |  |  | 0
2020-01-03 01:00 | 50 |  |  | 0
2020-01-03 02:00 | 51 |  |  | 0
2020-01-03 03:00 | 52 |  |  | 0
2020-01-03 04:00 | 53 |  |  | 0
2020-01-03 05:00 | 54 |  |  | 0
2020-01-03 06:00 | 55 |  |  | 0
2020-01-03 07:00 | 56 |  |  | 0
2020-01-03 08:00 | 57 |  |  | 0
2020-01-03 09:00 | 58 |  |  | 0.0099239
2020-01-03 10:00 | 59 |  |  | 0.079391
2020-01-03 11:00 | 60 |  |  | 0.16374
2020-01-03 12:00 | 61 |  |  | 0.14555
2020-01-03 13:00 | 62 |  |  | 0.13397
2020-01-03 14:00 | 63 |  |  | 0.081045
2020-01-03 15:00 | 64 |  |  | 0.043004
2020-01-03 16:00 | 65 |  |  | 0.013232
2020-01-03 17:00 | 66 |  |  | 0
2020-01-03 18:00 | 67 |  |  | 0
2020-01-03 19:00 | 68 |  |  | 0
2020-01-03 20:00 | 69 |  |  | 0
2020-01-03 21:00 | 70 |  |  | 0
2020-01-03 22:00 | 71 |  |  | 0
2020-01-03 23:00 | 72 |  |  | 0
2020-01-04 | 73 |  |  | 0
2020-01-04 01:00 | 74 |  |  | 0
2020-01-04 02:00 | 75 |  |  | 0
2020-01-04 03:00 | 76 |  |  | 0
2020-01-04 04:00 | 77 |  |  | 0
2020-01-04 05:00 | 78 |  |  | 0
2020-01-04 06:00 | 79 |  |  | 0
2020-01-04 07:00 | 80 |  |  | 0
2020-01-04 08:00 | 81 |  |  | 0.021502
2020-01-04 09:00 | 82 |  |  | 0.19517
2020-01-04 10:00 | 83 |  |  | 0.31426
2020-01-04 11:00 | 84 |  |  | 0.39861
2020-01-04 12:00 | 85 |  |  | 0.42673
2020-01-04 13:00 | 86 |  |  | 0.42011
2020-01-04 14:00 | 87 |  |  | 0.30764
2020-01-04 15:00 | 88 |  |  | 0.15878
2020-01-04 16:00 | 89 |  |  | 0.02481
2020-01-04 17:00 | 90 |  |  | 0
2020-01-04 18:00 | 91 |  |  | 0
2020-01-04 19:00 | 92 |  |  | 0
2020-01-04 20:00 | 93 |  |  | 0
2020-01-04 21:00 | 94 |  |  | 0
2020-01-04 22:00 | 95 |  |  | 0
2020-01-04 23:00 | 96 |  |  | 0
2020-01-05 | 97 |  |  | 0
2020-01-05 01:00 | 98 |  |  | 0
2020-01-05 02:00 | 99 |  |  | 0
2020-01-05 03:00 | 100 |  |  | 0
2020-01-05 04:00 | 101 |  |  | 0
2020-01-05 05:00 | 102 |  |  | 0
2020-01-05 06:00 | 103 |  |  | 0
2020-01-05 07:00 | 104 |  |  | 0
2020-01-05 08:00 | 105 |  |  | 0.018194
2020-01-05 09:00 | 106 |  |  | 0.18028
2020-01-05 10:00 | 107 |  |  | 0.34899
2020-01-05 11:00 | 108 |  |  | 0.42673
2020-01-05 12:00 | 109 |  |  | 0.42673
2020-01-05 13:00 | 110 |  |  | 0.42011
2020-01-05 14:00 | 111 |  |  | 0.31095
2020-01-05 15:00 | 112 |  |  | 0.16705
2020-01-05 16:00 | 113 |  |  | 0.01654
2020-01-05 17:00 | 114 |  |  | 0
2020-01-05 18:00 | 115 |  |  | 0
2020-01-05 19:00 | 116 |  |  | 0
2020-01-05 20:00 | 117 |  |  | 0
2020-01-05 21:00 | 118 |  |  | 0
2020-01-05 22:00 | 119 |  |  | 0
2020-01-05 23:00 | 120 |  |  | 0
2020-01-06 | 121 |  |  | 0
2020-01-06 01:00 | 122 |  |  | 0
2020-01-06 02:00 | 123 |  |  | 0
2020-01-06 03:00 | 124 |  |  | 0
2020-01-06 04:00 | 125 |  |  | 0
2020-01-06 05:00 | 126 |  |  | 0
2020-01-06 06:00 | 127 |  |  | 0
2020-01-06 07:00 | 128 |  |  | 0
2020-01-06 08:00 | 129 |  |  | 0.0082699
2020-01-06 09:00 | 130 |  |  | 0.11743
2020-01-06 10:00 | 131 |  |  | 0.28449
2020-01-06 11:00 | 132 |  |  | 0.39199
2020-01-06 12:00 | 133 |  |  | 0.42177
2020-01-06 13:00 | 134 |  |  | 0.40357
2020-01-06 14:00 | 135 |  |  | 0.28118
2020-01-06 15:00 | 136 |  |  | 0.13893
2020-01-06 16:00 | 137 |  |  | 0.01654
2020-01-06 17:00 | 138 |  |  | 0
2020-01-06 18:00 | 139 |  |  | 0
2020-01-06 19:00 | 140 |  |  | 0
2020-01-06 20:00 | 141 |  |  | 0
2020-01-06 21:00 | 142 |  |  | 0
2020-01-06 22:00 | 143 |  |  | 0
2020-01-06 23:00 | 144 |  |  | 0
2020-01-07 | 145 |  |  | 0
2020-01-07 01:00 | 146 |  |  | 0
2020-01-07 02:00 | 147 |  |  | 0
2020-01-07 03:00 | 148 |  |  | 0
2020-01-07 04:00 | 149 |  |  | 0
2020-01-07 05:00 | 150 |  |  | 0
2020-01-07 06:00 | 151 |  |  | 0
2020-01-07 07:00 | 152 |  |  | 0
2020-01-07 08:00 | 153 |  |  | 0
2020-01-07 09:00 | 154 |  |  | 0.023156
2020-01-07 10:00 | 155 |  |  | 0.16374
2020-01-07 11:00 | 156 |  |  | 0.36718
2020-01-07 12:00 | 157 |  |  | 0.42673
2020-01-07 13:00 | 158 |  |  | 0.41019
2020-01-07 14:00 | 159 |  |  | 0.28945
2020-01-07 15:00 | 160 |  |  | 0.15382
2020-01-07 16:00 | 161 |  |  | 0.011578
2020-01-07 17:00 | 162 |  |  | 0
2020-01-07 18:00 | 163 |  |  | 0
2020-01-07 19:00 | 164 |  |  | 0
2020-01-07 20:00 | 165 |  |  | 0
2020-01-07 21:00 | 166 |  |  | 0
2020-01-07 22:00 | 167 |  |  | 0
2020-01-07 23:00 | 168 |  |  | 0
2020-01-08 | 169 |  |  | 0
2020-01-08 01:00 | 170 |  |  | 0
2020-01-08 02:00 | 171 |  |  | 0
2020-01-08 03:00 | 172 |  |  | 0
2020-01-08 04:00 | 173 |  |  | 0
2020-01-08 05:00 | 174 |  |  | 0
2020-01-08 06:00 | 175 |  |  | 0
2020-01-08 07:00 | 176 |  |  | 0
2020-01-08 08:00 | 177 |  |  | 0
2020-01-08 09:00 | 178 |  |  | 0.10255
2020-01-08 10:00 | 179 |  |  | 0.32914
2020-01-08 11:00 | 180 |  |  | 0.42507
2020-01-08 12:00 | 181 |  |  | 0.42673
2020-01-08 13:00 | 182 |  |  | 0.39696
2020-01-08 14:00 | 183 |  |  | 0.28779
2020-01-08 15:00 | 184 |  |  | 0.14059
2020-01-08 16:00 | 185 |  |  | 0.021502
2020-01-08 17:00 | 186 |  |  | 0
2020-01-08 18:00 | 187 |  |  | 0
2020-01-08 19:00 | 188 |  |  | 0
2020-01-08 20:00 | 189 |  |  | 0
2020-01-08 21:00 | 190 |  |  | 0
2020-01-08 22:00 | 191 |  |  | 0
2020-01-08 23:00 | 192 |  |  | 0
2020-01-09 | 193 |  |  | 0
2020-01-09 01:00 | 194 |  |  | 0
2020-01-09 02:00 | 195 |  |  | 0
2020-01-09 03:00 | 196 |  |  | 0
2020-01-09 04:00 | 197 |  |  | 0
2020-01-09 05:00 | 198 |  |  | 0
2020-01-09 06:00 | 199 |  |  | 0
2020-01-09 07:00 | 200 |  |  | 0
2020-01-09 08:00 | 201 |  |  | 0.014886
2020-01-09 09:00 | 202 |  |  | 0.17201
2020-01-09 10:00 | 203 |  |  | 0.3126
2020-01-09 11:00 | 204 |  |  | 0.42507
2020-01-09 12:00 | 205 |  |  | 0.42673
2020-01-09 13:00 | 206 |  |  | 0.41846
2020-01-09 14:00 | 207 |  |  | 0.3126
2020-01-09 15:00 | 208 |  |  | 0.17201
2020-01-09 16:00 | 209 |  |  | 0.021502
2020-01-09 17:00 | 210 |  |  | 0
2020-01-09 18:00 | 211 |  |  | 0
2020-01-09 19:00 | 212 |  |  | 0
2020-01-09 20:00 | 213 |  |  | 0
2020-01-09 21:00 | 214 |  |  | 0
2020-01-09 22:00 | 215 |  |  | 0
2020-01-09 23:00 | 216 |  |  | 0
2020-01-10 | 217 |  |  | 0
2020-01-10 01:00 | 218 |  |  | 0
2020-01-10 02:00 | 219 |  |  | 0
2020-01-10 03:00 | 220 |  |  | 0
2020-01-10 04:00 | 221 |  |  | 0
2020-01-10 05:00 | 222 |  |  | 0
2020-01-10 06:00 | 223 |  |  | 0
2020-01-10 07:00 | 224 |  |  | 0
2020-01-10 08:00 | 225 |  |  | 0.0082699
2020-01-10 09:00 | 226 |  |  | 0.074429
2020-01-10 10:00 | 227 |  |  | 0.22163
2020-01-10 11:00 | 228 |  |  | 0.23652
2020-01-10 12:00 | 229 |  |  | 0.27125
2020-01-10 13:00 | 230 |  |  | 0.44161
2020-01-10 14:00 | 231 |  |  | 0.30599
2020-01-10 15:00 | 232 |  |  | 0.16871
2020-01-10 16:00 | 233 |  |  | 0.014886
2020-01-10 17:00 | 234 |  |  | 0
2020-01-10 18:00 | 235 |  |  | 0
2020-01-10 19:00 | 236 |  |  | 0
2020-01-10 20:00 | 237 |  |  | 0
2020-01-10 21:00 | 238 |  |  | 0
2020-01-10 22:00 | 239 |  |  | 0
2020-01-10 23:00 | 240 |  |  | 0
2020-01-11 | 241 |  |  | 0
2020-01-11 01:00 | 242 |  |  | 0
2020-01-11 02:00 | 243 |  |  | 0
2020-01-11 03:00 | 244 |  |  | 0
2020-01-11 04:00 | 245 |  |  | 0
2020-01-11 05:00 | 246 |  |  | 0
2020-01-11 06:00 | 247 |  |  | 0
2020-01-11 07:00 | 248 |  |  | 0
2020-01-11 08:00 | 249 |  |  | 0.018194
2020-01-11 09:00 | 250 |  |  | 0.18028
2020-01-11 10:00 | 251 |  |  | 0.35395
2020-01-11 11:00 | 252 |  |  | 0.44492
2020-01-11 12:00 | 253 |  |  | 0.44823
2020-01-11 13:00 | 254 |  |  | 0.42673
2020-01-11 14:00 | 255 |  |  | 0.33741
2020-01-11 15:00 | 256 |  |  | 0.19352
2020-01-11 16:00 | 257 |  |  | 0.031426
2020-01-11 17:00 | 258 |  |  | 0
2020-01-11 18:00 | 259 |  |  | 0
2020-01-11 19:00 | 260 |  |  | 0
2020-01-11 20:00 | 261 |  |  | 0
2020-01-11 21:00 | 262 |  |  | 0
2020-01-11 22:00 | 263 |  |  | 0
2020-01-11 23:00 | 264 |  |  | 0
2020-01-12 | 265 |  |  | 0
2020-01-12 01:00 | 266 |  |  | 0
2020-01-12 02:00 | 267 |  |  | 0
2020-01-12 03:00 | 268 |  |  | 0
2020-01-12 04:00 | 269 |  |  | 0
2020-01-12 05:00 | 270 |  |  | 0
2020-01-12 06:00 | 271 |  |  | 0
2020-01-12 07:00 | 272 |  |  | 0
2020-01-12 08:00 | 273 |  |  | 0.023156
2020-01-12 09:00 | 274 |  |  | 0.1869
2020-01-12 10:00 | 275 |  |  | 0.35395
2020-01-12 11:00 | 276 |  |  | 0.44988
2020-01-12 12:00 | 277 |  |  | 0.46973
2020-01-12 13:00 | 278 |  |  | 0.43831
2020-01-12 14:00 | 279 |  |  | 0.32584
2020-01-12 15:00 | 280 |  |  | 0.19352
2020-01-12 16:00 | 281 |  |  | 0.03308
2020-01-12 17:00 | 282 |  |  | 0
2020-01-12 18:00 | 283 |  |  | 0
2020-01-12 19:00 | 284 |  |  | 0
2020-01-12 20:00 | 285 |  |  | 0
2020-01-12 21:00 | 286 |  |  | 0
2020-01-12 22:00 | 287 |  |  | 0
2020-01-12 23:00 | 288 |  |  | 0
2020-01-13 | 289 |  |  | 0
2020-01-13 01:00 | 290 |  |  | 0
2020-01-13 02:00 | 291 |  |  | 0
2020-01-13 03:00 | 292 |  |  | 0
2020-01-13 04:00 | 293 |  |  | 0
2020-01-13 05:00 | 294 |  |  | 0
2020-01-13 06:00 | 295 |  |  | 0
2020-01-13 07:00 | 296 |  |  | 0
2020-01-13 08:00 | 297 |  |  | 0.014886
2020-01-13 09:00 | 298 |  |  | 0.13728
2020-01-13 10:00 | 299 |  |  | 0.27787
2020-01-13 11:00 | 300 |  |  | 0.36718
2020-01-13 12:00 | 301 |  |  | 0.39365
2020-01-13 13:00 | 302 |  |  | 0.39696
2020-01-13 14:00 | 303 |  |  | 0.27787
2020-01-13 15:00 | 304 |  |  | 0.12901
2020-01-13 16:00 | 305 |  |  | 0.031426
2020-01-13 17:00 | 306 |  |  | 0
2020-01-13 18:00 | 307 |  |  | 0
2020-01-13 19:00 | 308 |  |  | 0
2020-01-13 20:00 | 309 |  |  | 0
2020-01-13 21:00 | 310 |  |  | 0
2020-01-13 22:00 | 311 |  |  | 0
2020-01-13 23:00 | 312 |  |  | 0
2020-01-14 | 313 |  |  | 0
2020-01-14 01:00 | 314 |  |  | 0
2020-01-14 02:00 | 315 |  |  | 0
2020-01-14 03:00 | 316 |  |  | 0
2020-01-14 04:00 | 317 |  |  | 0
2020-01-14 05:00 | 318 |  |  | 0
2020-01-14 06:00 | 319 |  |  | 0
2020-01-14 07:00 | 320 |  |  | 0
2020-01-14 08:00 | 321 |  |  | 0.0066159
2020-01-14 09:00 | 322 |  |  | 0.1257
2020-01-14 10:00 | 323 |  |  | 0.26464
2020-01-14 11:00 | 324 |  |  | 0.36057
2020-01-14 12:00 | 325 |  |  | 0.41019
2020-01-14 13:00 | 326 |  |  | 0.37049
2020-01-14 14:00 | 327 |  |  | 0.28779
2020-01-14 15:00 | 328 |  |  | 0.15051
2020-01-14 16:00 | 329 |  |  | 0.029772
2020-01-14 17:00 | 330 |  |  | 0
2020-01-14 18:00 | 331 |  |  | 0
2020-01-14 19:00 | 332 |  |  | 0
2020-01-14 20:00 | 333 |  |  | 0
2020-01-14 21:00 | 334 |  |  | 0
2020-01-14 22:00 | 335 |  |  | 0
2020-01-14 23:00 | 336 |  |  | 0
2020-01-15 | 337 |  |  | 0
2020-01-15 01:00 | 338 |  |  | 0
2020-01-15 02:00 | 339 |  |  | 0
2020-01-15 03:00 | 340 |  |  | 0
2020-01-15 04:00 | 341 |  |  | 0
2020-01-15 05:00 | 342 |  |  | 0
2020-01-15 06:00 | 343 |  |  | 0
2020-01-15 07:00 | 344 |  |  | 0
2020-01-15 08:00 | 345 |  |  | 0.001654
2020-01-15 09:00 | 346 |  |  | 0.029772
2020-01-15 10:00 | 347 |  |  | 0.10089
2020-01-15 11:00 | 348 |  |  | 0.26795
2020-01-15 12:00 | 349 |  |  | 0.43004
2020-01-15 13:00 | 350 |  |  | 0.41515
2020-01-15 14:00 | 351 |  |  | 0.20675
2020-01-15 15:00 | 352 |  |  | 0.11909
2020-01-15 16:00 | 353 |  |  | 0.043004
2020-01-15 17:00 | 354 |  |  | 0
2020-01-15 18:00 | 355 |  |  | 0
2020-01-15 19:00 | 356 |  |  | 0
2020-01-15 20:00 | 357 |  |  | 0
2020-01-15 21:00 | 358 |  |  | 0
2020-01-15 22:00 | 359 |  |  | 0
2020-01-15 23:00 | 360 |  |  | 0
2020-01-16 | 361 |  |  | 0
2020-01-16 01:00 | 362 |  |  | 0
2020-01-16 02:00 | 363 |  |  | 0
2020-01-16 03:00 | 364 |  |  | 0
2020-01-16 04:00 | 365 |  |  | 0
2020-01-16 05:00 | 366 |  |  | 0
2020-01-16 06:00 | 367 |  |  | 0
2020-01-16 07:00 | 368 |  |  | 0
2020-01-16 08:00 | 369 |  |  | 0.011578
2020-01-16 09:00 | 370 |  |  | 0.15713
2020-01-16 10:00 | 371 |  |  | 0.30599
2020-01-16 11:00 | 372 |  |  | 0.42011
2020-01-16 12:00 | 373 |  |  | 0.43996
2020-01-16 13:00 | 374 |  |  | 0.42673
2020-01-16 14:00 | 375 |  |  | 0.33411
2020-01-16 15:00 | 376 |  |  | 0.18194
2020-01-16 16:00 | 377 |  |  | 0.034734
2020-01-16 17:00 | 378 |  |  | 0
2020-01-16 18:00 | 379 |  |  | 0
2020-01-16 19:00 | 380 |  |  | 0
2020-01-16 20:00 | 381 |  |  | 0
2020-01-16 21:00 | 382 |  |  | 0
2020-01-16 22:00 | 383 |  |  | 0
2020-01-16 23:00 | 384 |  |  | 0
2020-01-17 | 385 |  |  | 0
2020-01-17 01:00 | 386 |  |  | 0
2020-01-17 02:00 | 387 |  |  | 0
2020-01-17 03:00 | 388 |  |  | 0
2020-01-17 04:00 | 389 |  |  | 0
2020-01-17 05:00 | 390 |  |  | 0
2020-01-17 06:00 | 391 |  |  | 0
2020-01-17 07:00 | 392 |  |  | 0
2020-01-17 08:00 | 393 |  |  | 0.023156
2020-01-17 09:00 | 394 |  |  | 0.17532
2020-01-17 10:00 | 395 |  |  | 0.29276
2020-01-17 11:00 | 396 |  |  | 0.15217
2020-01-17 12:00 | 397 |  |  | 0.16209
2020-01-17 13:00 | 398 |  |  | 0.3523
2020-01-17 14:00 | 399 |  |  | 0.32914
2020-01-17 15:00 | 400 |  |  | 0.1654
2020-01-17 16:00 | 401 |  |  | 0.0082699
2020-01-17 17:00 | 402 |  |  | 0
2020-01-17 18:00 | 403 |  |  | 0
2020-01-17 19:00 | 404 |  |  | 0
2020-01-17 20:00 | 405 |  |  | 0
2020-01-17 21:00 | 406 |  |  | 0
2020-01-17 22:00 | 407 |  |  | 0
2020-01-17 23:00 | 408 |  |  | 0
2020-01-18 | 409 |  |  | 0
2020-01-18 01:00 | 410 |  |  | 0
2020-01-18 02:00 | 411 |  |  | 0
2020-01-18 03:00 | 412 |  |  | 0
2020-01-18 04:00 | 413 |  |  | 0
2020-01-18 05:00 | 414 |  |  | 0
2020-01-18 06:00 | 415 |  |  | 0
2020-01-18 07:00 | 416 |  |  | 0
2020-01-18 08:00 | 417 |  |  | 0.021502
2020-01-18 09:00 | 418 |  |  | 0.18194
2020-01-18 10:00 | 419 |  |  | 0.35891
2020-01-18 11:00 | 420 |  |  | 0.49289
2020-01-18 12:00 | 421 |  |  | 0.54912
2020-01-18 13:00 | 422 |  |  | 0.50116
2020-01-18 14:00 | 423 |  |  | 0.40192
2020-01-18 15:00 | 424 |  |  | 0.22825
2020-01-18 16:00 | 425 |  |  | 0.047966
2020-01-18 17:00 | 426 |  |  | 0
2020-01-18 18:00 | 427 |  |  | 0
2020-01-18 19:00 | 428 |  |  | 0
2020-01-18 20:00 | 429 |  |  | 0
2020-01-18 21:00 | 430 |  |  | 0
2020-01-18 22:00 | 431 |  |  | 0
2020-01-18 23:00 | 432 |  |  | 0
2020-01-19 | 433 |  |  | 0
2020-01-19 01:00 | 434 |  |  | 0
2020-01-19 02:00 | 435 |  |  | 0
2020-01-19 03:00 | 436 |  |  | 0
2020-01-19 04:00 | 437 |  |  | 0
2020-01-19 05:00 | 438 |  |  | 0
2020-01-19 06:00 | 439 |  |  | 0
2020-01-19 07:00 | 440 |  |  | 0
2020-01-19 08:00 | 441 |  |  | 0.003308
2020-01-19 09:00 | 442 |  |  | 0.069467
2020-01-19 10:00 | 443 |  |  | 0.20509
2020-01-19 11:00 | 444 |  |  | 0.42011
2020-01-19 12:00 | 445 |  |  | 0.50943
2020-01-19 13:00 | 446 |  |  | 0.37215
2020-01-19 14:00 | 447 |  |  | 0.31426
2020-01-19 15:00 | 448 |  |  | 0.15713
2020-01-19 16:00 | 449 |  |  | 0.03308
2020-01-19 17:00 | 450 |  |  | 0
2020-01-19 18:00 | 451 |  |  | 0
2020-01-19 19:00 | 452 |  |  | 0
2020-01-19 20:00 | 453 |  |  | 0
2020-01-19 21:00 | 454 |  |  | 0
2020-01-19 22:00 | 455 |  |  | 0
2020-01-19 23:00 | 456 |  |  | 0
2020-01-20 | 457 |  |  | 0
2020-01-20 01:00 | 458 |  |  | 0
2020-01-20 02:00 | 459 |  |  | 0
2020-01-20 03:00 | 460 |  |  | 0
2020-01-20 04:00 | 461 |  |  | 0
2020-01-20 05:00 | 462 |  |  | 0
2020-01-20 06:00 | 463 |  |  | 0
2020-01-20 07:00 | 464 |  |  | 0
2020-01-20 08:00 | 465 |  |  | 0
2020-01-20 09:00 | 466 |  |  | 0.02481
2020-01-20 10:00 | 467 |  |  | 0.12074
2020-01-20 11:00 | 468 |  |  | 0.18194
2020-01-20 12:00 | 469 |  |  | 0.40357
2020-01-20 13:00 | 470 |  |  | 0.48131
2020-01-20 14:00 | 471 |  |  | 0.38869
2020-01-20 15:00 | 472 |  |  | 0.23156
2020-01-20 16:00 | 473 |  |  | 0.04962
2020-01-20 17:00 | 474 |  |  | 0
2020-01-20 18:00 | 475 |  |  | 0
2020-01-20 19:00 | 476 |  |  | 0
2020-01-20 20:00 | 477 |  |  | 0
2020-01-20 21:00 | 478 |  |  | 0
2020-01-20 22:00 | 479 |  |  | 0
2020-01-20 23:00 | 480 |  |  | 0
2020-01-21 | 481 |  |  | 0
2020-01-21 01:00 | 482 |  |  | 0
2020-01-21 02:00 | 483 |  |  | 0
2020-01-21 03:00 | 484 |  |  | 0
2020-01-21 04:00 | 485 |  |  | 0
2020-01-21 05:00 | 486 |  |  | 0
2020-01-21 06:00 | 487 |  |  | 0
2020-01-21 07:00 | 488 |  |  | 0
2020-01-21 08:00 | 489 |  |  | 0.02481
2020-01-21 09:00 | 490 |  |  | 0.1654
2020-01-21 10:00 | 491 |  |  | 0.15051
2020-01-21 11:00 | 492 |  |  | 0.16209
2020-01-21 12:00 | 493 |  |  | 0.18525
2020-01-21 13:00 | 494 |  |  | 0.1654
2020-01-21 14:00 | 495 |  |  | 0.20013
2020-01-21 15:00 | 496 |  |  | 0.14059
2020-01-21 16:00 | 497 |  |  | 0.02481
2020-01-21 17:00 | 498 |  |  | 0
2020-01-21 18:00 | 499 |  |  | 0
2020-01-21 19:00 | 500 |  |  | 0
2020-01-21 20:00 | 501 |  |  | 0
2020-01-21 21:00 | 502 |  |  | 0
2020-01-21 22:00 | 503 |  |  | 0
2020-01-21 23:00 | 504 |  |  | 0
2020-01-22 | 505 |  |  | 0
2020-01-22 01:00 | 506 |  |  | 0
2020-01-22 02:00 | 507 |  |  | 0
2020-01-22 03:00 | 508 |  |  | 0
2020-01-22 04:00 | 509 |  |  | 0
2020-01-22 05:00 | 510 |  |  | 0
2020-01-22 06:00 | 511 |  |  | 0
2020-01-22 07:00 | 512 |  |  | 0
2020-01-22 08:00 | 513 |  |  | 0.026464
2020-01-22 09:00 | 514 |  |  | 0.11413
2020-01-22 10:00 | 515 |  |  | 0.28449
2020-01-22 11:00 | 516 |  |  | 0.39365
2020-01-22 12:00 | 517 |  |  | 0.42177
2020-01-22 13:00 | 518 |  |  | 0.45154
2020-01-22 14:00 | 519 |  |  | 0.32418
2020-01-22 15:00 | 520 |  |  | 0.14224
2020-01-22 16:00 | 521 |  |  | 0.062851
2020-01-22 17:00 | 522 |  |  | 0
2020-01-22 18:00 | 523 |  |  | 0
2020-01-22 19:00 | 524 |  |  | 0
2020-01-22 20:00 | 525 |  |  | 0
2020-01-22 21:00 | 526 |  |  | 0
2020-01-22 22:00 | 527 |  |  | 0
2020-01-22 23:00 | 528 |  |  | 0
2020-01-23 | 529 |  |  | 0
2020-01-23 01:00 | 530 |  |  | 0
2020-01-23 02:00 | 531 |  |  | 0
2020-01-23 03:00 | 532 |  |  | 0
2020-01-23 04:00 | 533 |  |  | 0
2020-01-23 05:00 | 534 |  |  | 0
2020-01-23 06:00 | 535 |  |  | 0
2020-01-23 07:00 | 536 |  |  | 0
2020-01-23 08:00 | 537 |  |  | 0.013232
2020-01-23 09:00 | 538 |  |  | 0.099239
2020-01-23 10:00 | 539 |  |  | 0.23487
2020-01-23 11:00 | 540 |  |  | 0.42342
2020-01-23 12:00 | 541 |  |  | 0.4168
2020-01-23 13:00 | 542 |  |  | 0.21998
2020-01-23 14:00 | 543 |  |  | 0.32749
2020-01-23 15:00 | 544 |  |  | 0.22329
2020-01-23 16:00 | 545 |  |  | 0.028118
2020-01-23 17:00 | 546 |  |  | 0
2020-01-23 18:00 | 547 |  |  | 0
2020-01-23 19:00 | 548 |  |  | 0
2020-01-23 20:00 | 549 |  |  | 0
2020-01-23 21:00 | 550 |  |  | 0
2020-01-23 22:00 | 551 |  |  | 0
2020-01-23 23:00 | 552 |  |  | 0
2020-01-24 | 553 |  |  | 0
2020-01-24 01:00 | 554 |  |  | 0
2020-01-24 02:00 | 555 |  |  | 0
2020-01-24 03:00 | 556 |  |  | 0
2020-01-24 04:00 | 557 |  |  | 0
2020-01-24 05:00 | 558 |  |  | 0
2020-01-24 06:00 | 559 |  |  | 0
2020-01-24 07:00 | 560 |  |  | 0
2020-01-24 08:00 | 561 |  |  | 0.014886
2020-01-24 09:00 | 562 |  |  | 0.077737
2020-01-24 10:00 | 563 |  |  | 0.14886
2020-01-24 11:00 | 564 |  |  | 0.16705
2020-01-24 12:00 | 565 |  |  | 0.28945
2020-01-24 13:00 | 566 |  |  | 0.13728
2020-01-24 14:00 | 567 |  |  | 0.22825
2020-01-24 15:00 | 568 |  |  | 0.099239
2020-01-24 16:00 | 569 |  |  | 0.046312
2020-01-24 17:00 | 570 |  |  | 0
2020-01-24 18:00 | 571 |  |  | 0
2020-01-24 19:00 | 572 |  |  | 0
2020-01-24 20:00 | 573 |  |  | 0
2020-01-24 21:00 | 574 |  |  | 0
2020-01-24 22:00 | 575 |  |  | 0
2020-01-24 23:00 | 576 |  |  | 0
2020-01-25 | 577 |  |  | 0
2020-01-25 01:00 | 578 |  |  | 0
2020-01-25 02:00 | 579 |  |  | 0
2020-01-25 03:00 | 580 |  |  | 0
2020-01-25 04:00 | 581 |  |  | 0
2020-01-25 05:00 | 582 |  |  | 0
2020-01-25 06:00 | 583 |  |  | 0
2020-01-25 07:00 | 584 |  |  | 0
2020-01-25 08:00 | 585 |  |  | 0.013232
2020-01-25 09:00 | 586 |  |  | 0.12074
2020-01-25 10:00 | 587 |  |  | 0.1472
2020-01-25 11:00 | 588 |  |  | 0.37711
2020-01-25 12:00 | 589 |  |  | 0.45154
2020-01-25 13:00 | 590 |  |  | 0.42673
2020-01-25 14:00 | 591 |  |  | 0.32914
2020-01-25 15:00 | 592 |  |  | 0.21006
2020-01-25 16:00 | 593 |  |  | 0.019848
2020-01-25 17:00 | 594 |  |  | 0
2020-01-25 18:00 | 595 |  |  | 0
2020-01-25 19:00 | 596 |  |  | 0
2020-01-25 20:00 | 597 |  |  | 0
2020-01-25 21:00 | 598 |  |  | 0
2020-01-25 22:00 | 599 |  |  | 0
2020-01-25 23:00 | 600 |  |  | 0
2020-01-26 | 601 |  |  | 0
2020-01-26 01:00 | 602 |  |  | 0
2020-01-26 02:00 | 603 |  |  | 0
2020-01-26 03:00 | 604 |  |  | 0
2020-01-26 04:00 | 605 |  |  | 0
2020-01-26 05:00 | 606 |  |  | 0
2020-01-26 06:00 | 607 |  |  | 0
2020-01-26 07:00 | 608 |  |  | 0
2020-01-26 08:00 | 609 |  |  | 0.021502
2020-01-26 09:00 | 610 |  |  | 0.12239
2020-01-26 10:00 | 611 |  |  | 0.24148
2020-01-26 11:00 | 612 |  |  | 0.30268
2020-01-26 12:00 | 613 |  |  | 0.33741
2020-01-26 13:00 | 614 |  |  | 0.36057
2020-01-26 14:00 | 615 |  |  | 0.40357
2020-01-26 15:00 | 616 |  |  | 0.17698
2020-01-26 16:00 | 617 |  |  | 0.028118
2020-01-26 17:00 | 618 |  |  | 0
2020-01-26 18:00 | 619 |  |  | 0
2020-01-26 19:00 | 620 |  |  | 0
2020-01-26 20:00 | 621 |  |  | 0
2020-01-26 21:00 | 622 |  |  | 0
2020-01-26 22:00 | 623 |  |  | 0
2020-01-26 23:00 | 624 |  |  | 0
2020-01-27 | 625 |  |  | 0
2020-01-27 01:00 | 626 |  |  | 0
2020-01-27 02:00 | 627 |  |  | 0
2020-01-27 03:00 | 628 |  |  | 0
2020-01-27 04:00 | 629 |  |  | 0
2020-01-27 05:00 | 630 |  |  | 0
2020-01-27 06:00 | 631 |  |  | 0
2020-01-27 07:00 | 632 |  |  | 0
2020-01-27 08:00 | 633 |  |  | 0.02481
2020-01-27 09:00 | 634 |  |  | 0.16374
2020-01-27 10:00 | 635 |  |  | 0.30433
2020-01-27 11:00 | 636 |  |  | 0.34238
2020-01-27 12:00 | 637 |  |  | 0.46973
2020-01-27 13:00 | 638 |  |  | 0.40357
2020-01-27 14:00 | 639 |  |  | 0.084353
2020-01-27 15:00 | 640 |  |  | 0.10255
2020-01-27 16:00 | 641 |  |  | 0.039696
2020-01-27 17:00 | 642 |  |  | 0
2020-01-27 18:00 | 643 |  |  | 0
2020-01-27 19:00 | 644 |  |  | 0
2020-01-27 20:00 | 645 |  |  | 0
2020-01-27 21:00 | 646 |  |  | 0
2020-01-27 22:00 | 647 |  |  | 0
2020-01-27 23:00 | 648 |  |  | 0
2020-01-28 | 649 |  |  | 0
2020-01-28 01:00 | 650 |  |  | 0
2020-01-28 02:00 | 651 |  |  | 0
2020-01-28 03:00 | 652 |  |  | 0
2020-01-28 04:00 | 653 |  |  | 0
2020-01-28 05:00 | 654 |  |  | 0
2020-01-28 06:00 | 655 |  |  | 0
2020-01-28 07:00 | 656 |  |  | 0
2020-01-28 08:00 | 657 |  |  | 0.003308
2020-01-28 09:00 | 658 |  |  | 0.099239
2020-01-28 10:00 | 659 |  |  | 0.26133
2020-01-28 11:00 | 660 |  |  | 0.40853
2020-01-28 12:00 | 661 |  |  | 0.48627
2020-01-28 13:00 | 662 |  |  | 0.48958
2020-01-28 14:00 | 663 |  |  | 0.478
2020-01-28 15:00 | 664 |  |  | 0.28614
2020-01-28 16:00 | 665 |  |  | 0.064505
2020-01-28 17:00 | 666 |  |  | 0
2020-01-28 18:00 | 667 |  |  | 0
2020-01-28 19:00 | 668 |  |  | 0
2020-01-28 20:00 | 669 |  |  | 0
2020-01-28 21:00 | 670 |  |  | 0
2020-01-28 22:00 | 671 |  |  | 0
2020-01-28 23:00 | 672 |  |  | 0
2020-01-29 | 673 |  |  | 0
2020-01-29 01:00 | 674 |  |  | 0
2020-01-29 02:00 | 675 |  |  | 0
2020-01-29 03:00 | 676 |  |  | 0
2020-01-29 04:00 | 677 |  |  | 0
2020-01-29 05:00 | 678 |  |  | 0
2020-01-29 06:00 | 679 |  |  | 0
2020-01-29 07:00 | 680 |  |  | 0
2020-01-29 08:00 | 681 |  |  | 0.031426
2020-01-29 09:00 | 682 |  |  | 0.20344
2020-01-29 10:00 | 683 |  |  | 0.37545
2020-01-29 11:00 | 684 |  |  | 0.48627
2020-01-29 12:00 | 685 |  |  | 0.56897
2020-01-29 13:00 | 686 |  |  | 0.55905
2020-01-29 14:00 | 687 |  |  | 0.48296
2020-01-29 15:00 | 688 |  |  | 0.3126
2020-01-29 16:00 | 689 |  |  | 0.11578
2020-01-29 17:00 | 690 |  |  | 0
2020-01-29 18:00 | 691 |  |  | 0
2020-01-29 19:00 | 692 |  |  | 0
2020-01-29 20:00 | 693 |  |  | 0
2020-01-29 21:00 | 694 |  |  | 0
2020-01-29 22:00 | 695 |  |  | 0
2020-01-29 23:00 | 696 |  |  | 0
2020-01-30 | 697 |  |  | 0
2020-01-30 01:00 | 698 |  |  | 0
2020-01-30 02:00 | 699 |  |  | 0
2020-01-30 03:00 | 700 |  |  | 0
2020-01-30 04:00 | 701 |  |  | 0
2020-01-30 05:00 | 702 |  |  | 0
2020-01-30 06:00 | 703 |  |  | 0
2020-01-30 07:00 | 704 |  |  | 0
2020-01-30 08:00 | 705 |  |  | 0.013232
2020-01-30 09:00 | 706 |  |  | 0.14059
2020-01-30 10:00 | 707 |  |  | 0.28449
2020-01-30 11:00 | 708 |  |  | 0.47139
2020-01-30 12:00 | 709 |  |  | 0.49454
2020-01-30 13:00 | 710 |  |  | 0.40523
2020-01-30 14:00 | 711 |  |  | 0.15713
2020-01-30 15:00 | 712 |  |  | 0.16705
2020-01-30 16:00 | 713 |  |  | 0.11578
2020-01-30 17:00 | 714 |  |  | 0.003308
2020-01-30 18:00 | 715 |  |  | 0
2020-01-30 19:00 | 716 |  |  | 0
2020-01-30 20:00 | 717 |  |  | 0
2020-01-30 21:00 | 718 |  |  | 0
2020-01-30 22:00 | 719 |  |  | 0
2020-01-30 23:00 | 720 |  |  | 0
2020-01-31 | 721 |  |  | 0
2020-01-31 01:00 | 722 |  |  | 0
2020-01-31 02:00 | 723 |  |  | 0
2020-01-31 03:00 | 724 |  |  | 0
2020-01-31 04:00 | 725 |  |  | 0
2020-01-31 05:00 | 726 |  |  | 0
2020-01-31 06:00 | 727 |  |  | 0
2020-01-31 07:00 | 728 |  |  | 0
2020-01-31 08:00 | 729 |  |  | 0.031426
2020-01-31 09:00 | 730 |  |  | 0.18028
2020-01-31 10:00 | 731 |  |  | 0.33411
2020-01-31 11:00 | 732 |  |  | 0.45485
2020-01-31 12:00 | 733 |  |  | 0.54085
2020-01-31 13:00 | 734 |  |  | 0.46973
2020-01-31 14:00 | 735 |  |  | 0.44492
2020-01-31 15:00 | 736 |  |  | 0.28614
2020-01-31 16:00 | 737 |  |  | 0.11578
2020-01-31 17:00 | 738 |  |  | 0
2020-01-31 18:00 | 739 |  |  | 0
2020-01-31 19:00 | 740 |  |  | 0
2020-01-31 20:00 | 741 |  |  | 0
2020-01-31 21:00 | 742 |  |  | 0
2020-01-31 22:00 | 743 |  |  | 0
2020-01-31 23:00 | 744 |  |  | 0
2020-02-01 | 745 |  |  | 0
2020-02-01 01:00 | 746 |  |  | 0
2020-02-01 02:00 | 747 |  |  | 0
2020-02-01 03:00 | 748 |  |  | 0
2020-02-01 04:00 | 749 |  |  | 0
2020-02-01 05:00 | 750 |  |  | 0
2020-02-01 06:00 | 751 |  |  | 0
2020-02-01 07:00 | 752 |  |  | 0
2020-02-01 08:00 | 753 |  |  | 0
2020-02-01 09:00 | 754 |  |  | 0.011578
2020-02-01 10:00 | 755 |  |  | 0.10751
2020-02-01 11:00 | 756 |  |  | 0.15051
2020-02-01 12:00 | 757 |  |  | 0.22494
2020-02-01 13:00 | 758 |  |  | 0.12901
2020-02-01 14:00 | 759 |  |  | 0.11082
2020-02-01 15:00 | 760 |  |  | 0.10751
2020-02-01 16:00 | 761 |  |  | 0.1257
2020-02-01 17:00 | 762 |  |  | 0.001654
2020-02-01 18:00 | 763 |  |  | 0
2020-02-01 19:00 | 764 |  |  | 0
2020-02-01 20:00 | 765 |  |  | 0
2020-02-01 21:00 | 766 |  |  | 0
2020-02-01 22:00 | 767 |  |  | 0
2020-02-01 23:00 | 768 |  |  | 0
2020-02-02 | 769 |  |  | 0
2020-02-02 01:00 | 770 |  |  | 0
2020-02-02 02:00 | 771 |  |  | 0
2020-02-02 03:00 | 772 |  |  | 0
2020-02-02 04:00 | 773 |  |  | 0
2020-02-02 05:00 | 774 |  |  | 0
2020-02-02 06:00 | 775 |  |  | 0
2020-02-02 07:00 | 776 |  |  | 0
2020-02-02 08:00 | 777 |  |  | 0
2020-02-02 09:00 | 778 |  |  | 0.044658
2020-02-02 10:00 | 779 |  |  | 0.13397
2020-02-02 11:00 | 780 |  |  | 0.43665
2020-02-02 12:00 | 781 |  |  | 0.52266
2020-02-02 13:00 | 782 |  |  | 0.53258
2020-02-02 14:00 | 783 |  |  | 0.44823
2020-02-02 15:00 | 784 |  |  | 0.27952
2020-02-02 16:00 | 785 |  |  | 0.086007
2020-02-02 17:00 | 786 |  |  | 0
2020-02-02 18:00 | 787 |  |  | 0
2020-02-02 19:00 | 788 |  |  | 0
2020-02-02 20:00 | 789 |  |  | 0
2020-02-02 21:00 | 790 |  |  | 0
2020-02-02 22:00 | 791 |  |  | 0
2020-02-02 23:00 | 792 |  |  | 0
2020-02-03 | 793 |  |  | 0
2020-02-03 01:00 | 794 |  |  | 0
2020-02-03 02:00 | 795 |  |  | 0
2020-02-03 03:00 | 796 |  |  | 0
2020-02-03 04:00 | 797 |  |  | 0
2020-02-03 05:00 | 798 |  |  | 0
2020-02-03 06:00 | 799 |  |  | 0
2020-02-03 07:00 | 800 |  |  | 0
2020-02-03 08:00 | 801 |  |  | 0.026464
2020-02-03 09:00 | 802 |  |  | 0.18525
2020-02-03 10:00 | 803 |  |  | 0.37049
2020-02-03 11:00 | 804 |  |  | 0.43996
2020-02-03 12:00 | 805 |  |  | 0.41846
2020-02-03 13:00 | 806 |  |  | 0.46808
2020-02-03 14:00 | 807 |  |  | 0.43996
2020-02-03 15:00 | 808 |  |  | 0.25471
2020-02-03 16:00 | 809 |  |  | 0.10089
2020-02-03 17:00 | 810 |  |  | 0.001654
2020-02-03 18:00 | 811 |  |  | 0
2020-02-03 19:00 | 812 |  |  | 0
2020-02-03 20:00 | 813 |  |  | 0
2020-02-03 21:00 | 814 |  |  | 0
2020-02-03 22:00 | 815 |  |  | 0
2020-02-03 23:00 | 816 |  |  | 0
2020-02-04 | 817 |  |  | 0
2020-02-04 01:00 | 818 |  |  | 0
2020-02-04 02:00 | 819 |  |  | 0
2020-02-04 03:00 | 820 |  |  | 0
2020-02-04 04:00 | 821 |  |  | 0
2020-02-04 05:00 | 822 |  |  | 0
2020-02-04 06:00 | 823 |  |  | 0
2020-02-04 07:00 | 824 |  |  | 0
2020-02-04 08:00 | 825 |  |  | 0.044658
2020-02-04 09:00 | 826 |  |  | 0.21833
2020-02-04 10:00 | 827 |  |  | 0.40688
2020-02-04 11:00 | 828 |  |  | 0.54416
2020-02-04 12:00 | 829 |  |  | 0.50447
2020-02-04 13:00 | 830 |  |  | 0.49289
2020-02-04 14:00 | 831 |  |  | 0.48958
2020-02-04 15:00 | 832 |  |  | 0.36222
2020-02-04 16:00 | 833 |  |  | 0.061197
2020-02-04 17:00 | 834 |  |  | 0.003308
2020-02-04 18:00 | 835 |  |  | 0
2020-02-04 19:00 | 836 |  |  | 0
2020-02-04 20:00 | 837 |  |  | 0
2020-02-04 21:00 | 838 |  |  | 0
2020-02-04 22:00 | 839 |  |  | 0
2020-02-04 23:00 | 840 |  |  | 0
2020-02-05 | 841 |  |  | 0
2020-02-05 01:00 | 842 |  |  | 0
2020-02-05 02:00 | 843 |  |  | 0
2020-02-05 03:00 | 844 |  |  | 0
2020-02-05 04:00 | 845 |  |  | 0
2020-02-05 05:00 | 846 |  |  | 0
2020-02-05 06:00 | 847 |  |  | 0
2020-02-05 07:00 | 848 |  |  | 0
2020-02-05 08:00 | 849 |  |  | 0.047966
2020-02-05 09:00 | 850 |  |  | 0.22825
2020-02-05 10:00 | 851 |  |  | 0.40688
2020-02-05 11:00 | 852 |  |  | 0.54085
2020-02-05 12:00 | 853 |  |  | 0.62851
2020-02-05 13:00 | 854 |  |  | 0.65002
2020-02-05 14:00 | 855 |  |  | 0.51274
2020-02-05 15:00 | 856 |  |  | 0.36057
2020-02-05 16:00 | 857 |  |  | 0.15713
2020-02-05 17:00 | 858 |  |  | 0.004962
2020-02-05 18:00 | 859 |  |  | 0
2020-02-05 19:00 | 860 |  |  | 0
2020-02-05 20:00 | 861 |  |  | 0
2020-02-05 21:00 | 862 |  |  | 0
2020-02-05 22:00 | 863 |  |  | 0
2020-02-05 23:00 | 864 |  |  | 0
2020-02-06 | 865 |  |  | 0
2020-02-06 01:00 | 866 |  |  | 0
2020-02-06 02:00 | 867 |  |  | 0
2020-02-06 03:00 | 868 |  |  | 0
2020-02-06 04:00 | 869 |  |  | 0
2020-02-06 05:00 | 870 |  |  | 0
2020-02-06 06:00 | 871 |  |  | 0
2020-02-06 07:00 | 872 |  |  | 0
2020-02-06 08:00 | 873 |  |  | 0.02481
2020-02-06 09:00 | 874 |  |  | 0.15878
2020-02-06 10:00 | 875 |  |  | 0.3308
2020-02-06 11:00 | 876 |  |  | 0.40192
2020-02-06 12:00 | 877 |  |  | 0.37215
2020-02-06 13:00 | 878 |  |  | 0.33411
2020-02-06 14:00 | 879 |  |  | 0.27291
2020-02-06 15:00 | 880 |  |  | 0.2266
2020-02-06 16:00 | 881 |  |  | 0.081045
2020-02-06 17:00 | 882 |  |  | 0.003308
2020-02-06 18:00 | 883 |  |  | 0
2020-02-06 19:00 | 884 |  |  | 0
2020-02-06 20:00 | 885 |  |  | 0
2020-02-06 21:00 | 886 |  |  | 0
2020-02-06 22:00 | 887 |  |  | 0
2020-02-06 23:00 | 888 |  |  | 0
2020-02-07 | 889 |  |  | 0
2020-02-07 01:00 | 890 |  |  | 0
2020-02-07 02:00 | 891 |  |  | 0
2020-02-07 03:00 | 892 |  |  | 0
2020-02-07 04:00 | 893 |  |  | 0
2020-02-07 05:00 | 894 |  |  | 0
2020-02-07 06:00 | 895 |  |  | 0
2020-02-07 07:00 | 896 |  |  | 0
2020-02-07 08:00 | 897 |  |  | 0.047966
2020-02-07 09:00 | 898 |  |  | 0.21998
2020-02-07 10:00 | 899 |  |  | 0.3953
2020-02-07 11:00 | 900 |  |  | 0.50447
2020-02-07 12:00 | 901 |  |  | 0.57724
2020-02-07 13:00 | 902 |  |  | 0.5822
2020-02-07 14:00 | 903 |  |  | 0.49123
2020-02-07 15:00 | 904 |  |  | 0.35395
2020-02-07 16:00 | 905 |  |  | 0.16044
2020-02-07 17:00 | 906 |  |  | 0.0082699
2020-02-07 18:00 | 907 |  |  | 0
2020-02-07 19:00 | 908 |  |  | 0
2020-02-07 20:00 | 909 |  |  | 0
2020-02-07 21:00 | 910 |  |  | 0
2020-02-07 22:00 | 911 |  |  | 0
2020-02-07 23:00 | 912 |  |  | 0
2020-02-08 | 913 |  |  | 0
2020-02-08 01:00 | 914 |  |  | 0
2020-02-08 02:00 | 915 |  |  | 0
2020-02-08 03:00 | 916 |  |  | 0
2020-02-08 04:00 | 917 |  |  | 0
2020-02-08 05:00 | 918 |  |  | 0
2020-02-08 06:00 | 919 |  |  | 0
2020-02-08 07:00 | 920 |  |  | 0
2020-02-08 08:00 | 921 |  |  | 0.061197
2020-02-08 09:00 | 922 |  |  | 0.19021
2020-02-08 10:00 | 923 |  |  | 0.18359
2020-02-08 11:00 | 924 |  |  | 0.42838
2020-02-08 12:00 | 925 |  |  | 0.48296
2020-02-08 13:00 | 926 |  |  | 0.42838
2020-02-08 14:00 | 927 |  |  | 0.37215
2020-02-08 15:00 | 928 |  |  | 0.33576
2020-02-08 16:00 | 929 |  |  | 0.084353
2020-02-08 17:00 | 930 |  |  | 0.001654
2020-02-08 18:00 | 931 |  |  | 0
2020-02-08 19:00 | 932 |  |  | 0
2020-02-08 20:00 | 933 |  |  | 0
2020-02-08 21:00 | 934 |  |  | 0
2020-02-08 22:00 | 935 |  |  | 0
2020-02-08 23:00 | 936 |  |  | 0
2020-02-09 | 937 |  |  | 0
2020-02-09 01:00 | 938 |  |  | 0
2020-02-09 02:00 | 939 |  |  | 0
2020-02-09 03:00 | 940 |  |  | 0
2020-02-09 04:00 | 941 |  |  | 0
2020-02-09 05:00 | 942 |  |  | 0
2020-02-09 06:00 | 943 |  |  | 0
2020-02-09 07:00 | 944 |  |  | 0
2020-02-09 08:00 | 945 |  |  | 0.046312
2020-02-09 09:00 | 946 |  |  | 0.1869
2020-02-09 10:00 | 947 |  |  | 0.34568
2020-02-09 11:00 | 948 |  |  | 0.45815
2020-02-09 12:00 | 949 |  |  | 0.52762
2020-02-09 13:00 | 950 |  |  | 0.52431
2020-02-09 14:00 | 951 |  |  | 0.42011
2020-02-09 15:00 | 952 |  |  | 0.24644
2020-02-09 16:00 | 953 |  |  | 0.076083
2020-02-09 17:00 | 954 |  |  | 0
2020-02-09 18:00 | 955 |  |  | 0
2020-02-09 19:00 | 956 |  |  | 0
2020-02-09 20:00 | 957 |  |  | 0
2020-02-09 21:00 | 958 |  |  | 0
2020-02-09 22:00 | 959 |  |  | 0
2020-02-09 23:00 | 960 |  |  | 0
2020-02-10 | 961 |  |  | 0
2020-02-10 01:00 | 962 |  |  | 0
2020-02-10 02:00 | 963 |  |  | 0
2020-02-10 03:00 | 964 |  |  | 0
2020-02-10 04:00 | 965 |  |  | 0
2020-02-10 05:00 | 966 |  |  | 0
2020-02-10 06:00 | 967 |  |  | 0
2020-02-10 07:00 | 968 |  |  | 0
2020-02-10 08:00 | 969 |  |  | 0.0099239
2020-02-10 09:00 | 970 |  |  | 0.082699
2020-02-10 10:00 | 971 |  |  | 0.34238
2020-02-10 11:00 | 972 |  |  | 0.49785
2020-02-10 12:00 | 973 |  |  | 0.54582
2020-02-10 13:00 | 974 |  |  | 0.59709
2020-02-10 14:00 | 975 |  |  | 0.48627
2020-02-10 15:00 | 976 |  |  | 0.34072
2020-02-10 16:00 | 977 |  |  | 0.13232
2020-02-10 17:00 | 978 |  |  | 0
2020-02-10 18:00 | 979 |  |  | 0
2020-02-10 19:00 | 980 |  |  | 0
2020-02-10 20:00 | 981 |  |  | 0
2020-02-10 21:00 | 982 |  |  | 0
2020-02-10 22:00 | 983 |  |  | 0
2020-02-10 23:00 | 984 |  |  | 0
2020-02-11 | 985 |  |  | 0
2020-02-11 01:00 | 986 |  |  | 0
2020-02-11 02:00 | 987 |  |  | 0
2020-02-11 03:00 | 988 |  |  | 0
2020-02-11 04:00 | 989 |  |  | 0
2020-02-11 05:00 | 990 |  |  | 0
2020-02-11 06:00 | 991 |  |  | 0
2020-02-11 07:00 | 992 |  |  | 0
2020-02-11 08:00 | 993 |  |  | 0.04962
2020-02-11 09:00 | 994 |  |  | 0.24644
2020-02-11 10:00 | 995 |  |  | 0.42177
2020-02-11 11:00 | 996 |  |  | 0.56732
2020-02-11 12:00 | 997 |  |  | 0.66656
2020-02-11 13:00 | 998 |  |  | 0.68806
2020-02-11 14:00 | 999 |  |  | 0.57724
2020-02-11 15:00 | 1000 |  |  | 0.41515
2020-02-11 16:00 | 1001 |  |  | 0.1869
2020-02-11 17:00 | 1002 |  |  | 0.021502
2020-02-11 18:00 | 1003 |  |  | 0
2020-02-11 19:00 | 1004 |  |  | 0
2020-02-11 20:00 | 1005 |  |  | 0
2020-02-11 21:00 | 1006 |  |  | 0
2020-02-11 22:00 | 1007 |  |  | 0
2020-02-11 23:00 | 1008 |  |  | 0
2020-02-12 | 1009 |  |  | 0
2020-02-12 01:00 | 1010 |  |  | 0
2020-02-12 02:00 | 1011 |  |  | 0
2020-02-12 03:00 | 1012 |  |  | 0
2020-02-12 04:00 | 1013 |  |  | 0
2020-02-12 05:00 | 1014 |  |  | 0
2020-02-12 06:00 | 1015 |  |  | 0
2020-02-12 07:00 | 1016 |  |  | 0
2020-02-12 08:00 | 1017 |  |  | 0.059543
2020-02-12 09:00 | 1018 |  |  | 0.2481
2020-02-12 10:00 | 1019 |  |  | 0.43169
2020-02-12 11:00 | 1020 |  |  | 0.56732
2020-02-12 12:00 | 1021 |  |  | 0.64671
2020-02-12 13:00 | 1022 |  |  | 0.68806
2020-02-12 14:00 | 1023 |  |  | 0.57724
2020-02-12 15:00 | 1024 |  |  | 0.43665
2020-02-12 16:00 | 1025 |  |  | 0.2084
2020-02-12 17:00 | 1026 |  |  | 0.026464
2020-02-12 18:00 | 1027 |  |  | 0
2020-02-12 19:00 | 1028 |  |  | 0
2020-02-12 20:00 | 1029 |  |  | 0
2020-02-12 21:00 | 1030 |  |  | 0
2020-02-12 22:00 | 1031 |  |  | 0
2020-02-12 23:00 | 1032 |  |  | 0
2020-02-13 | 1033 |  |  | 0
2020-02-13 01:00 | 1034 |  |  | 0
2020-02-13 02:00 | 1035 |  |  | 0
2020-02-13 03:00 | 1036 |  |  | 0
2020-02-13 04:00 | 1037 |  |  | 0
2020-02-13 05:00 | 1038 |  |  | 0
2020-02-13 06:00 | 1039 |  |  | 0
2020-02-13 07:00 | 1040 |  |  | 0
2020-02-13 08:00 | 1041 |  |  | 0.046312
2020-02-13 09:00 | 1042 |  |  | 0.23652
2020-02-13 10:00 | 1043 |  |  | 0.40192
2020-02-13 11:00 | 1044 |  |  | 0.53589
2020-02-13 12:00 | 1045 |  |  | 0.61528
2020-02-13 13:00 | 1046 |  |  | 0.53755
2020-02-13 14:00 | 1047 |  |  | 0.23156
2020-02-13 15:00 | 1048 |  |  | 0.20179
2020-02-13 16:00 | 1049 |  |  | 0.15051
2020-02-13 17:00 | 1050 |  |  | 0
2020-02-13 18:00 | 1051 |  |  | 0
2020-02-13 19:00 | 1052 |  |  | 0
2020-02-13 20:00 | 1053 |  |  | 0
2020-02-13 21:00 | 1054 |  |  | 0
2020-02-13 22:00 | 1055 |  |  | 0
2020-02-13 23:00 | 1056 |  |  | 0
2020-02-14 | 1057 |  |  | 0
2020-02-14 01:00 | 1058 |  |  | 0
2020-02-14 02:00 | 1059 |  |  | 0
2020-02-14 03:00 | 1060 |  |  | 0
2020-02-14 04:00 | 1061 |  |  | 0
2020-02-14 05:00 | 1062 |  |  | 0
2020-02-14 06:00 | 1063 |  |  | 0
2020-02-14 07:00 | 1064 |  |  | 0
2020-02-14 08:00 | 1065 |  |  | 0.051274
2020-02-14 09:00 | 1066 |  |  | 0.2266
2020-02-14 10:00 | 1067 |  |  | 0.39199
2020-02-14 11:00 | 1068 |  |  | 0.52928
2020-02-14 12:00 | 1069 |  |  | 0.60205
2020-02-14 13:00 | 1070 |  |  | 0.59047
2020-02-14 14:00 | 1071 |  |  | 0.5392
2020-02-14 15:00 | 1072 |  |  | 0.39365
2020-02-14 16:00 | 1073 |  |  | 0.20509
2020-02-14 17:00 | 1074 |  |  | 0.028118
2020-02-14 18:00 | 1075 |  |  | 0
2020-02-14 19:00 | 1076 |  |  | 0
2020-02-14 20:00 | 1077 |  |  | 0
2020-02-14 21:00 | 1078 |  |  | 0
2020-02-14 22:00 | 1079 |  |  | 0
2020-02-14 23:00 | 1080 |  |  | 0
2020-02-15 | 1081 |  |  | 0
2020-02-15 01:00 | 1082 |  |  | 0
2020-02-15 02:00 | 1083 |  |  | 0
2020-02-15 03:00 | 1084 |  |  | 0
2020-02-15 04:00 | 1085 |  |  | 0
2020-02-15 05:00 | 1086 |  |  | 0
2020-02-15 06:00 | 1087 |  |  | 0
2020-02-15 07:00 | 1088 |  |  | 0
2020-02-15 08:00 | 1089 |  |  | 0.069467
2020-02-15 09:00 | 1090 |  |  | 0.2084
2020-02-15 10:00 | 1091 |  |  | 0.31922
2020-02-15 11:00 | 1092 |  |  | 0.54085
2020-02-15 12:00 | 1093 |  |  | 0.60205
2020-02-15 13:00 | 1094 |  |  | 0.60205
2020-02-15 14:00 | 1095 |  |  | 0.52266
2020-02-15 15:00 | 1096 |  |  | 0.35726
2020-02-15 16:00 | 1097 |  |  | 0.15547
2020-02-15 17:00 | 1098 |  |  | 0.02481
2020-02-15 18:00 | 1099 |  |  | 0
2020-02-15 19:00 | 1100 |  |  | 0
2020-02-15 20:00 | 1101 |  |  | 0
2020-02-15 21:00 | 1102 |  |  | 0
2020-02-15 22:00 | 1103 |  |  | 0
2020-02-15 23:00 | 1104 |  |  | 0
2020-02-16 | 1105 |  |  | 0
2020-02-16 01:00 | 1106 |  |  | 0
2020-02-16 02:00 | 1107 |  |  | 0
2020-02-16 03:00 | 1108 |  |  | 0
2020-02-16 04:00 | 1109 |  |  | 0
2020-02-16 05:00 | 1110 |  |  | 0
2020-02-16 06:00 | 1111 |  |  | 0
2020-02-16 07:00 | 1112 |  |  | 0
2020-02-16 08:00 | 1113 |  |  | 0.044658
2020-02-16 09:00 | 1114 |  |  | 0.19682
2020-02-16 10:00 | 1115 |  |  | 0.36057
2020-02-16 11:00 | 1116 |  |  | 0.31922
2020-02-16 12:00 | 1117 |  |  | 0.30433
2020-02-16 13:00 | 1118 |  |  | 0.21006
2020-02-16 14:00 | 1119 |  |  | 0.24975
2020-02-16 15:00 | 1120 |  |  | 0.099239
2020-02-16 16:00 | 1121 |  |  | 0.044658
2020-02-16 17:00 | 1122 |  |  | 0
2020-02-16 18:00 | 1123 |  |  | 0
2020-02-16 19:00 | 1124 |  |  | 0
2020-02-16 20:00 | 1125 |  |  | 0
2020-02-16 21:00 | 1126 |  |  | 0
2020-02-16 22:00 | 1127 |  |  | 0
2020-02-16 23:00 | 1128 |  |  | 0
2020-02-17 | 1129 |  |  | 0
2020-02-17 01:00 | 1130 |  |  | 0
2020-02-17 02:00 | 1131 |  |  | 0
2020-02-17 03:00 | 1132 |  |  | 0
2020-02-17 04:00 | 1133 |  |  | 0
2020-02-17 05:00 | 1134 |  |  | 0
2020-02-17 06:00 | 1135 |  |  | 0
2020-02-17 07:00 | 1136 |  |  | 0
2020-02-17 08:00 | 1137 |  |  | 0.031426
2020-02-17 09:00 | 1138 |  |  | 0.086007
2020-02-17 10:00 | 1139 |  |  | 0.21998
2020-02-17 11:00 | 1140 |  |  | 0.37545
2020-02-17 12:00 | 1141 |  |  | 0.49785
2020-02-17 13:00 | 1142 |  |  | 0.51604
2020-02-17 14:00 | 1143 |  |  | 0.40523
2020-02-17 15:00 | 1144 |  |  | 0.25968
2020-02-17 16:00 | 1145 |  |  | 0.11909
2020-02-17 17:00 | 1146 |  |  | 0.001654
2020-02-17 18:00 | 1147 |  |  | 0
2020-02-17 19:00 | 1148 |  |  | 0
2020-02-17 20:00 | 1149 |  |  | 0
2020-02-17 21:00 | 1150 |  |  | 0
2020-02-17 22:00 | 1151 |  |  | 0
2020-02-17 23:00 | 1152 |  |  | 0
2020-02-18 | 1153 |  |  | 0
2020-02-18 01:00 | 1154 |  |  | 0
2020-02-18 02:00 | 1155 |  |  | 0
2020-02-18 03:00 | 1156 |  |  | 0
2020-02-18 04:00 | 1157 |  |  | 0
2020-02-18 05:00 | 1158 |  |  | 0
2020-02-18 06:00 | 1159 |  |  | 0
2020-02-18 07:00 | 1160 |  |  | 0
2020-02-18 08:00 | 1161 |  |  | 0.066159
2020-02-18 09:00 | 1162 |  |  | 0.2299
2020-02-18 10:00 | 1163 |  |  | 0.39696
2020-02-18 11:00 | 1164 |  |  | 0.50777
2020-02-18 12:00 | 1165 |  |  | 0.6004
2020-02-18 13:00 | 1166 |  |  | 0.58882
2020-02-18 14:00 | 1167 |  |  | 0.49123
2020-02-18 15:00 | 1168 |  |  | 0.38703
2020-02-18 16:00 | 1169 |  |  | 0.21833
2020-02-18 17:00 | 1170 |  |  | 0.034734
2020-02-18 18:00 | 1171 |  |  | 0
2020-02-18 19:00 | 1172 |  |  | 0
2020-02-18 20:00 | 1173 |  |  | 0
2020-02-18 21:00 | 1174 |  |  | 0
2020-02-18 22:00 | 1175 |  |  | 0
2020-02-18 23:00 | 1176 |  |  | 0
2020-02-19 | 1177 |  |  | 0
2020-02-19 01:00 | 1178 |  |  | 0
2020-02-19 02:00 | 1179 |  |  | 0
2020-02-19 03:00 | 1180 |  |  | 0
2020-02-19 04:00 | 1181 |  |  | 0
2020-02-19 05:00 | 1182 |  |  | 0
2020-02-19 06:00 | 1183 |  |  | 0
2020-02-19 07:00 | 1184 |  |  | 0
2020-02-19 08:00 | 1185 |  |  | 0.062851
2020-02-19 09:00 | 1186 |  |  | 0.21171
2020-02-19 10:00 | 1187 |  |  | 0.19517
2020-02-19 11:00 | 1188 |  |  | 0.4962
2020-02-19 12:00 | 1189 |  |  | 0.60205
2020-02-19 13:00 | 1190 |  |  | 0.60205
2020-02-19 14:00 | 1191 |  |  | 0.59709
2020-02-19 15:00 | 1192 |  |  | 0.43996
2020-02-19 16:00 | 1193 |  |  | 0.23983
2020-02-19 17:00 | 1194 |  |  | 0.04962
2020-02-19 18:00 | 1195 |  |  | 0
2020-02-19 19:00 | 1196 |  |  | 0
2020-02-19 20:00 | 1197 |  |  | 0
2020-02-19 21:00 | 1198 |  |  | 0
2020-02-19 22:00 | 1199 |  |  | 0
2020-02-19 23:00 | 1200 |  |  | 0
2020-02-20 | 1201 |  |  | 0
2020-02-20 01:00 | 1202 |  |  | 0
2020-02-20 02:00 | 1203 |  |  | 0
2020-02-20 03:00 | 1204 |  |  | 0
2020-02-20 04:00 | 1205 |  |  | 0
2020-02-20 05:00 | 1206 |  |  | 0
2020-02-20 06:00 | 1207 |  |  | 0
2020-02-20 07:00 | 1208 |  |  | 0
2020-02-20 08:00 | 1209 |  |  | 0.087661
2020-02-20 09:00 | 1210 |  |  | 0.2299
2020-02-20 10:00 | 1211 |  |  | 0.38869
2020-02-20 11:00 | 1212 |  |  | 0.46477
2020-02-20 12:00 | 1213 |  |  | 0.62521
2020-02-20 13:00 | 1214 |  |  | 0.47966
2020-02-20 14:00 | 1215 |  |  | 0.5822
2020-02-20 15:00 | 1216 |  |  | 0.38372
2020-02-20 16:00 | 1217 |  |  | 0.21502
2020-02-20 17:00 | 1218 |  |  | 0.043004
2020-02-20 18:00 | 1219 |  |  | 0
2020-02-20 19:00 | 1220 |  |  | 0
2020-02-20 20:00 | 1221 |  |  | 0
2020-02-20 21:00 | 1222 |  |  | 0
2020-02-20 22:00 | 1223 |  |  | 0
2020-02-20 23:00 | 1224 |  |  | 0
2020-02-21 | 1225 |  |  | 0
2020-02-21 01:00 | 1226 |  |  | 0
2020-02-21 02:00 | 1227 |  |  | 0
2020-02-21 03:00 | 1228 |  |  | 0
2020-02-21 04:00 | 1229 |  |  | 0
2020-02-21 05:00 | 1230 |  |  | 0
2020-02-21 06:00 | 1231 |  |  | 0
2020-02-21 07:00 | 1232 |  |  | 0
2020-02-21 08:00 | 1233 |  |  | 0.072775
2020-02-21 09:00 | 1234 |  |  | 0.23817
2020-02-21 10:00 | 1235 |  |  | 0.36553
2020-02-21 11:00 | 1236 |  |  | 0.35891
2020-02-21 12:00 | 1237 |  |  | 0.34734
2020-02-21 13:00 | 1238 |  |  | 0.36884
2020-02-21 14:00 | 1239 |  |  | 0.32584
2020-02-21 15:00 | 1240 |  |  | 0.29441
2020-02-21 16:00 | 1241 |  |  | 0.17367
2020-02-21 17:00 | 1242 |  |  | 0.026464
2020-02-21 18:00 | 1243 |  |  | 0
2020-02-21 19:00 | 1244 |  |  | 0
2020-02-21 20:00 | 1245 |  |  | 0
2020-02-21 21:00 | 1246 |  |  | 0
2020-02-21 22:00 | 1247 |  |  | 0
2020-02-21 23:00 | 1248 |  |  | 0
2020-02-22 | 1249 |  |  | 0
2020-02-22 01:00 | 1250 |  |  | 0
2020-02-22 02:00 | 1251 |  |  | 0
2020-02-22 03:00 | 1252 |  |  | 0
2020-02-22 04:00 | 1253 |  |  | 0
2020-02-22 05:00 | 1254 |  |  | 0
2020-02-22 06:00 | 1255 |  |  | 0
2020-02-22 07:00 | 1256 |  |  | 0
2020-02-22 08:00 | 1257 |  |  | 0.076083
2020-02-22 09:00 | 1258 |  |  | 0.21006
2020-02-22 10:00 | 1259 |  |  | 0.36553
2020-02-22 11:00 | 1260 |  |  | 0.47966
2020-02-22 12:00 | 1261 |  |  | 0.56566
2020-02-22 13:00 | 1262 |  |  | 0.56897
2020-02-22 14:00 | 1263 |  |  | 0.50777
2020-02-22 15:00 | 1264 |  |  | 0.37049
2020-02-22 16:00 | 1265 |  |  | 0.19682
2020-02-22 17:00 | 1266 |  |  | 0.031426
2020-02-22 18:00 | 1267 |  |  | 0
2020-02-22 19:00 | 1268 |  |  | 0
2020-02-22 20:00 | 1269 |  |  | 0
2020-02-22 21:00 | 1270 |  |  | 0
2020-02-22 22:00 | 1271 |  |  | 0
2020-02-22 23:00 | 1272 |  |  | 0
2020-02-23 | 1273 |  |  | 0
2020-02-23 01:00 | 1274 |  |  | 0
2020-02-23 02:00 | 1275 |  |  | 0
2020-02-23 03:00 | 1276 |  |  | 0
2020-02-23 04:00 | 1277 |  |  | 0
2020-02-23 05:00 | 1278 |  |  | 0
2020-02-23 06:00 | 1279 |  |  | 0
2020-02-23 07:00 | 1280 |  |  | 0
2020-02-23 08:00 | 1281 |  |  | 0.029772
2020-02-23 09:00 | 1282 |  |  | 0.15878
2020-02-23 10:00 | 1283 |  |  | 0.27952
2020-02-23 11:00 | 1284 |  |  | 0.34734
2020-02-23 12:00 | 1285 |  |  | 0.45319
2020-02-23 13:00 | 1286 |  |  | 0.18525
2020-02-23 14:00 | 1287 |  |  | 0.14224
2020-02-23 15:00 | 1288 |  |  | 0.14224
2020-02-23 16:00 | 1289 |  |  | 0.15217
2020-02-23 17:00 | 1290 |  |  | 0.062851
2020-02-23 18:00 | 1291 |  |  | 0
2020-02-23 19:00 | 1292 |  |  | 0
2020-02-23 20:00 | 1293 |  |  | 0
2020-02-23 21:00 | 1294 |  |  | 0
2020-02-23 22:00 | 1295 |  |  | 0
2020-02-23 23:00 | 1296 |  |  | 0
2020-02-24 | 1297 |  |  | 0
2020-02-24 01:00 | 1298 |  |  | 0
2020-02-24 02:00 | 1299 |  |  | 0
2020-02-24 03:00 | 1300 |  |  | 0
2020-02-24 04:00 | 1301 |  |  | 0
2020-02-24 05:00 | 1302 |  |  | 0
2020-02-24 06:00 | 1303 |  |  | 0
2020-02-24 07:00 | 1304 |  |  | 0
2020-02-24 08:00 | 1305 |  |  | 0.089315
2020-02-24 09:00 | 1306 |  |  | 0.26464
2020-02-24 10:00 | 1307 |  |  | 0.43004
2020-02-24 11:00 | 1308 |  |  | 0.54251
2020-02-24 12:00 | 1309 |  |  | 0.61694
2020-02-24 13:00 | 1310 |  |  | 0.61032
2020-02-24 14:00 | 1311 |  |  | 0.58882
2020-02-24 15:00 | 1312 |  |  | 0.44823
2020-02-24 16:00 | 1313 |  |  | 0.25471
2020-02-24 17:00 | 1314 |  |  | 0.05789
2020-02-24 18:00 | 1315 |  |  | 0
2020-02-24 19:00 | 1316 |  |  | 0
2020-02-24 20:00 | 1317 |  |  | 0
2020-02-24 21:00 | 1318 |  |  | 0
2020-02-24 22:00 | 1319 |  |  | 0
2020-02-24 23:00 | 1320 |  |  | 0
2020-02-25 | 1321 |  |  | 0
2020-02-25 01:00 | 1322 |  |  | 0
2020-02-25 02:00 | 1323 |  |  | 0
2020-02-25 03:00 | 1324 |  |  | 0
2020-02-25 04:00 | 1325 |  |  | 0
2020-02-25 05:00 | 1326 |  |  | 0
2020-02-25 06:00 | 1327 |  |  | 0
2020-02-25 07:00 | 1328 |  |  | 0
2020-02-25 08:00 | 1329 |  |  | 0
2020-02-25 09:00 | 1330 |  |  | 0.090969
2020-02-25 10:00 | 1331 |  |  | 0.14224
2020-02-25 11:00 | 1332 |  |  | 0.14224
2020-02-25 12:00 | 1333 |  |  | 0.10586
2020-02-25 13:00 | 1334 |  |  | 0.16374
2020-02-25 14:00 | 1335 |  |  | 0.24975
2020-02-25 15:00 | 1336 |  |  | 0.17863
2020-02-25 16:00 | 1337 |  |  | 0.1042
2020-02-25 17:00 | 1338 |  |  | 0.011578
2020-02-25 18:00 | 1339 |  |  | 0
2020-02-25 19:00 | 1340 |  |  | 0
2020-02-25 20:00 | 1341 |  |  | 0
2020-02-25 21:00 | 1342 |  |  | 0
2020-02-25 22:00 | 1343 |  |  | 0
2020-02-25 23:00 | 1344 |  |  | 0
2020-02-26 | 1345 |  |  | 0
2020-02-26 01:00 | 1346 |  |  | 0
2020-02-26 02:00 | 1347 |  |  | 0
2020-02-26 03:00 | 1348 |  |  | 0
2020-02-26 04:00 | 1349 |  |  | 0
2020-02-26 05:00 | 1350 |  |  | 0
2020-02-26 06:00 | 1351 |  |  | 0
2020-02-26 07:00 | 1352 |  |  | 0
2020-02-26 08:00 | 1353 |  |  | 0.10255
2020-02-26 09:00 | 1354 |  |  | 0.3093
2020-02-26 10:00 | 1355 |  |  | 0.45815
2020-02-26 11:00 | 1356 |  |  | 0.61859
2020-02-26 12:00 | 1357 |  |  | 0.66325
2020-02-26 13:00 | 1358 |  |  | 0.71618
2020-02-26 14:00 | 1359 |  |  | 0.69302
2020-02-26 15:00 | 1360 |  |  | 0.52431
2020-02-26 16:00 | 1361 |  |  | 0.32584
2020-02-26 17:00 | 1362 |  |  | 0.021502
2020-02-26 18:00 | 1363 |  |  | 0
2020-02-26 19:00 | 1364 |  |  | 0
2020-02-26 20:00 | 1365 |  |  | 0
2020-02-26 21:00 | 1366 |  |  | 0
2020-02-26 22:00 | 1367 |  |  | 0
2020-02-26 23:00 | 1368 |  |  | 0
2020-02-27 | 1369 |  |  | 0
2020-02-27 01:00 | 1370 |  |  | 0
2020-02-27 02:00 | 1371 |  |  | 0
2020-02-27 03:00 | 1372 |  |  | 0
2020-02-27 04:00 | 1373 |  |  | 0
2020-02-27 05:00 | 1374 |  |  | 0
2020-02-27 06:00 | 1375 |  |  | 0
2020-02-27 07:00 | 1376 |  |  | 0
2020-02-27 08:00 | 1377 |  |  | 0.092623
2020-02-27 09:00 | 1378 |  |  | 0.2481
2020-02-27 10:00 | 1379 |  |  | 0.40192
2020-02-27 11:00 | 1380 |  |  | 0.55739
2020-02-27 12:00 | 1381 |  |  | 0.53258
2020-02-27 13:00 | 1382 |  |  | 0.36222
2020-02-27 14:00 | 1383 |  |  | 0.13563
2020-02-27 15:00 | 1384 |  |  | 0.11082
2020-02-27 16:00 | 1385 |  |  | 0.1439
2020-02-27 17:00 | 1386 |  |  | 0.019848
2020-02-27 18:00 | 1387 |  |  | 0
2020-02-27 19:00 | 1388 |  |  | 0
2020-02-27 20:00 | 1389 |  |  | 0
2020-02-27 21:00 | 1390 |  |  | 0
2020-02-27 22:00 | 1391 |  |  | 0
2020-02-27 23:00 | 1392 |  |  | 0
2020-02-28 | 1393 |  |  | 0
2020-02-28 01:00 | 1394 |  |  | 0
2020-02-28 02:00 | 1395 |  |  | 0
2020-02-28 03:00 | 1396 |  |  | 0
2020-02-28 04:00 | 1397 |  |  | 0
2020-02-28 05:00 | 1398 |  |  | 0
2020-02-28 06:00 | 1399 |  |  | 0
2020-02-28 07:00 | 1400 |  |  | 0
2020-02-28 08:00 | 1401 |  |  | 0.095931
2020-02-28 09:00 | 1402 |  |  | 0.28945
2020-02-28 10:00 | 1403 |  |  | 0.47139
2020-02-28 11:00 | 1404 |  |  | 0.59874
2020-02-28 12:00 | 1405 |  |  | 0.68971
2020-02-28 13:00 | 1406 |  |  | 0.69798
2020-02-28 14:00 | 1407 |  |  | 0.63513
2020-02-28 15:00 | 1408 |  |  | 0.48793
2020-02-28 16:00 | 1409 |  |  | 0.28779
2020-02-28 17:00 | 1410 |  |  | 0.074429
2020-02-28 18:00 | 1411 |  |  | 0
2020-02-28 19:00 | 1412 |  |  | 0
2020-02-28 20:00 | 1413 |  |  | 0
2020-02-28 21:00 | 1414 |  |  | 0
2020-02-28 22:00 | 1415 |  |  | 0
2020-02-28 23:00 | 1416 |  |  | 0
2020-02-29 | 1417 |  |  | 0
2020-02-29 01:00 | 1418 |  |  | 0
2020-02-29 02:00 | 1419 |  |  | 0
2020-02-29 03:00 | 1420 |  |  | 0
2020-02-29 04:00 | 1421 |  |  | 0
2020-02-29 05:00 | 1422 |  |  | 0
2020-02-29 06:00 | 1423 |  |  | 0
2020-02-29 07:00 | 1424 |  |  | 0.0066159
2020-02-29 08:00 | 1425 |  |  | 0.047966
2020-02-29 09:00 | 1426 |  |  | 0.15382
2020-02-29 10:00 | 1427 |  |  | 0.33245
2020-02-29 11:00 | 1428 |  |  | 0.31426
2020-02-29 12:00 | 1429 |  |  | 0.2911
2020-02-29 13:00 | 1430 |  |  | 0.54416
2020-02-29 14:00 | 1431 |  |  | 0.45815
2020-02-29 15:00 | 1432 |  |  | 0.1439
2020-02-29 16:00 | 1433 |  |  | 0.05789
2020-02-29 17:00 | 1434 |  |  | 0.0082699
2020-02-29 18:00 | 1435 |  |  | 0
2020-02-29 19:00 | 1436 |  |  | 0
2020-02-29 20:00 | 1437 |  |  | 0
2020-02-29 21:00 | 1438 |  |  | 0
2020-02-29 22:00 | 1439 |  |  | 0
2020-02-29 23:00 | 1440 |  |  | 0
2020-03-01 | 1441 |  |  | 0
2020-03-01 01:00 | 1442 |  |  | 0
2020-03-01 02:00 | 1443 |  |  | 0
2020-03-01 03:00 | 1444 |  |  | 0
2020-03-01 04:00 | 1445 |  |  | 0
2020-03-01 05:00 | 1446 |  |  | 0
2020-03-01 06:00 | 1447 |  |  | 0
2020-03-01 07:00 | 1448 |  |  | 0
2020-03-01 08:00 | 1449 |  |  | 0.044658
2020-03-01 09:00 | 1450 |  |  | 0.11578
2020-03-01 10:00 | 1451 |  |  | 0.16705
2020-03-01 11:00 | 1452 |  |  | 0.23321
2020-03-01 12:00 | 1453 |  |  | 0.19517
2020-03-01 13:00 | 1454 |  |  | 0.54416
2020-03-01 14:00 | 1455 |  |  | 0.25968
2020-03-01 15:00 | 1456 |  |  | 0.32087
2020-03-01 16:00 | 1457 |  |  | 0.16705
2020-03-01 17:00 | 1458 |  |  | 0.047966
2020-03-01 18:00 | 1459 |  |  | 0
2020-03-01 19:00 | 1460 |  |  | 0
2020-03-01 20:00 | 1461 |  |  | 0
2020-03-01 21:00 | 1462 |  |  | 0
2020-03-01 22:00 | 1463 |  |  | 0
2020-03-01 23:00 | 1464 |  |  | 0
2020-03-02 | 1465 |  |  | 0
2020-03-02 01:00 | 1466 |  |  | 0
2020-03-02 02:00 | 1467 |  |  | 0
2020-03-02 03:00 | 1468 |  |  | 0
2020-03-02 04:00 | 1469 |  |  | 0
2020-03-02 05:00 | 1470 |  |  | 0
2020-03-02 06:00 | 1471 |  |  | 0
2020-03-02 07:00 | 1472 |  |  | 0
2020-03-02 08:00 | 1473 |  |  | 0
2020-03-02 09:00 | 1474 |  |  | 0.004962
2020-03-02 10:00 | 1475 |  |  | 0.001654
2020-03-02 11:00 | 1476 |  |  | 0.031426
2020-03-02 12:00 | 1477 |  |  | 0.047966
2020-03-02 13:00 | 1478 |  |  | 0.069467
2020-03-02 14:00 | 1479 |  |  | 0.034734
2020-03-02 15:00 | 1480 |  |  | 0.0066159
2020-03-02 16:00 | 1481 |  |  | 0.02481
2020-03-02 17:00 | 1482 |  |  | 0.018194
2020-03-02 18:00 | 1483 |  |  | 0
2020-03-02 19:00 | 1484 |  |  | 0
2020-03-02 20:00 | 1485 |  |  | 0
2020-03-02 21:00 | 1486 |  |  | 0
2020-03-02 22:00 | 1487 |  |  | 0
2020-03-02 23:00 | 1488 |  |  | 0
2020-03-03 | 1489 |  |  | 0
2020-03-03 01:00 | 1490 |  |  | 0
2020-03-03 02:00 | 1491 |  |  | 0
2020-03-03 03:00 | 1492 |  |  | 0
2020-03-03 04:00 | 1493 |  |  | 0
2020-03-03 05:00 | 1494 |  |  | 0
2020-03-03 06:00 | 1495 |  |  | 0
2020-03-03 07:00 | 1496 |  |  | 0
2020-03-03 08:00 | 1497 |  |  | 0.11413
2020-03-03 09:00 | 1498 |  |  | 0.33907
2020-03-03 10:00 | 1499 |  |  | 0.5177
2020-03-03 11:00 | 1500 |  |  | 0.66159
2020-03-03 12:00 | 1501 |  |  | 0.71121
2020-03-03 13:00 | 1502 |  |  | 0.70294
2020-03-03 14:00 | 1503 |  |  | 0.61032
2020-03-03 15:00 | 1504 |  |  | 0.3126
2020-03-03 16:00 | 1505 |  |  | 0.26795
2020-03-03 17:00 | 1506 |  |  | 0.11413
2020-03-03 18:00 | 1507 |  |  | 0
2020-03-03 19:00 | 1508 |  |  | 0
2020-03-03 20:00 | 1509 |  |  | 0
2020-03-03 21:00 | 1510 |  |  | 0
2020-03-03 22:00 | 1511 |  |  | 0
2020-03-03 23:00 | 1512 |  |  | 0
2020-03-04 | 1513 |  |  | 0
2020-03-04 01:00 | 1514 |  |  | 0
2020-03-04 02:00 | 1515 |  |  | 0
2020-03-04 03:00 | 1516 |  |  | 0
2020-03-04 04:00 | 1517 |  |  | 0
2020-03-04 05:00 | 1518 |  |  | 0
2020-03-04 06:00 | 1519 |  |  | 0
2020-03-04 07:00 | 1520 |  |  | 0
2020-03-04 08:00 | 1521 |  |  | 0.12239
2020-03-04 09:00 | 1522 |  |  | 0.33245
2020-03-04 10:00 | 1523 |  |  | 0.4995
2020-03-04 11:00 | 1524 |  |  | 0.64175
2020-03-04 12:00 | 1525 |  |  | 0.69302
2020-03-04 13:00 | 1526 |  |  | 0.60867
2020-03-04 14:00 | 1527 |  |  | 0.39861
2020-03-04 15:00 | 1528 |  |  | 0.52762
2020-03-04 16:00 | 1529 |  |  | 0.34568
2020-03-04 17:00 | 1530 |  |  | 0.11082
2020-03-04 18:00 | 1531 |  |  | 0
2020-03-04 19:00 | 1532 |  |  | 0
2020-03-04 20:00 | 1533 |  |  | 0
2020-03-04 21:00 | 1534 |  |  | 0
2020-03-04 22:00 | 1535 |  |  | 0
2020-03-04 23:00 | 1536 |  |  | 0
2020-03-05 | 1537 |  |  | 0
2020-03-05 01:00 | 1538 |  |  | 0
2020-03-05 02:00 | 1539 |  |  | 0
2020-03-05 03:00 | 1540 |  |  | 0
2020-03-05 04:00 | 1541 |  |  | 0
2020-03-05 05:00 | 1542 |  |  | 0
2020-03-05 06:00 | 1543 |  |  | 0
2020-03-05 07:00 | 1544 |  |  | 0.026464
2020-03-05 08:00 | 1545 |  |  | 0.1257
2020-03-05 09:00 | 1546 |  |  | 0.21336
2020-03-05 10:00 | 1547 |  |  | 0.39199
2020-03-05 11:00 | 1548 |  |  | 0.36884
2020-03-05 12:00 | 1549 |  |  | 0.26298
2020-03-05 13:00 | 1550 |  |  | 0.10751
2020-03-05 14:00 | 1551 |  |  | 0.10255
2020-03-05 15:00 | 1552 |  |  | 0.11082
2020-03-05 16:00 | 1553 |  |  | 0.04962
2020-03-05 17:00 | 1554 |  |  | 0
2020-03-05 18:00 | 1555 |  |  | 0
2020-03-05 19:00 | 1556 |  |  | 0
2020-03-05 20:00 | 1557 |  |  | 0
2020-03-05 21:00 | 1558 |  |  | 0
2020-03-05 22:00 | 1559 |  |  | 0
2020-03-05 23:00 | 1560 |  |  | 0
2020-03-06 | 1561 |  |  | 0
2020-03-06 01:00 | 1562 |  |  | 0
2020-03-06 02:00 | 1563 |  |  | 0
2020-03-06 03:00 | 1564 |  |  | 0
2020-03-06 04:00 | 1565 |  |  | 0
2020-03-06 05:00 | 1566 |  |  | 0
2020-03-06 06:00 | 1567 |  |  | 0
2020-03-06 07:00 | 1568 |  |  | 0
2020-03-06 08:00 | 1569 |  |  | 0.05789
2020-03-06 09:00 | 1570 |  |  | 0.069467
2020-03-06 10:00 | 1571 |  |  | 0.11413
2020-03-06 11:00 | 1572 |  |  | 0.16044
2020-03-06 12:00 | 1573 |  |  | 0.2911
2020-03-06 13:00 | 1574 |  |  | 0.70129
2020-03-06 14:00 | 1575 |  |  | 0.68144
2020-03-06 15:00 | 1576 |  |  | 0.39199
2020-03-06 16:00 | 1577 |  |  | 0.16374
2020-03-06 17:00 | 1578 |  |  | 0.036388
2020-03-06 18:00 | 1579 |  |  | 0
2020-03-06 19:00 | 1580 |  |  | 0
2020-03-06 20:00 | 1581 |  |  | 0
2020-03-06 21:00 | 1582 |  |  | 0
2020-03-06 22:00 | 1583 |  |  | 0
2020-03-06 23:00 | 1584 |  |  | 0
2020-03-07 | 1585 |  |  | 0
2020-03-07 01:00 | 1586 |  |  | 0
2020-03-07 02:00 | 1587 |  |  | 0
2020-03-07 03:00 | 1588 |  |  | 0
2020-03-07 04:00 | 1589 |  |  | 0
2020-03-07 05:00 | 1590 |  |  | 0
2020-03-07 06:00 | 1591 |  |  | 0
2020-03-07 07:00 | 1592 |  |  | 0.003308
2020-03-07 08:00 | 1593 |  |  | 0.13563
2020-03-07 09:00 | 1594 |  |  | 0.34899
2020-03-07 10:00 | 1595 |  |  | 0.5177
2020-03-07 11:00 | 1596 |  |  | 0.6434
2020-03-07 12:00 | 1597 |  |  | 0.71121
2020-03-07 13:00 | 1598 |  |  | 0.70294
2020-03-07 14:00 | 1599 |  |  | 0.68971
2020-03-07 15:00 | 1600 |  |  | 0.55905
2020-03-07 16:00 | 1601 |  |  | 0.35065
2020-03-07 17:00 | 1602 |  |  | 0.12736
2020-03-07 18:00 | 1603 |  |  | 0
2020-03-07 19:00 | 1604 |  |  | 0
2020-03-07 20:00 | 1605 |  |  | 0
2020-03-07 21:00 | 1606 |  |  | 0
2020-03-07 22:00 | 1607 |  |  | 0
2020-03-07 23:00 | 1608 |  |  | 0
2020-03-08 | 1609 |  |  | 0
2020-03-08 01:00 | 1610 |  |  | 0
2020-03-08 02:00 | 1611 |  |  | 0
2020-03-08 03:00 | 1612 |  |  | 0
2020-03-08 04:00 | 1613 |  |  | 0
2020-03-08 05:00 | 1614 |  |  | 0
2020-03-08 06:00 | 1615 |  |  | 0
2020-03-08 07:00 | 1616 |  |  | 0.023156
2020-03-08 08:00 | 1617 |  |  | 0.15382
2020-03-08 09:00 | 1618 |  |  | 0.28779
2020-03-08 10:00 | 1619 |  |  | 0.30764
2020-03-08 11:00 | 1620 |  |  | 0.6649
2020-03-08 12:00 | 1621 |  |  | 0.51935
2020-03-08 13:00 | 1622 |  |  | 0.435
2020-03-08 14:00 | 1623 |  |  | 0.50943
2020-03-08 15:00 | 1624 |  |  | 0.31591
2020-03-08 16:00 | 1625 |  |  | 0.3308
2020-03-08 17:00 | 1626 |  |  | 0.018194
2020-03-08 18:00 | 1627 |  |  | 0
2020-03-08 19:00 | 1628 |  |  | 0
2020-03-08 20:00 | 1629 |  |  | 0
2020-03-08 21:00 | 1630 |  |  | 0
2020-03-08 22:00 | 1631 |  |  | 0
2020-03-08 23:00 | 1632 |  |  | 0
2020-03-09 | 1633 |  |  | 0
2020-03-09 01:00 | 1634 |  |  | 0
2020-03-09 02:00 | 1635 |  |  | 0
2020-03-09 03:00 | 1636 |  |  | 0
2020-03-09 04:00 | 1637 |  |  | 0
2020-03-09 05:00 | 1638 |  |  | 0
2020-03-09 06:00 | 1639 |  |  | 0
2020-03-09 07:00 | 1640 |  |  | 0
2020-03-09 08:00 | 1641 |  |  | 0.004962
2020-03-09 09:00 | 1642 |  |  | 0.066159
2020-03-09 10:00 | 1643 |  |  | 0.2084
2020-03-09 11:00 | 1644 |  |  | 0.44492
2020-03-09 12:00 | 1645 |  |  | 0.4135
2020-03-09 13:00 | 1646 |  |  | 0.36553
2020-03-09 14:00 | 1647 |  |  | 0.38703
2020-03-09 15:00 | 1648 |  |  | 0.47469
2020-03-09 16:00 | 1649 |  |  | 0.3308
2020-03-09 17:00 | 1650 |  |  | 0.10089
2020-03-09 18:00 | 1651 |  |  | 0
2020-03-09 19:00 | 1652 |  |  | 0
2020-03-09 20:00 | 1653 |  |  | 0
2020-03-09 21:00 | 1654 |  |  | 0
2020-03-09 22:00 | 1655 |  |  | 0
2020-03-09 23:00 | 1656 |  |  | 0
2020-03-10 | 1657 |  |  | 0
2020-03-10 01:00 | 1658 |  |  | 0
2020-03-10 02:00 | 1659 |  |  | 0
2020-03-10 03:00 | 1660 |  |  | 0
2020-03-10 04:00 | 1661 |  |  | 0
2020-03-10 05:00 | 1662 |  |  | 0
2020-03-10 06:00 | 1663 |  |  | 0
2020-03-10 07:00 | 1664 |  |  | 0.0066159
2020-03-10 08:00 | 1665 |  |  | 0.11578
2020-03-10 09:00 | 1666 |  |  | 0.32749
2020-03-10 10:00 | 1667 |  |  | 0.47304
2020-03-10 11:00 | 1668 |  |  | 0.55574
2020-03-10 12:00 | 1669 |  |  | 0.69964
2020-03-10 13:00 | 1670 |  |  | 0.70956
2020-03-10 14:00 | 1671 |  |  | 0.67317
2020-03-10 15:00 | 1672 |  |  | 0.56732
2020-03-10 16:00 | 1673 |  |  | 0.34072
2020-03-10 17:00 | 1674 |  |  | 0.11909
2020-03-10 18:00 | 1675 |  |  | 0
2020-03-10 19:00 | 1676 |  |  | 0
2020-03-10 20:00 | 1677 |  |  | 0
2020-03-10 21:00 | 1678 |  |  | 0
2020-03-10 22:00 | 1679 |  |  | 0
2020-03-10 23:00 | 1680 |  |  | 0
2020-03-11 | 1681 |  |  | 0
2020-03-11 01:00 | 1682 |  |  | 0
2020-03-11 02:00 | 1683 |  |  | 0
2020-03-11 03:00 | 1684 |  |  | 0
2020-03-11 04:00 | 1685 |  |  | 0
2020-03-11 05:00 | 1686 |  |  | 0
2020-03-11 06:00 | 1687 |  |  | 0
2020-03-11 07:00 | 1688 |  |  | 0.003308
2020-03-11 08:00 | 1689 |  |  | 0.13893
2020-03-11 09:00 | 1690 |  |  | 0.33907
2020-03-11 10:00 | 1691 |  |  | 0.4995
2020-03-11 11:00 | 1692 |  |  | 0.61032
2020-03-11 12:00 | 1693 |  |  | 0.7046
2020-03-11 13:00 | 1694 |  |  | 0.71121
2020-03-11 14:00 | 1695 |  |  | 0.66821
2020-03-11 15:00 | 1696 |  |  | 0.56732
2020-03-11 16:00 | 1697 |  |  | 0.35395
2020-03-11 17:00 | 1698 |  |  | 0.1257
2020-03-11 18:00 | 1699 |  |  | 0
2020-03-11 19:00 | 1700 |  |  | 0
2020-03-11 20:00 | 1701 |  |  | 0
2020-03-11 21:00 | 1702 |  |  | 0
2020-03-11 22:00 | 1703 |  |  | 0
2020-03-11 23:00 | 1704 |  |  | 0
2020-03-12 | 1705 |  |  | 0
2020-03-12 01:00 | 1706 |  |  | 0
2020-03-12 02:00 | 1707 |  |  | 0
2020-03-12 03:00 | 1708 |  |  | 0
2020-03-12 04:00 | 1709 |  |  | 0
2020-03-12 05:00 | 1710 |  |  | 0
2020-03-12 06:00 | 1711 |  |  | 0
2020-03-12 07:00 | 1712 |  |  | 0
2020-03-12 08:00 | 1713 |  |  | 0.034734
2020-03-12 09:00 | 1714 |  |  | 0.17367
2020-03-12 10:00 | 1715 |  |  | 0.3126
2020-03-12 11:00 | 1716 |  |  | 0.31922
2020-03-12 12:00 | 1717 |  |  | 0.25637
2020-03-12 13:00 | 1718 |  |  | 0.17863
2020-03-12 14:00 | 1719 |  |  | 0.18028
2020-03-12 15:00 | 1720 |  |  | 0.14555
2020-03-12 16:00 | 1721 |  |  | 0.081045
2020-03-12 17:00 | 1722 |  |  | 0.0066159
2020-03-12 18:00 | 1723 |  |  | 0
2020-03-12 19:00 | 1724 |  |  | 0
2020-03-12 20:00 | 1725 |  |  | 0
2020-03-12 21:00 | 1726 |  |  | 0
2020-03-12 22:00 | 1727 |  |  | 0
2020-03-12 23:00 | 1728 |  |  | 0
2020-03-13 | 1729 |  |  | 0
2020-03-13 01:00 | 1730 |  |  | 0
2020-03-13 02:00 | 1731 |  |  | 0
2020-03-13 03:00 | 1732 |  |  | 0
2020-03-13 04:00 | 1733 |  |  | 0
2020-03-13 05:00 | 1734 |  |  | 0
2020-03-13 06:00 | 1735 |  |  | 0
2020-03-13 07:00 | 1736 |  |  | 0
2020-03-13 08:00 | 1737 |  |  | 0.10751
2020-03-13 09:00 | 1738 |  |  | 0.11578
2020-03-13 10:00 | 1739 |  |  | 0.35561
2020-03-13 11:00 | 1740 |  |  | 0.61363
2020-03-13 12:00 | 1741 |  |  | 0.62851
2020-03-13 13:00 | 1742 |  |  | 0.67813
2020-03-13 14:00 | 1743 |  |  | 0.63348
2020-03-13 15:00 | 1744 |  |  | 0.51439
2020-03-13 16:00 | 1745 |  |  | 0.33576
2020-03-13 17:00 | 1746 |  |  | 0.10089
2020-03-13 18:00 | 1747 |  |  | 0
2020-03-13 19:00 | 1748 |  |  | 0
2020-03-13 20:00 | 1749 |  |  | 0
2020-03-13 21:00 | 1750 |  |  | 0
2020-03-13 22:00 | 1751 |  |  | 0
2020-03-13 23:00 | 1752 |  |  | 0
2020-03-14 | 1753 |  |  | 0
2020-03-14 01:00 | 1754 |  |  | 0
2020-03-14 02:00 | 1755 |  |  | 0
2020-03-14 03:00 | 1756 |  |  | 0
2020-03-14 04:00 | 1757 |  |  | 0
2020-03-14 05:00 | 1758 |  |  | 0
2020-03-14 06:00 | 1759 |  |  | 0
2020-03-14 07:00 | 1760 |  |  | 0
2020-03-14 08:00 | 1761 |  |  | 0
2020-03-14 09:00 | 1762 |  |  | 0
2020-03-14 10:00 | 1763 |  |  | 0.046312
2020-03-14 11:00 | 1764 |  |  | 0.086007
2020-03-14 12:00 | 1765 |  |  | 0.044658
2020-03-14 13:00 | 1766 |  |  | 0.069467
2020-03-14 14:00 | 1767 |  |  | 0.10916
2020-03-14 15:00 | 1768 |  |  | 0.044658
2020-03-14 16:00 | 1769 |  |  | 0.0099239
2020-03-14 17:00 | 1770 |  |  | 0
2020-03-14 18:00 | 1771 |  |  | 0
2020-03-14 19:00 | 1772 |  |  | 0
2020-03-14 20:00 | 1773 |  |  | 0
2020-03-14 21:00 | 1774 |  |  | 0
2020-03-14 22:00 | 1775 |  |  | 0
2020-03-14 23:00 | 1776 |  |  | 0
2020-03-15 | 1777 |  |  | 0
2020-03-15 01:00 | 1778 |  |  | 0
2020-03-15 02:00 | 1779 |  |  | 0
2020-03-15 03:00 | 1780 |  |  | 0
2020-03-15 04:00 | 1781 |  |  | 0
2020-03-15 05:00 | 1782 |  |  | 0
2020-03-15 06:00 | 1783 |  |  | 0
2020-03-15 07:00 | 1784 |  |  | 0.0082699
2020-03-15 08:00 | 1785 |  |  | 0.01654
2020-03-15 09:00 | 1786 |  |  | 0.038042
2020-03-15 10:00 | 1787 |  |  | 0.094277
2020-03-15 11:00 | 1788 |  |  | 0.14224
2020-03-15 12:00 | 1789 |  |  | 0.14886
2020-03-15 13:00 | 1790 |  |  | 0.20013
2020-03-15 14:00 | 1791 |  |  | 0.22494
2020-03-15 15:00 | 1792 |  |  | 0.17036
2020-03-15 16:00 | 1793 |  |  | 0.13232
2020-03-15 17:00 | 1794 |  |  | 0.028118
2020-03-15 18:00 | 1795 |  |  | 0
2020-03-15 19:00 | 1796 |  |  | 0
2020-03-15 20:00 | 1797 |  |  | 0
2020-03-15 21:00 | 1798 |  |  | 0
2020-03-15 22:00 | 1799 |  |  | 0
2020-03-15 23:00 | 1800 |  |  | 0
2020-03-16 | 1801 |  |  | 0
2020-03-16 01:00 | 1802 |  |  | 0
2020-03-16 02:00 | 1803 |  |  | 0
2020-03-16 03:00 | 1804 |  |  | 0
2020-03-16 04:00 | 1805 |  |  | 0
2020-03-16 05:00 | 1806 |  |  | 0
2020-03-16 06:00 | 1807 |  |  | 0
2020-03-16 07:00 | 1808 |  |  | 0
2020-03-16 08:00 | 1809 |  |  | 0.039696
2020-03-16 09:00 | 1810 |  |  | 0.064505
2020-03-16 10:00 | 1811 |  |  | 0.13563
2020-03-16 11:00 | 1812 |  |  | 0.20675
2020-03-16 12:00 | 1813 |  |  | 0.37876
2020-03-16 13:00 | 1814 |  |  | 0.55739
2020-03-16 14:00 | 1815 |  |  | 0.54747
2020-03-16 15:00 | 1816 |  |  | 0.20013
2020-03-16 16:00 | 1817 |  |  | 0.082699
2020-03-16 17:00 | 1818 |  |  | 0.0082699
2020-03-16 18:00 | 1819 |  |  | 0
2020-03-16 19:00 | 1820 |  |  | 0
2020-03-16 20:00 | 1821 |  |  | 0
2020-03-16 21:00 | 1822 |  |  | 0
2020-03-16 22:00 | 1823 |  |  | 0
2020-03-16 23:00 | 1824 |  |  | 0
2020-03-17 | 1825 |  |  | 0
2020-03-17 01:00 | 1826 |  |  | 0
2020-03-17 02:00 | 1827 |  |  | 0
2020-03-17 03:00 | 1828 |  |  | 0
2020-03-17 04:00 | 1829 |  |  | 0
2020-03-17 05:00 | 1830 |  |  | 0
2020-03-17 06:00 | 1831 |  |  | 0
2020-03-17 07:00 | 1832 |  |  | 0.031426
2020-03-17 08:00 | 1833 |  |  | 0.11909
2020-03-17 09:00 | 1834 |  |  | 0.22163
2020-03-17 10:00 | 1835 |  |  | 0.37049
2020-03-17 11:00 | 1836 |  |  | 0.59543
2020-03-17 12:00 | 1837 |  |  | 0.69137
2020-03-17 13:00 | 1838 |  |  | 0.71452
2020-03-17 14:00 | 1839 |  |  | 0.65829
2020-03-17 15:00 | 1840 |  |  | 0.56732
2020-03-17 16:00 | 1841 |  |  | 0.36884
2020-03-17 17:00 | 1842 |  |  | 0.1472
2020-03-17 18:00 | 1843 |  |  | 0.001654
2020-03-17 19:00 | 1844 |  |  | 0
2020-03-17 20:00 | 1845 |  |  | 0
2020-03-17 21:00 | 1846 |  |  | 0
2020-03-17 22:00 | 1847 |  |  | 0
2020-03-17 23:00 | 1848 |  |  | 0
2020-03-18 | 1849 |  |  | 0
2020-03-18 01:00 | 1850 |  |  | 0
2020-03-18 02:00 | 1851 |  |  | 0
2020-03-18 03:00 | 1852 |  |  | 0
2020-03-18 04:00 | 1853 |  |  | 0
2020-03-18 05:00 | 1854 |  |  | 0
2020-03-18 06:00 | 1855 |  |  | 0
2020-03-18 07:00 | 1856 |  |  | 0.018194
2020-03-18 08:00 | 1857 |  |  | 0.16044
2020-03-18 09:00 | 1858 |  |  | 0.34899
2020-03-18 10:00 | 1859 |  |  | 0.50943
2020-03-18 11:00 | 1860 |  |  | 0.59378
2020-03-18 12:00 | 1861 |  |  | 0.68806
2020-03-18 13:00 | 1862 |  |  | 0.71121
2020-03-18 14:00 | 1863 |  |  | 0.65498
2020-03-18 15:00 | 1864 |  |  | 0.54251
2020-03-18 16:00 | 1865 |  |  | 0.35395
2020-03-18 17:00 | 1866 |  |  | 0.13563
2020-03-18 18:00 | 1867 |  |  | 0.001654
2020-03-18 19:00 | 1868 |  |  | 0
2020-03-18 20:00 | 1869 |  |  | 0
2020-03-18 21:00 | 1870 |  |  | 0
2020-03-18 22:00 | 1871 |  |  | 0
2020-03-18 23:00 | 1872 |  |  | 0
2020-03-19 | 1873 |  |  | 0
2020-03-19 01:00 | 1874 |  |  | 0
2020-03-19 02:00 | 1875 |  |  | 0
2020-03-19 03:00 | 1876 |  |  | 0
2020-03-19 04:00 | 1877 |  |  | 0
2020-03-19 05:00 | 1878 |  |  | 0
2020-03-19 06:00 | 1879 |  |  | 0
2020-03-19 07:00 | 1880 |  |  | 0.02481
2020-03-19 08:00 | 1881 |  |  | 0.16209
2020-03-19 09:00 | 1882 |  |  | 0.34734
2020-03-19 10:00 | 1883 |  |  | 0.51108
2020-03-19 11:00 | 1884 |  |  | 0.60701
2020-03-19 12:00 | 1885 |  |  | 0.7046
2020-03-19 13:00 | 1886 |  |  | 0.71121
2020-03-19 14:00 | 1887 |  |  | 0.67648
2020-03-19 15:00 | 1888 |  |  | 0.56897
2020-03-19 16:00 | 1889 |  |  | 0.38372
2020-03-19 17:00 | 1890 |  |  | 0.15713
2020-03-19 18:00 | 1891 |  |  | 0.003308
2020-03-19 19:00 | 1892 |  |  | 0
2020-03-19 20:00 | 1893 |  |  | 0
2020-03-19 21:00 | 1894 |  |  | 0
2020-03-19 22:00 | 1895 |  |  | 0
2020-03-19 23:00 | 1896 |  |  | 0
2020-03-20 | 1897 |  |  | 0
2020-03-20 01:00 | 1898 |  |  | 0
2020-03-20 02:00 | 1899 |  |  | 0
2020-03-20 03:00 | 1900 |  |  | 0
2020-03-20 04:00 | 1901 |  |  | 0
2020-03-20 05:00 | 1902 |  |  | 0
2020-03-20 06:00 | 1903 |  |  | 0
2020-03-20 07:00 | 1904 |  |  | 0.066159
2020-03-20 08:00 | 1905 |  |  | 0.12736
2020-03-20 09:00 | 1906 |  |  | 0.19186
2020-03-20 10:00 | 1907 |  |  | 0.31922
2020-03-20 11:00 | 1908 |  |  | 0.17863
2020-03-20 12:00 | 1909 |  |  | 0.69137
2020-03-20 13:00 | 1910 |  |  | 0.64505
2020-03-20 14:00 | 1911 |  |  | 0.42673
2020-03-20 15:00 | 1912 |  |  | 0.43831
2020-03-20 16:00 | 1913 |  |  | 0.082699
2020-03-20 17:00 | 1914 |  |  | 0.11247
2020-03-20 18:00 | 1915 |  |  | 0.003308
2020-03-20 19:00 | 1916 |  |  | 0
2020-03-20 20:00 | 1917 |  |  | 0
2020-03-20 21:00 | 1918 |  |  | 0
2020-03-20 22:00 | 1919 |  |  | 0
2020-03-20 23:00 | 1920 |  |  | 0
2020-03-21 | 1921 |  |  | 0
2020-03-21 01:00 | 1922 |  |  | 0
2020-03-21 02:00 | 1923 |  |  | 0
2020-03-21 03:00 | 1924 |  |  | 0
2020-03-21 04:00 | 1925 |  |  | 0
2020-03-21 05:00 | 1926 |  |  | 0
2020-03-21 06:00 | 1927 |  |  | 0
2020-03-21 07:00 | 1928 |  |  | 0.02481
2020-03-21 08:00 | 1929 |  |  | 0.17201
2020-03-21 09:00 | 1930 |  |  | 0.35065
2020-03-21 10:00 | 1931 |  |  | 0.5177
2020-03-21 11:00 | 1932 |  |  | 0.60701
2020-03-21 12:00 | 1933 |  |  | 0.68971
2020-03-21 13:00 | 1934 |  |  | 0.71121
2020-03-21 14:00 | 1935 |  |  | 0.64671
2020-03-21 15:00 | 1936 |  |  | 0.55078
2020-03-21 16:00 | 1937 |  |  | 0.3738
2020-03-21 17:00 | 1938 |  |  | 0.12736
2020-03-21 18:00 | 1939 |  |  | 0
2020-03-21 19:00 | 1940 |  |  | 0
2020-03-21 20:00 | 1941 |  |  | 0
2020-03-21 21:00 | 1942 |  |  | 0
2020-03-21 22:00 | 1943 |  |  | 0
2020-03-21 23:00 | 1944 |  |  | 0
2020-03-22 | 1945 |  |  | 0
2020-03-22 01:00 | 1946 |  |  | 0
2020-03-22 02:00 | 1947 |  |  | 0
2020-03-22 03:00 | 1948 |  |  | 0
2020-03-22 04:00 | 1949 |  |  | 0
2020-03-22 05:00 | 1950 |  |  | 0
2020-03-22 06:00 | 1951 |  |  | 0
2020-03-22 07:00 | 1952 |  |  | 0.028118
2020-03-22 08:00 | 1953 |  |  | 0.092623
2020-03-22 09:00 | 1954 |  |  | 0.084353
2020-03-22 10:00 | 1955 |  |  | 0.081045
2020-03-22 11:00 | 1956 |  |  | 0.029772
2020-03-22 12:00 | 1957 |  |  | 0.062851
2020-03-22 13:00 | 1958 |  |  | 0.11578
2020-03-22 14:00 | 1959 |  |  | 0.18194
2020-03-22 15:00 | 1960 |  |  | 0.11082
2020-03-22 16:00 | 1961 |  |  | 0.099239
2020-03-22 17:00 | 1962 |  |  | 0.047966
2020-03-22 18:00 | 1963 |  |  | 0
2020-03-22 19:00 | 1964 |  |  | 0
2020-03-22 20:00 | 1965 |  |  | 0
2020-03-22 21:00 | 1966 |  |  | 0
2020-03-22 22:00 | 1967 |  |  | 0
2020-03-22 23:00 | 1968 |  |  | 0
2020-03-23 | 1969 |  |  | 0
2020-03-23 01:00 | 1970 |  |  | 0
2020-03-23 02:00 | 1971 |  |  | 0
2020-03-23 03:00 | 1972 |  |  | 0
2020-03-23 04:00 | 1973 |  |  | 0
2020-03-23 05:00 | 1974 |  |  | 0
2020-03-23 06:00 | 1975 |  |  | 0
2020-03-23 07:00 | 1976 |  |  | 0
2020-03-23 08:00 | 1977 |  |  | 0.018194
2020-03-23 09:00 | 1978 |  |  | 0.077737
2020-03-23 10:00 | 1979 |  |  | 0.14059
2020-03-23 11:00 | 1980 |  |  | 0.14059
2020-03-23 12:00 | 1981 |  |  | 0.17201
2020-03-23 13:00 | 1982 |  |  | 0.22825
2020-03-23 14:00 | 1983 |  |  | 0.21006
2020-03-23 15:00 | 1984 |  |  | 0.15051
2020-03-23 16:00 | 1985 |  |  | 0.11909
2020-03-23 17:00 | 1986 |  |  | 0.02481
2020-03-23 18:00 | 1987 |  |  | 0
2020-03-23 19:00 | 1988 |  |  | 0
2020-03-23 20:00 | 1989 |  |  | 0
2020-03-23 21:00 | 1990 |  |  | 0
2020-03-23 22:00 | 1991 |  |  | 0
2020-03-23 23:00 | 1992 |  |  | 0
2020-03-24 | 1993 |  |  | 0
2020-03-24 01:00 | 1994 |  |  | 0
2020-03-24 02:00 | 1995 |  |  | 0
2020-03-24 03:00 | 1996 |  |  | 0
2020-03-24 04:00 | 1997 |  |  | 0
2020-03-24 05:00 | 1998 |  |  | 0
2020-03-24 06:00 | 1999 |  |  | 0
2020-03-24 07:00 | 2000 |  |  | 0
2020-03-24 08:00 | 2001 |  |  | 0.076083
2020-03-24 09:00 | 2002 |  |  | 0.3738
2020-03-24 10:00 | 2003 |  |  | 0.50943
2020-03-24 11:00 | 2004 |  |  | 0.58386
2020-03-24 12:00 | 2005 |  |  | 0.73437
2020-03-24 13:00 | 2006 |  |  | 0.77241
2020-03-24 14:00 | 2007 |  |  | 0.73106
2020-03-24 15:00 | 2008 |  |  | 0.63348
2020-03-24 16:00 | 2009 |  |  | 0.47635
2020-03-24 17:00 | 2010 |  |  | 0.21171
2020-03-24 18:00 | 2011 |  |  | 0.013232
2020-03-24 19:00 | 2012 |  |  | 0
2020-03-24 20:00 | 2013 |  |  | 0
2020-03-24 21:00 | 2014 |  |  | 0
2020-03-24 22:00 | 2015 |  |  | 0
2020-03-24 23:00 | 2016 |  |  | 0
2020-03-25 | 2017 |  |  | 0
2020-03-25 01:00 | 2018 |  |  | 0
2020-03-25 02:00 | 2019 |  |  | 0
2020-03-25 03:00 | 2020 |  |  | 0
2020-03-25 04:00 | 2021 |  |  | 0
2020-03-25 05:00 | 2022 |  |  | 0
2020-03-25 06:00 | 2023 |  |  | 0
2020-03-25 07:00 | 2024 |  |  | 0
2020-03-25 08:00 | 2025 |  |  | 0.046312
2020-03-25 09:00 | 2026 |  |  | 0.051274
2020-03-25 10:00 | 2027 |  |  | 0.054582
2020-03-25 11:00 | 2028 |  |  | 0.23156
2020-03-25 12:00 | 2029 |  |  | 0.28779
2020-03-25 13:00 | 2030 |  |  | 0.25968
2020-03-25 14:00 | 2031 |  |  | 0.30764
2020-03-25 15:00 | 2032 |  |  | 0.3308
2020-03-25 16:00 | 2033 |  |  | 0.28614
2020-03-25 17:00 | 2034 |  |  | 0.056236
2020-03-25 18:00 | 2035 |  |  | 0
2020-03-25 19:00 | 2036 |  |  | 0
2020-03-25 20:00 | 2037 |  |  | 0
2020-03-25 21:00 | 2038 |  |  | 0
2020-03-25 22:00 | 2039 |  |  | 0
2020-03-25 23:00 | 2040 |  |  | 0
2020-03-26 | 2041 |  |  | 0
2020-03-26 01:00 | 2042 |  |  | 0
2020-03-26 02:00 | 2043 |  |  | 0
2020-03-26 03:00 | 2044 |  |  | 0
2020-03-26 04:00 | 2045 |  |  | 0
2020-03-26 05:00 | 2046 |  |  | 0
2020-03-26 06:00 | 2047 |  |  | 0
2020-03-26 07:00 | 2048 |  |  | 0.052928
2020-03-26 08:00 | 2049 |  |  | 0.15713
2020-03-26 09:00 | 2050 |  |  | 0.26795
2020-03-26 10:00 | 2051 |  |  | 0.2481
2020-03-26 11:00 | 2052 |  |  | 0.13728
2020-03-26 12:00 | 2053 |  |  | 0.10586
2020-03-26 13:00 | 2054 |  |  | 0.13397
2020-03-26 14:00 | 2055 |  |  | 0.2299
2020-03-26 15:00 | 2056 |  |  | 0.10586
2020-03-26 16:00 | 2057 |  |  | 0.0066159
2020-03-26 17:00 | 2058 |  |  | 0
2020-03-26 18:00 | 2059 |  |  | 0
2020-03-26 19:00 | 2060 |  |  | 0
2020-03-26 20:00 | 2061 |  |  | 0
2020-03-26 21:00 | 2062 |  |  | 0
2020-03-26 22:00 | 2063 |  |  | 0
2020-03-26 23:00 | 2064 |  |  | 0
2020-03-27 | 2065 |  |  | 0
2020-03-27 01:00 | 2066 |  |  | 0
2020-03-27 02:00 | 2067 |  |  | 0
2020-03-27 03:00 | 2068 |  |  | 0
2020-03-27 04:00 | 2069 |  |  | 0
2020-03-27 05:00 | 2070 |  |  | 0
2020-03-27 06:00 | 2071 |  |  | 0
2020-03-27 07:00 | 2072 |  |  | 0
2020-03-27 08:00 | 2073 |  |  | 0.038042
2020-03-27 09:00 | 2074 |  |  | 0.062851
2020-03-27 10:00 | 2075 |  |  | 0.13397
2020-03-27 11:00 | 2076 |  |  | 0.18525
2020-03-27 12:00 | 2077 |  |  | 0.21998
2020-03-27 13:00 | 2078 |  |  | 0.14224
2020-03-27 14:00 | 2079 |  |  | 0.28614
2020-03-27 15:00 | 2080 |  |  | 0.22329
2020-03-27 16:00 | 2081 |  |  | 0.13066
2020-03-27 17:00 | 2082 |  |  | 0
2020-03-27 18:00 | 2083 |  |  | 0
2020-03-27 19:00 | 2084 |  |  | 0
2020-03-27 20:00 | 2085 |  |  | 0
2020-03-27 21:00 | 2086 |  |  | 0
2020-03-27 22:00 | 2087 |  |  | 0
2020-03-27 23:00 | 2088 |  |  | 0
2020-03-28 | 2089 |  |  | 0
2020-03-28 01:00 | 2090 |  |  | 0
2020-03-28 02:00 | 2091 |  |  | 0
2020-03-28 03:00 | 2092 |  |  | 0
2020-03-28 04:00 | 2093 |  |  | 0
2020-03-28 05:00 | 2094 |  |  | 0
2020-03-28 06:00 | 2095 |  |  | 0
2020-03-28 07:00 | 2096 |  |  | 0.051274
2020-03-28 08:00 | 2097 |  |  | 0.19517
2020-03-28 09:00 | 2098 |  |  | 0.3738
2020-03-28 10:00 | 2099 |  |  | 0.52762
2020-03-28 11:00 | 2100 |  |  | 0.64505
2020-03-28 12:00 | 2101 |  |  | 0.71121
2020-03-28 13:00 | 2102 |  |  | 0.70294
2020-03-28 14:00 | 2103 |  |  | 0.67813
2020-03-28 15:00 | 2104 |  |  | 0.5822
2020-03-28 16:00 | 2105 |  |  | 0.42011
2020-03-28 17:00 | 2106 |  |  | 0.18855
2020-03-28 18:00 | 2107 |  |  | 0.0099239
2020-03-28 19:00 | 2108 |  |  | 0
2020-03-28 20:00 | 2109 |  |  | 0
2020-03-28 21:00 | 2110 |  |  | 0
2020-03-28 22:00 | 2111 |  |  | 0
2020-03-28 23:00 | 2112 |  |  | 0
2020-03-29 | 2113 |  |  | 0
2020-03-29 01:00 | 2114 |  |  | 0
2020-03-29 02:00 | 2115 |  |  | 0
2020-03-29 03:00 | 2116 |  |  | 0
2020-03-29 04:00 | 2117 |  |  | 0
2020-03-29 05:00 | 2118 |  |  | 0
2020-03-29 06:00 | 2119 |  |  | 0
2020-03-29 07:00 | 2120 |  |  | 0.03308
2020-03-29 08:00 | 2121 |  |  | 0.12736
2020-03-29 09:00 | 2122 |  |  | 0.32087
2020-03-29 10:00 | 2123 |  |  | 0.35395
2020-03-29 11:00 | 2124 |  |  | 0.44327
2020-03-29 12:00 | 2125 |  |  | 0.37049
2020-03-29 13:00 | 2126 |  |  | 0.46146
2020-03-29 14:00 | 2127 |  |  | 0.2911
2020-03-29 15:00 | 2128 |  |  | 0.23321
2020-03-29 16:00 | 2129 |  |  | 0.16705
2020-03-29 17:00 | 2130 |  |  | 0.046312
2020-03-29 18:00 | 2131 |  |  | 0
2020-03-29 19:00 | 2132 |  |  | 0
2020-03-29 20:00 | 2133 |  |  | 0
2020-03-29 21:00 | 2134 |  |  | 0
2020-03-29 22:00 | 2135 |  |  | 0
2020-03-29 23:00 | 2136 |  |  | 0
2020-03-30 | 2137 |  |  | 0
2020-03-30 01:00 | 2138 |  |  | 0
2020-03-30 02:00 | 2139 |  |  | 0
2020-03-30 03:00 | 2140 |  |  | 0
2020-03-30 04:00 | 2141 |  |  | 0
2020-03-30 05:00 | 2142 |  |  | 0
2020-03-30 06:00 | 2143 |  |  | 0
2020-03-30 07:00 | 2144 |  |  | 0
2020-03-30 08:00 | 2145 |  |  | 0.0082699
2020-03-30 09:00 | 2146 |  |  | 0.051274
2020-03-30 10:00 | 2147 |  |  | 0.2911
2020-03-30 11:00 | 2148 |  |  | 0.25802
2020-03-30 12:00 | 2149 |  |  | 0.34238
2020-03-30 13:00 | 2150 |  |  | 0.20179
2020-03-30 14:00 | 2151 |  |  | 0.37049
2020-03-30 15:00 | 2152 |  |  | 0.24644
2020-03-30 16:00 | 2153 |  |  | 0.18194
2020-03-30 17:00 | 2154 |  |  | 0.028118
2020-03-30 18:00 | 2155 |  |  | 0
2020-03-30 19:00 | 2156 |  |  | 0
2020-03-30 20:00 | 2157 |  |  | 0
2020-03-30 21:00 | 2158 |  |  | 0
2020-03-30 22:00 | 2159 |  |  | 0
2020-03-30 23:00 | 2160 |  |  | 0
2020-03-31 | 2161 |  |  | 0
2020-03-31 01:00 | 2162 |  |  | 0
2020-03-31 02:00 | 2163 |  |  | 0
2020-03-31 03:00 | 2164 |  |  | 0
2020-03-31 04:00 | 2165 |  |  | 0
2020-03-31 05:00 | 2166 |  |  | 0
2020-03-31 06:00 | 2167 |  |  | 0
2020-03-31 07:00 | 2168 |  |  | 0
2020-03-31 08:00 | 2169 |  |  | 0.026464
2020-03-31 09:00 | 2170 |  |  | 0.089315
2020-03-31 10:00 | 2171 |  |  | 0.13397
2020-03-31 11:00 | 2172 |  |  | 0.11413
2020-03-31 12:00 | 2173 |  |  | 0.15217
2020-03-31 13:00 | 2174 |  |  | 0.27456
2020-03-31 14:00 | 2175 |  |  | 0.30764
2020-03-31 15:00 | 2176 |  |  | 0.28614
2020-03-31 16:00 | 2177 |  |  | 0.089315
2020-03-31 17:00 | 2178 |  |  | 0
2020-03-31 18:00 | 2179 |  |  | 0
2020-03-31 19:00 | 2180 |  |  | 0
2020-03-31 20:00 | 2181 |  |  | 0
2020-03-31 21:00 | 2182 |  |  | 0
2020-03-31 22:00 | 2183 |  |  | 0
2020-03-31 23:00 | 2184 |  |  | 0
2020-04-01 | 2185 |  |  | 0
2020-04-01 01:00 | 2186 |  |  | 0
2020-04-01 02:00 | 2187 |  |  | 0
2020-04-01 03:00 | 2188 |  |  | 0
2020-04-01 04:00 | 2189 |  |  | 0
2020-04-01 05:00 | 2190 |  |  | 0
2020-04-01 06:00 | 2191 |  |  | 0
2020-04-01 07:00 | 2192 |  |  | 0
2020-04-01 08:00 | 2193 |  |  | 0.051274
2020-04-01 09:00 | 2194 |  |  | 0.13232
2020-04-01 10:00 | 2195 |  |  | 0.16374
2020-04-01 11:00 | 2196 |  |  | 0.26629
2020-04-01 12:00 | 2197 |  |  | 0.42177
2020-04-01 13:00 | 2198 |  |  | 0.37876
2020-04-01 14:00 | 2199 |  |  | 0.33411
2020-04-01 15:00 | 2200 |  |  | 0.26795
2020-04-01 16:00 | 2201 |  |  | 0.40853
2020-04-01 17:00 | 2202 |  |  | 0.21006
2020-04-01 18:00 | 2203 |  |  | 0.018194
2020-04-01 19:00 | 2204 |  |  | 0
2020-04-01 20:00 | 2205 |  |  | 0
2020-04-01 21:00 | 2206 |  |  | 0
2020-04-01 22:00 | 2207 |  |  | 0
2020-04-01 23:00 | 2208 |  |  | 0
2020-04-02 | 2209 |  |  | 0
2020-04-02 01:00 | 2210 |  |  | 0
2020-04-02 02:00 | 2211 |  |  | 0
2020-04-02 03:00 | 2212 |  |  | 0
2020-04-02 04:00 | 2213 |  |  | 0
2020-04-02 05:00 | 2214 |  |  | 0
2020-04-02 06:00 | 2215 |  |  | 0
2020-04-02 07:00 | 2216 |  |  | 0.059543
2020-04-02 08:00 | 2217 |  |  | 0.21998
2020-04-02 09:00 | 2218 |  |  | 0.4135
2020-04-02 10:00 | 2219 |  |  | 0.57393
2020-04-02 11:00 | 2220 |  |  | 0.70129
2020-04-02 12:00 | 2221 |  |  | 0.73437
2020-04-02 13:00 | 2222 |  |  | 0.73602
2020-04-02 14:00 | 2223 |  |  | 0.70791
2020-04-02 15:00 | 2224 |  |  | 0.6004
2020-04-02 16:00 | 2225 |  |  | 0.435
2020-04-02 17:00 | 2226 |  |  | 0.21336
2020-04-02 18:00 | 2227 |  |  | 0.019848
2020-04-02 19:00 | 2228 |  |  | 0
2020-04-02 20:00 | 2229 |  |  | 0
2020-04-02 21:00 | 2230 |  |  | 0
2020-04-02 22:00 | 2231 |  |  | 0
2020-04-02 23:00 | 2232 |  |  | 0
2020-04-03 | 2233 |  |  | 0
2020-04-03 01:00 | 2234 |  |  | 0
2020-04-03 02:00 | 2235 |  |  | 0
2020-04-03 03:00 | 2236 |  |  | 0
2020-04-03 04:00 | 2237 |  |  | 0
2020-04-03 05:00 | 2238 |  |  | 0
2020-04-03 06:00 | 2239 |  |  | 0
2020-04-03 07:00 | 2240 |  |  | 0.066159
2020-04-03 08:00 | 2241 |  |  | 0.21502
2020-04-03 09:00 | 2242 |  |  | 0.39199
2020-04-03 10:00 | 2243 |  |  | 0.55905
2020-04-03 11:00 | 2244 |  |  | 0.6649
2020-04-03 12:00 | 2245 |  |  | 0.70294
2020-04-03 13:00 | 2246 |  |  | 0.71121
2020-04-03 14:00 | 2247 |  |  | 0.65829
2020-04-03 15:00 | 2248 |  |  | 0.53589
2020-04-03 16:00 | 2249 |  |  | 0.41846
2020-04-03 17:00 | 2250 |  |  | 0.20179
2020-04-03 18:00 | 2251 |  |  | 0.02481
2020-04-03 19:00 | 2252 |  |  | 0
2020-04-03 20:00 | 2253 |  |  | 0
2020-04-03 21:00 | 2254 |  |  | 0
2020-04-03 22:00 | 2255 |  |  | 0
2020-04-03 23:00 | 2256 |  |  | 0
2020-04-04 | 2257 |  |  | 0
2020-04-04 01:00 | 2258 |  |  | 0
2020-04-04 02:00 | 2259 |  |  | 0
2020-04-04 03:00 | 2260 |  |  | 0
2020-04-04 04:00 | 2261 |  |  | 0
2020-04-04 05:00 | 2262 |  |  | 0
2020-04-04 06:00 | 2263 |  |  | 0
2020-04-04 07:00 | 2264 |  |  | 0.066159
2020-04-04 08:00 | 2265 |  |  | 0.21171
2020-04-04 09:00 | 2266 |  |  | 0.3953
2020-04-04 10:00 | 2267 |  |  | 0.55574
2020-04-04 11:00 | 2268 |  |  | 0.65332
2020-04-04 12:00 | 2269 |  |  | 0.71121
2020-04-04 13:00 | 2270 |  |  | 0.71121
2020-04-04 14:00 | 2271 |  |  | 0.68971
2020-04-04 15:00 | 2272 |  |  | 0.56566
2020-04-04 16:00 | 2273 |  |  | 0.41184
2020-04-04 17:00 | 2274 |  |  | 0.19848
2020-04-04 18:00 | 2275 |  |  | 0.021502
2020-04-04 19:00 | 2276 |  |  | 0
2020-04-04 20:00 | 2277 |  |  | 0
2020-04-04 21:00 | 2278 |  |  | 0
2020-04-04 22:00 | 2279 |  |  | 0
2020-04-04 23:00 | 2280 |  |  | 0
2020-04-05 | 2281 |  |  | 0
2020-04-05 01:00 | 2282 |  |  | 0
2020-04-05 02:00 | 2283 |  |  | 0
2020-04-05 03:00 | 2284 |  |  | 0
2020-04-05 04:00 | 2285 |  |  | 0
2020-04-05 05:00 | 2286 |  |  | 0
2020-04-05 06:00 | 2287 |  |  | 0.0066159
2020-04-05 07:00 | 2288 |  |  | 0.086007
2020-04-05 08:00 | 2289 |  |  | 0.19517
2020-04-05 09:00 | 2290 |  |  | 0.36553
2020-04-05 10:00 | 2291 |  |  | 0.47635
2020-04-05 11:00 | 2292 |  |  | 0.6831
2020-04-05 12:00 | 2293 |  |  | 0.71121
2020-04-05 13:00 | 2294 |  |  | 0.71121
2020-04-05 14:00 | 2295 |  |  | 0.69137
2020-04-05 15:00 | 2296 |  |  | 0.59047
2020-04-05 16:00 | 2297 |  |  | 0.43334
2020-04-05 17:00 | 2298 |  |  | 0.22163
2020-04-05 18:00 | 2299 |  |  | 0.028118
2020-04-05 19:00 | 2300 |  |  | 0
2020-04-05 20:00 | 2301 |  |  | 0
2020-04-05 21:00 | 2302 |  |  | 0
2020-04-05 22:00 | 2303 |  |  | 0
2020-04-05 23:00 | 2304 |  |  | 0
2020-04-06 | 2305 |  |  | 0
2020-04-06 01:00 | 2306 |  |  | 0
2020-04-06 02:00 | 2307 |  |  | 0
2020-04-06 03:00 | 2308 |  |  | 0
2020-04-06 04:00 | 2309 |  |  | 0
2020-04-06 05:00 | 2310 |  |  | 0
2020-04-06 06:00 | 2311 |  |  | 0
2020-04-06 07:00 | 2312 |  |  | 0.061197
2020-04-06 08:00 | 2313 |  |  | 0.22163
2020-04-06 09:00 | 2314 |  |  | 0.41019
2020-04-06 10:00 | 2315 |  |  | 0.5607
2020-04-06 11:00 | 2316 |  |  | 0.66821
2020-04-06 12:00 | 2317 |  |  | 0.71121
2020-04-06 13:00 | 2318 |  |  | 0.70294
2020-04-06 14:00 | 2319 |  |  | 0.6831
2020-04-06 15:00 | 2320 |  |  | 0.57228
2020-04-06 16:00 | 2321 |  |  | 0.4135
2020-04-06 17:00 | 2322 |  |  | 0.21833
2020-04-06 18:00 | 2323 |  |  | 0.029772
2020-04-06 19:00 | 2324 |  |  | 0
2020-04-06 20:00 | 2325 |  |  | 0
2020-04-06 21:00 | 2326 |  |  | 0
2020-04-06 22:00 | 2327 |  |  | 0
2020-04-06 23:00 | 2328 |  |  | 0
2020-04-07 | 2329 |  |  | 0
2020-04-07 01:00 | 2330 |  |  | 0
2020-04-07 02:00 | 2331 |  |  | 0
2020-04-07 03:00 | 2332 |  |  | 0
2020-04-07 04:00 | 2333 |  |  | 0
2020-04-07 05:00 | 2334 |  |  | 0
2020-04-07 06:00 | 2335 |  |  | 0
2020-04-07 07:00 | 2336 |  |  | 0.05789
2020-04-07 08:00 | 2337 |  |  | 0.2299
2020-04-07 09:00 | 2338 |  |  | 0.41184
2020-04-07 10:00 | 2339 |  |  | 0.57063
2020-04-07 11:00 | 2340 |  |  | 0.68806
2020-04-07 12:00 | 2341 |  |  | 0.71452
2020-04-07 13:00 | 2342 |  |  | 0.71948
2020-04-07 14:00 | 2343 |  |  | 0.7046
2020-04-07 15:00 | 2344 |  |  | 0.59874
2020-04-07 16:00 | 2345 |  |  | 0.44658
2020-04-07 17:00 | 2346 |  |  | 0.23983
2020-04-07 18:00 | 2347 |  |  | 0.044658
2020-04-07 19:00 | 2348 |  |  | 0
2020-04-07 20:00 | 2349 |  |  | 0
2020-04-07 21:00 | 2350 |  |  | 0
2020-04-07 22:00 | 2351 |  |  | 0
2020-04-07 23:00 | 2352 |  |  | 0
2020-04-08 | 2353 |  |  | 0
2020-04-08 01:00 | 2354 |  |  | 0
2020-04-08 02:00 | 2355 |  |  | 0
2020-04-08 03:00 | 2356 |  |  | 0
2020-04-08 04:00 | 2357 |  |  | 0
2020-04-08 05:00 | 2358 |  |  | 0
2020-04-08 06:00 | 2359 |  |  | 0
2020-04-08 07:00 | 2360 |  |  | 0.061197
2020-04-08 08:00 | 2361 |  |  | 0.22494
2020-04-08 09:00 | 2362 |  |  | 0.4135
2020-04-08 10:00 | 2363 |  |  | 0.56566
2020-04-08 11:00 | 2364 |  |  | 0.67317
2020-04-08 12:00 | 2365 |  |  | 0.71121
2020-04-08 13:00 | 2366 |  |  | 0.71121
2020-04-08 14:00 | 2367 |  |  | 0.69964
2020-04-08 15:00 | 2368 |  |  | 0.58882
2020-04-08 16:00 | 2369 |  |  | 0.44823
2020-04-08 17:00 | 2370 |  |  | 0.23817
2020-04-08 18:00 | 2371 |  |  | 0.038042
2020-04-08 19:00 | 2372 |  |  | 0
2020-04-08 20:00 | 2373 |  |  | 0
2020-04-08 21:00 | 2374 |  |  | 0
2020-04-08 22:00 | 2375 |  |  | 0
2020-04-08 23:00 | 2376 |  |  | 0
2020-04-09 | 2377 |  |  | 0
2020-04-09 01:00 | 2378 |  |  | 0
2020-04-09 02:00 | 2379 |  |  | 0
2020-04-09 03:00 | 2380 |  |  | 0
2020-04-09 04:00 | 2381 |  |  | 0
2020-04-09 05:00 | 2382 |  |  | 0
2020-04-09 06:00 | 2383 |  |  | 0
2020-04-09 07:00 | 2384 |  |  | 0.05789
2020-04-09 08:00 | 2385 |  |  | 0.2299
2020-04-09 09:00 | 2386 |  |  | 0.42177
2020-04-09 10:00 | 2387 |  |  | 0.57228
2020-04-09 11:00 | 2388 |  |  | 0.67317
2020-04-09 12:00 | 2389 |  |  | 0.71121
2020-04-09 13:00 | 2390 |  |  | 0.71452
2020-04-09 14:00 | 2391 |  |  | 0.69633
2020-04-09 15:00 | 2392 |  |  | 0.59378
2020-04-09 16:00 | 2393 |  |  | 0.44988
2020-04-09 17:00 | 2394 |  |  | 0.23321
2020-04-09 18:00 | 2395 |  |  | 0.044658
2020-04-09 19:00 | 2396 |  |  | 0
2020-04-09 20:00 | 2397 |  |  | 0
2020-04-09 21:00 | 2398 |  |  | 0
2020-04-09 22:00 | 2399 |  |  | 0
2020-04-09 23:00 | 2400 |  |  | 0
2020-04-10 | 2401 |  |  | 0
2020-04-10 01:00 | 2402 |  |  | 0
2020-04-10 02:00 | 2403 |  |  | 0
2020-04-10 03:00 | 2404 |  |  | 0
2020-04-10 04:00 | 2405 |  |  | 0
2020-04-10 05:00 | 2406 |  |  | 0
2020-04-10 06:00 | 2407 |  |  | 0
2020-04-10 07:00 | 2408 |  |  | 0.059543
2020-04-10 08:00 | 2409 |  |  | 0.23487
2020-04-10 09:00 | 2410 |  |  | 0.42507
2020-04-10 10:00 | 2411 |  |  | 0.56566
2020-04-10 11:00 | 2412 |  |  | 0.68971
2020-04-10 12:00 | 2413 |  |  | 0.71121
2020-04-10 13:00 | 2414 |  |  | 0.7046
2020-04-10 14:00 | 2415 |  |  | 0.70625
2020-04-10 15:00 | 2416 |  |  | 0.60536
2020-04-10 16:00 | 2417 |  |  | 0.46312
2020-04-10 17:00 | 2418 |  |  | 0.25637
2020-04-10 18:00 | 2419 |  |  | 0.04962
2020-04-10 19:00 | 2420 |  |  | 0
2020-04-10 20:00 | 2421 |  |  | 0
2020-04-10 21:00 | 2422 |  |  | 0
2020-04-10 22:00 | 2423 |  |  | 0
2020-04-10 23:00 | 2424 |  |  | 0
2020-04-11 | 2425 |  |  | 0
2020-04-11 01:00 | 2426 |  |  | 0
2020-04-11 02:00 | 2427 |  |  | 0
2020-04-11 03:00 | 2428 |  |  | 0
2020-04-11 04:00 | 2429 |  |  | 0
2020-04-11 05:00 | 2430 |  |  | 0
2020-04-11 06:00 | 2431 |  |  | 0
2020-04-11 07:00 | 2432 |  |  | 0.064505
2020-04-11 08:00 | 2433 |  |  | 0.23487
2020-04-11 09:00 | 2434 |  |  | 0.42177
2020-04-11 10:00 | 2435 |  |  | 0.57228
2020-04-11 11:00 | 2436 |  |  | 0.69467
2020-04-11 12:00 | 2437 |  |  | 0.70294
2020-04-11 13:00 | 2438 |  |  | 0.71287
2020-04-11 14:00 | 2439 |  |  | 0.70294
2020-04-11 15:00 | 2440 |  |  | 0.59874
2020-04-11 16:00 | 2441 |  |  | 0.45815
2020-04-11 17:00 | 2442 |  |  | 0.25471
2020-04-11 18:00 | 2443 |  |  | 0.051274
2020-04-11 19:00 | 2444 |  |  | 0
2020-04-11 20:00 | 2445 |  |  | 0
2020-04-11 21:00 | 2446 |  |  | 0
2020-04-11 22:00 | 2447 |  |  | 0
2020-04-11 23:00 | 2448 |  |  | 0
2020-04-12 | 2449 |  |  | 0
2020-04-12 01:00 | 2450 |  |  | 0
2020-04-12 02:00 | 2451 |  |  | 0
2020-04-12 03:00 | 2452 |  |  | 0
2020-04-12 04:00 | 2453 |  |  | 0
2020-04-12 05:00 | 2454 |  |  | 0
2020-04-12 06:00 | 2455 |  |  | 0
2020-04-12 07:00 | 2456 |  |  | 0.064505
2020-04-12 08:00 | 2457 |  |  | 0.23817
2020-04-12 09:00 | 2458 |  |  | 0.44161
2020-04-12 10:00 | 2459 |  |  | 0.59047
2020-04-12 11:00 | 2460 |  |  | 0.69467
2020-04-12 12:00 | 2461 |  |  | 0.70129
2020-04-12 13:00 | 2462 |  |  | 0.68475
2020-04-12 14:00 | 2463 |  |  | 0.45319
2020-04-12 15:00 | 2464 |  |  | 0.46477
2020-04-12 16:00 | 2465 |  |  | 0.29276
2020-04-12 17:00 | 2466 |  |  | 0.21667
2020-04-12 18:00 | 2467 |  |  | 0.039696
2020-04-12 19:00 | 2468 |  |  | 0
2020-04-12 20:00 | 2469 |  |  | 0
2020-04-12 21:00 | 2470 |  |  | 0
2020-04-12 22:00 | 2471 |  |  | 0
2020-04-12 23:00 | 2472 |  |  | 0
2020-04-13 | 2473 |  |  | 0
2020-04-13 01:00 | 2474 |  |  | 0
2020-04-13 02:00 | 2475 |  |  | 0
2020-04-13 03:00 | 2476 |  |  | 0
2020-04-13 04:00 | 2477 |  |  | 0
2020-04-13 05:00 | 2478 |  |  | 0
2020-04-13 06:00 | 2479 |  |  | 0.003308
2020-04-13 07:00 | 2480 |  |  | 0.071121
2020-04-13 08:00 | 2481 |  |  | 0.23817
2020-04-13 09:00 | 2482 |  |  | 0.34734
2020-04-13 10:00 | 2483 |  |  | 0.51935
2020-04-13 11:00 | 2484 |  |  | 0.55739
2020-04-13 12:00 | 2485 |  |  | 0.66325
2020-04-13 13:00 | 2486 |  |  | 0.71948
2020-04-13 14:00 | 2487 |  |  | 0.38372
2020-04-13 15:00 | 2488 |  |  | 0.2481
2020-04-13 16:00 | 2489 |  |  | 0.16044
2020-04-13 17:00 | 2490 |  |  | 0.090969
2020-04-13 18:00 | 2491 |  |  | 0
2020-04-13 19:00 | 2492 |  |  | 0
2020-04-13 20:00 | 2493 |  |  | 0
2020-04-13 21:00 | 2494 |  |  | 0
2020-04-13 22:00 | 2495 |  |  | 0
2020-04-13 23:00 | 2496 |  |  | 0
2020-04-14 | 2497 |  |  | 0
2020-04-14 01:00 | 2498 |  |  | 0
2020-04-14 02:00 | 2499 |  |  | 0
2020-04-14 03:00 | 2500 |  |  | 0
2020-04-14 04:00 | 2501 |  |  | 0
2020-04-14 05:00 | 2502 |  |  | 0
2020-04-14 06:00 | 2503 |  |  | 0
2020-04-14 07:00 | 2504 |  |  | 0.069467
2020-04-14 08:00 | 2505 |  |  | 0.23983
2020-04-14 09:00 | 2506 |  |  | 0.43169
2020-04-14 10:00 | 2507 |  |  | 0.56897
2020-04-14 11:00 | 2508 |  |  | 0.68806
2020-04-14 12:00 | 2509 |  |  | 0.71121
2020-04-14 13:00 | 2510 |  |  | 0.70294
2020-04-14 14:00 | 2511 |  |  | 0.69467
2020-04-14 15:00 | 2512 |  |  | 0.59378
2020-04-14 16:00 | 2513 |  |  | 0.44658
2020-04-14 17:00 | 2514 |  |  | 0.25802
2020-04-14 18:00 | 2515 |  |  | 0.056236
2020-04-14 19:00 | 2516 |  |  | 0
2020-04-14 20:00 | 2517 |  |  | 0
2020-04-14 21:00 | 2518 |  |  | 0
2020-04-14 22:00 | 2519 |  |  | 0
2020-04-14 23:00 | 2520 |  |  | 0
2020-04-15 | 2521 |  |  | 0
2020-04-15 01:00 | 2522 |  |  | 0
2020-04-15 02:00 | 2523 |  |  | 0
2020-04-15 03:00 | 2524 |  |  | 0
2020-04-15 04:00 | 2525 |  |  | 0
2020-04-15 05:00 | 2526 |  |  | 0
2020-04-15 06:00 | 2527 |  |  | 0
2020-04-15 07:00 | 2528 |  |  | 0.056236
2020-04-15 08:00 | 2529 |  |  | 0.14555
2020-04-15 09:00 | 2530 |  |  | 0.26795
2020-04-15 10:00 | 2531 |  |  | 0.37711
2020-04-15 11:00 | 2532 |  |  | 0.58717
2020-04-15 12:00 | 2533 |  |  | 0.74264
2020-04-15 13:00 | 2534 |  |  | 0.73933
2020-04-15 14:00 | 2535 |  |  | 0.71121
2020-04-15 15:00 | 2536 |  |  | 0.61859
2020-04-15 16:00 | 2537 |  |  | 0.478
2020-04-15 17:00 | 2538 |  |  | 0.27952
2020-04-15 18:00 | 2539 |  |  | 0.062851
2020-04-15 19:00 | 2540 |  |  | 0
2020-04-15 20:00 | 2541 |  |  | 0
2020-04-15 21:00 | 2542 |  |  | 0
2020-04-15 22:00 | 2543 |  |  | 0
2020-04-15 23:00 | 2544 |  |  | 0
2020-04-16 | 2545 |  |  | 0
2020-04-16 01:00 | 2546 |  |  | 0
2020-04-16 02:00 | 2547 |  |  | 0
2020-04-16 03:00 | 2548 |  |  | 0
2020-04-16 04:00 | 2549 |  |  | 0
2020-04-16 05:00 | 2550 |  |  | 0
2020-04-16 06:00 | 2551 |  |  | 0
2020-04-16 07:00 | 2552 |  |  | 0.082699
2020-04-16 08:00 | 2553 |  |  | 0.22825
2020-04-16 09:00 | 2554 |  |  | 0.34238
2020-04-16 10:00 | 2555 |  |  | 0.54416
2020-04-16 11:00 | 2556 |  |  | 0.52431
2020-04-16 12:00 | 2557 |  |  | 0.54912
2020-04-16 13:00 | 2558 |  |  | 0.45981
2020-04-16 14:00 | 2559 |  |  | 0.61032
2020-04-16 15:00 | 2560 |  |  | 0.61032
2020-04-16 16:00 | 2561 |  |  | 0.47139
2020-04-16 17:00 | 2562 |  |  | 0.25968
2020-04-16 18:00 | 2563 |  |  | 0.054582
2020-04-16 19:00 | 2564 |  |  | 0
2020-04-16 20:00 | 2565 |  |  | 0
2020-04-16 21:00 | 2566 |  |  | 0
2020-04-16 22:00 | 2567 |  |  | 0
2020-04-16 23:00 | 2568 |  |  | 0
2020-04-17 | 2569 |  |  | 0
2020-04-17 01:00 | 2570 |  |  | 0
2020-04-17 02:00 | 2571 |  |  | 0
2020-04-17 03:00 | 2572 |  |  | 0
2020-04-17 04:00 | 2573 |  |  | 0
2020-04-17 05:00 | 2574 |  |  | 0
2020-04-17 06:00 | 2575 |  |  | 0
2020-04-17 07:00 | 2576 |  |  | 0.087661
2020-04-17 08:00 | 2577 |  |  | 0.24644
2020-04-17 09:00 | 2578 |  |  | 0.45319
2020-04-17 10:00 | 2579 |  |  | 0.53258
2020-04-17 11:00 | 2580 |  |  | 0.5822
2020-04-17 12:00 | 2581 |  |  | 0.48627
2020-04-17 13:00 | 2582 |  |  | 0.43334
2020-04-17 14:00 | 2583 |  |  | 0.33411
2020-04-17 15:00 | 2584 |  |  | 0.35726
2020-04-17 16:00 | 2585 |  |  | 0.28614
2020-04-17 17:00 | 2586 |  |  | 0.090969
2020-04-17 18:00 | 2587 |  |  | 0.003308
2020-04-17 19:00 | 2588 |  |  | 0
2020-04-17 20:00 | 2589 |  |  | 0
2020-04-17 21:00 | 2590 |  |  | 0
2020-04-17 22:00 | 2591 |  |  | 0
2020-04-17 23:00 | 2592 |  |  | 0
2020-04-18 | 2593 |  |  | 0
2020-04-18 01:00 | 2594 |  |  | 0
2020-04-18 02:00 | 2595 |  |  | 0
2020-04-18 03:00 | 2596 |  |  | 0
2020-04-18 04:00 | 2597 |  |  | 0
2020-04-18 05:00 | 2598 |  |  | 0
2020-04-18 06:00 | 2599 |  |  | 0.021502
2020-04-18 07:00 | 2600 |  |  | 0.097585
2020-04-18 08:00 | 2601 |  |  | 0.24479
2020-04-18 09:00 | 2602 |  |  | 0.36553
2020-04-18 10:00 | 2603 |  |  | 0.52266
2020-04-18 11:00 | 2604 |  |  | 0.4962
2020-04-18 12:00 | 2605 |  |  | 0.5789
2020-04-18 13:00 | 2606 |  |  | 0.35561
2020-04-18 14:00 | 2607 |  |  | 0.59543
2020-04-18 15:00 | 2608 |  |  | 0.54085
2020-04-18 16:00 | 2609 |  |  | 0.43334
2020-04-18 17:00 | 2610 |  |  | 0.21833
2020-04-18 18:00 | 2611 |  |  | 0.051274
2020-04-18 19:00 | 2612 |  |  | 0
2020-04-18 20:00 | 2613 |  |  | 0
2020-04-18 21:00 | 2614 |  |  | 0
2020-04-18 22:00 | 2615 |  |  | 0
2020-04-18 23:00 | 2616 |  |  | 0
2020-04-19 | 2617 |  |  | 0
2020-04-19 01:00 | 2618 |  |  | 0
2020-04-19 02:00 | 2619 |  |  | 0
2020-04-19 03:00 | 2620 |  |  | 0
2020-04-19 04:00 | 2621 |  |  | 0
2020-04-19 05:00 | 2622 |  |  | 0
2020-04-19 06:00 | 2623 |  |  | 0.026464
2020-04-19 07:00 | 2624 |  |  | 0.11743
2020-04-19 08:00 | 2625 |  |  | 0.25141
2020-04-19 09:00 | 2626 |  |  | 0.29772
2020-04-19 10:00 | 2627 |  |  | 0.28283
2020-04-19 11:00 | 2628 |  |  | 0.25306
2020-04-19 12:00 | 2629 |  |  | 0.1472
2020-04-19 13:00 | 2630 |  |  | 0.15713
2020-04-19 14:00 | 2631 |  |  | 0.11909
2020-04-19 15:00 | 2632 |  |  | 0.054582
2020-04-19 16:00 | 2633 |  |  | 0.04135
2020-04-19 17:00 | 2634 |  |  | 0.036388
2020-04-19 18:00 | 2635 |  |  | 0
2020-04-19 19:00 | 2636 |  |  | 0
2020-04-19 20:00 | 2637 |  |  | 0
2020-04-19 21:00 | 2638 |  |  | 0
2020-04-19 22:00 | 2639 |  |  | 0
2020-04-19 23:00 | 2640 |  |  | 0
2020-04-20 | 2641 |  |  | 0
2020-04-20 01:00 | 2642 |  |  | 0
2020-04-20 02:00 | 2643 |  |  | 0
2020-04-20 03:00 | 2644 |  |  | 0
2020-04-20 04:00 | 2645 |  |  | 0
2020-04-20 05:00 | 2646 |  |  | 0
2020-04-20 06:00 | 2647 |  |  | 0
2020-04-20 07:00 | 2648 |  |  | 0
2020-04-20 08:00 | 2649 |  |  | 0
2020-04-20 09:00 | 2650 |  |  | 0.0066159
2020-04-20 10:00 | 2651 |  |  | 0.018194
2020-04-20 11:00 | 2652 |  |  | 0.043004
2020-04-20 12:00 | 2653 |  |  | 0.043004
2020-04-20 13:00 | 2654 |  |  | 0.011578
2020-04-20 14:00 | 2655 |  |  | 0.0066159
2020-04-20 15:00 | 2656 |  |  | 0.004962
2020-04-20 16:00 | 2657 |  |  | 0.001654
2020-04-20 17:00 | 2658 |  |  | 0
2020-04-20 18:00 | 2659 |  |  | 0
2020-04-20 19:00 | 2660 |  |  | 0
2020-04-20 20:00 | 2661 |  |  | 0
2020-04-20 21:00 | 2662 |  |  | 0
2020-04-20 22:00 | 2663 |  |  | 0
2020-04-20 23:00 | 2664 |  |  | 0
2020-04-21 | 2665 |  |  | 0
2020-04-21 01:00 | 2666 |  |  | 0
2020-04-21 02:00 | 2667 |  |  | 0
2020-04-21 03:00 | 2668 |  |  | 0
2020-04-21 04:00 | 2669 |  |  | 0
2020-04-21 05:00 | 2670 |  |  | 0
2020-04-21 06:00 | 2671 |  |  | 0
2020-04-21 07:00 | 2672 |  |  | 0.004962
2020-04-21 08:00 | 2673 |  |  | 0.054582
2020-04-21 09:00 | 2674 |  |  | 0.076083
2020-04-21 10:00 | 2675 |  |  | 0.13728
2020-04-21 11:00 | 2676 |  |  | 0.11909
2020-04-21 12:00 | 2677 |  |  | 0.19352
2020-04-21 13:00 | 2678 |  |  | 0.20509
2020-04-21 14:00 | 2679 |  |  | 0.14886
2020-04-21 15:00 | 2680 |  |  | 0.14059
2020-04-21 16:00 | 2681 |  |  | 0.066159
2020-04-21 17:00 | 2682 |  |  | 0.013232
2020-04-21 18:00 | 2683 |  |  | 0
2020-04-21 19:00 | 2684 |  |  | 0
2020-04-21 20:00 | 2685 |  |  | 0
2020-04-21 21:00 | 2686 |  |  | 0
2020-04-21 22:00 | 2687 |  |  | 0
2020-04-21 23:00 | 2688 |  |  | 0
2020-04-22 | 2689 |  |  | 0
2020-04-22 01:00 | 2690 |  |  | 0
2020-04-22 02:00 | 2691 |  |  | 0
2020-04-22 03:00 | 2692 |  |  | 0
2020-04-22 04:00 | 2693 |  |  | 0
2020-04-22 05:00 | 2694 |  |  | 0
2020-04-22 06:00 | 2695 |  |  | 0.018194
2020-04-22 07:00 | 2696 |  |  | 0.1257
2020-04-22 08:00 | 2697 |  |  | 0.28614
2020-04-22 09:00 | 2698 |  |  | 0.42342
2020-04-22 10:00 | 2699 |  |  | 0.6219
2020-04-22 11:00 | 2700 |  |  | 0.72445
2020-04-22 12:00 | 2701 |  |  | 0.80384
2020-04-22 13:00 | 2702 |  |  | 0.79226
2020-04-22 14:00 | 2703 |  |  | 0.72114
2020-04-22 15:00 | 2704 |  |  | 0.65002
2020-04-22 16:00 | 2705 |  |  | 0.50612
2020-04-22 17:00 | 2706 |  |  | 0.30103
2020-04-22 18:00 | 2707 |  |  | 0.086007
2020-04-22 19:00 | 2708 |  |  | 0
2020-04-22 20:00 | 2709 |  |  | 0
2020-04-22 21:00 | 2710 |  |  | 0
2020-04-22 22:00 | 2711 |  |  | 0
2020-04-22 23:00 | 2712 |  |  | 0
2020-04-23 | 2713 |  |  | 0
2020-04-23 01:00 | 2714 |  |  | 0
2020-04-23 02:00 | 2715 |  |  | 0
2020-04-23 03:00 | 2716 |  |  | 0
2020-04-23 04:00 | 2717 |  |  | 0
2020-04-23 05:00 | 2718 |  |  | 0
2020-04-23 06:00 | 2719 |  |  | 0.001654
2020-04-23 07:00 | 2720 |  |  | 0.092623
2020-04-23 08:00 | 2721 |  |  | 0.27787
2020-04-23 09:00 | 2722 |  |  | 0.48296
2020-04-23 10:00 | 2723 |  |  | 0.61363
2020-04-23 11:00 | 2724 |  |  | 0.71618
2020-04-23 12:00 | 2725 |  |  | 0.76249
2020-04-23 13:00 | 2726 |  |  | 0.74595
2020-04-23 14:00 | 2727 |  |  | 0.72114
2020-04-23 15:00 | 2728 |  |  | 0.62024
2020-04-23 16:00 | 2729 |  |  | 0.478
2020-04-23 17:00 | 2730 |  |  | 0.28614
2020-04-23 18:00 | 2731 |  |  | 0.081045
2020-04-23 19:00 | 2732 |  |  | 0
2020-04-23 20:00 | 2733 |  |  | 0
2020-04-23 21:00 | 2734 |  |  | 0
2020-04-23 22:00 | 2735 |  |  | 0
2020-04-23 23:00 | 2736 |  |  | 0
2020-04-24 | 2737 |  |  | 0
2020-04-24 01:00 | 2738 |  |  | 0
2020-04-24 02:00 | 2739 |  |  | 0
2020-04-24 03:00 | 2740 |  |  | 0
2020-04-24 04:00 | 2741 |  |  | 0
2020-04-24 05:00 | 2742 |  |  | 0
2020-04-24 06:00 | 2743 |  |  | 0.01654
2020-04-24 07:00 | 2744 |  |  | 0.099239
2020-04-24 08:00 | 2745 |  |  | 0.27952
2020-04-24 09:00 | 2746 |  |  | 0.46973
2020-04-24 10:00 | 2747 |  |  | 0.62024
2020-04-24 11:00 | 2748 |  |  | 0.71287
2020-04-24 12:00 | 2749 |  |  | 0.76745
2020-04-24 13:00 | 2750 |  |  | 0.77737
2020-04-24 14:00 | 2751 |  |  | 0.71948
2020-04-24 15:00 | 2752 |  |  | 0.63513
2020-04-24 16:00 | 2753 |  |  | 0.48296
2020-04-24 17:00 | 2754 |  |  | 0.28449
2020-04-24 18:00 | 2755 |  |  | 0.081045
2020-04-24 19:00 | 2756 |  |  | 0
2020-04-24 20:00 | 2757 |  |  | 0
2020-04-24 21:00 | 2758 |  |  | 0
2020-04-24 22:00 | 2759 |  |  | 0
2020-04-24 23:00 | 2760 |  |  | 0
2020-04-25 | 2761 |  |  | 0
2020-04-25 01:00 | 2762 |  |  | 0
2020-04-25 02:00 | 2763 |  |  | 0
2020-04-25 03:00 | 2764 |  |  | 0
2020-04-25 04:00 | 2765 |  |  | 0
2020-04-25 05:00 | 2766 |  |  | 0
2020-04-25 06:00 | 2767 |  |  | 0.019848
2020-04-25 07:00 | 2768 |  |  | 0.11082
2020-04-25 08:00 | 2769 |  |  | 0.19682
2020-04-25 09:00 | 2770 |  |  | 0.48296
2020-04-25 10:00 | 2771 |  |  | 0.62024
2020-04-25 11:00 | 2772 |  |  | 0.70294
2020-04-25 12:00 | 2773 |  |  | 0.75422
2020-04-25 13:00 | 2774 |  |  | 0.75091
2020-04-25 14:00 | 2775 |  |  | 0.64175
2020-04-25 15:00 | 2776 |  |  | 0.51274
2020-04-25 16:00 | 2777 |  |  | 0.42177
2020-04-25 17:00 | 2778 |  |  | 0.16209
2020-04-25 18:00 | 2779 |  |  | 0.044658
2020-04-25 19:00 | 2780 |  |  | 0
2020-04-25 20:00 | 2781 |  |  | 0
2020-04-25 21:00 | 2782 |  |  | 0
2020-04-25 22:00 | 2783 |  |  | 0
2020-04-25 23:00 | 2784 |  |  | 0
2020-04-26 | 2785 |  |  | 0
2020-04-26 01:00 | 2786 |  |  | 0
2020-04-26 02:00 | 2787 |  |  | 0
2020-04-26 03:00 | 2788 |  |  | 0
2020-04-26 04:00 | 2789 |  |  | 0
2020-04-26 05:00 | 2790 |  |  | 0
2020-04-26 06:00 | 2791 |  |  | 0.046312
2020-04-26 07:00 | 2792 |  |  | 0.064505
2020-04-26 08:00 | 2793 |  |  | 0.12074
2020-04-26 09:00 | 2794 |  |  | 0.23817
2020-04-26 10:00 | 2795 |  |  | 0.33741
2020-04-26 11:00 | 2796 |  |  | 0.63348
2020-04-26 12:00 | 2797 |  |  | 0.51108
2020-04-26 13:00 | 2798 |  |  | 0.25471
2020-04-26 14:00 | 2799 |  |  | 0.17532
2020-04-26 15:00 | 2800 |  |  | 0.26133
2020-04-26 16:00 | 2801 |  |  | 0.13563
2020-04-26 17:00 | 2802 |  |  | 0.013232
2020-04-26 18:00 | 2803 |  |  | 0.001654
2020-04-26 19:00 | 2804 |  |  | 0
2020-04-26 20:00 | 2805 |  |  | 0
2020-04-26 21:00 | 2806 |  |  | 0
2020-04-26 22:00 | 2807 |  |  | 0
2020-04-26 23:00 | 2808 |  |  | 0
2020-04-27 | 2809 |  |  | 0
2020-04-27 01:00 | 2810 |  |  | 0
2020-04-27 02:00 | 2811 |  |  | 0
2020-04-27 03:00 | 2812 |  |  | 0
2020-04-27 04:00 | 2813 |  |  | 0
2020-04-27 05:00 | 2814 |  |  | 0
2020-04-27 06:00 | 2815 |  |  | 0
2020-04-27 07:00 | 2816 |  |  | 0
2020-04-27 08:00 | 2817 |  |  | 0.086007
2020-04-27 09:00 | 2818 |  |  | 0.27125
2020-04-27 10:00 | 2819 |  |  | 0.2911
2020-04-27 11:00 | 2820 |  |  | 0.42673
2020-04-27 12:00 | 2821 |  |  | 0.32087
2020-04-27 13:00 | 2822 |  |  | 0.16209
2020-04-27 14:00 | 2823 |  |  | 0.066159
2020-04-27 15:00 | 2824 |  |  | 0.34238
2020-04-27 16:00 | 2825 |  |  | 0.19682
2020-04-27 17:00 | 2826 |  |  | 0.014886
2020-04-27 18:00 | 2827 |  |  | 0
2020-04-27 19:00 | 2828 |  |  | 0
2020-04-27 20:00 | 2829 |  |  | 0
2020-04-27 21:00 | 2830 |  |  | 0
2020-04-27 22:00 | 2831 |  |  | 0
2020-04-27 23:00 | 2832 |  |  | 0
2020-04-28 | 2833 |  |  | 0
2020-04-28 01:00 | 2834 |  |  | 0
2020-04-28 02:00 | 2835 |  |  | 0
2020-04-28 03:00 | 2836 |  |  | 0
2020-04-28 04:00 | 2837 |  |  | 0
2020-04-28 05:00 | 2838 |  |  | 0
2020-04-28 06:00 | 2839 |  |  | 0
2020-04-28 07:00 | 2840 |  |  | 0
2020-04-28 08:00 | 2841 |  |  | 0.031426
2020-04-28 09:00 | 2842 |  |  | 0.059543
2020-04-28 10:00 | 2843 |  |  | 0.056236
2020-04-28 11:00 | 2844 |  |  | 0.059543
2020-04-28 12:00 | 2845 |  |  | 0.047966
2020-04-28 13:00 | 2846 |  |  | 0.10089
2020-04-28 14:00 | 2847 |  |  | 0.20179
2020-04-28 15:00 | 2848 |  |  | 0.15382
2020-04-28 16:00 | 2849 |  |  | 0.16705
2020-04-28 17:00 | 2850 |  |  | 0.013232
2020-04-28 18:00 | 2851 |  |  | 0.0082699
2020-04-28 19:00 | 2852 |  |  | 0
2020-04-28 20:00 | 2853 |  |  | 0
2020-04-28 21:00 | 2854 |  |  | 0
2020-04-28 22:00 | 2855 |  |  | 0
2020-04-28 23:00 | 2856 |  |  | 0
2020-04-29 | 2857 |  |  | 0
2020-04-29 01:00 | 2858 |  |  | 0
2020-04-29 02:00 | 2859 |  |  | 0
2020-04-29 03:00 | 2860 |  |  | 0
2020-04-29 04:00 | 2861 |  |  | 0
2020-04-29 05:00 | 2862 |  |  | 0
2020-04-29 06:00 | 2863 |  |  | 0.047966
2020-04-29 07:00 | 2864 |  |  | 0.1257
2020-04-29 08:00 | 2865 |  |  | 0.16374
2020-04-29 09:00 | 2866 |  |  | 0.55905
2020-04-29 10:00 | 2867 |  |  | 0.64009
2020-04-29 11:00 | 2868 |  |  | 0.73106
2020-04-29 12:00 | 2869 |  |  | 0.79061
2020-04-29 13:00 | 2870 |  |  | 0.81045
2020-04-29 14:00 | 2871 |  |  | 0.75256
2020-04-29 15:00 | 2872 |  |  | 0.66159
2020-04-29 16:00 | 2873 |  |  | 0.52266
2020-04-29 17:00 | 2874 |  |  | 0.33907
2020-04-29 18:00 | 2875 |  |  | 0.11743
2020-04-29 19:00 | 2876 |  |  | 0
2020-04-29 20:00 | 2877 |  |  | 0
2020-04-29 21:00 | 2878 |  |  | 0
2020-04-29 22:00 | 2879 |  |  | 0
2020-04-29 23:00 | 2880 |  |  | 0
2020-04-30 | 2881 |  |  | 0
2020-04-30 01:00 | 2882 |  |  | 0
2020-04-30 02:00 | 2883 |  |  | 0
2020-04-30 03:00 | 2884 |  |  | 0
2020-04-30 04:00 | 2885 |  |  | 0
2020-04-30 05:00 | 2886 |  |  | 0
2020-04-30 06:00 | 2887 |  |  | 0.04135
2020-04-30 07:00 | 2888 |  |  | 0.13728
2020-04-30 08:00 | 2889 |  |  | 0.2266
2020-04-30 09:00 | 2890 |  |  | 0.27952
2020-04-30 10:00 | 2891 |  |  | 0.23487
2020-04-30 11:00 | 2892 |  |  | 0.34403
2020-04-30 12:00 | 2893 |  |  | 0.2084
2020-04-30 13:00 | 2894 |  |  | 0.11247
2020-04-30 14:00 | 2895 |  |  | 0.34568
2020-04-30 15:00 | 2896 |  |  | 0.32087
2020-04-30 16:00 | 2897 |  |  | 0.16871
2020-04-30 17:00 | 2898 |  |  | 0.067813
2020-04-30 18:00 | 2899 |  |  | 0.11909
2020-04-30 19:00 | 2900 |  |  | 0
2020-04-30 20:00 | 2901 |  |  | 0
2020-04-30 21:00 | 2902 |  |  | 0
2020-04-30 22:00 | 2903 |  |  | 0
2020-04-30 23:00 | 2904 |  |  | 0
2020-05-01 | 2905 |  |  | 0
2020-05-01 01:00 | 2906 |  |  | 0
2020-05-01 02:00 | 2907 |  |  | 0
2020-05-01 03:00 | 2908 |  |  | 0
2020-05-01 04:00 | 2909 |  |  | 0
2020-05-01 05:00 | 2910 |  |  | 0
2020-05-01 06:00 | 2911 |  |  | 0.051274
2020-05-01 07:00 | 2912 |  |  | 0.14555
2020-05-01 08:00 | 2913 |  |  | 0.26464
2020-05-01 09:00 | 2914 |  |  | 0.35726
2020-05-01 10:00 | 2915 |  |  | 0.5822
2020-05-01 11:00 | 2916 |  |  | 0.54416
2020-05-01 12:00 | 2917 |  |  | 0.46973
2020-05-01 13:00 | 2918 |  |  | 0.5789
2020-05-01 14:00 | 2919 |  |  | 0.50447
2020-05-01 15:00 | 2920 |  |  | 0.1257
2020-05-01 16:00 | 2921 |  |  | 0.12405
2020-05-01 17:00 | 2922 |  |  | 0.11743
2020-05-01 18:00 | 2923 |  |  | 0.0082699
2020-05-01 19:00 | 2924 |  |  | 0
2020-05-01 20:00 | 2925 |  |  | 0
2020-05-01 21:00 | 2926 |  |  | 0
2020-05-01 22:00 | 2927 |  |  | 0
2020-05-01 23:00 | 2928 |  |  | 0
2020-05-02 | 2929 |  |  | 0
2020-05-02 01:00 | 2930 |  |  | 0
2020-05-02 02:00 | 2931 |  |  | 0
2020-05-02 03:00 | 2932 |  |  | 0
2020-05-02 04:00 | 2933 |  |  | 0
2020-05-02 05:00 | 2934 |  |  | 0
2020-05-02 06:00 | 2935 |  |  | 0.028118
2020-05-02 07:00 | 2936 |  |  | 0.11082
2020-05-02 08:00 | 2937 |  |  | 0.27125
2020-05-02 09:00 | 2938 |  |  | 0.48793
2020-05-02 10:00 | 2939 |  |  | 0.66325
2020-05-02 11:00 | 2940 |  |  | 0.75587
2020-05-02 12:00 | 2941 |  |  | 0.81211
2020-05-02 13:00 | 2942 |  |  | 0.83692
2020-05-02 14:00 | 2943 |  |  | 0.78068
2020-05-02 15:00 | 2944 |  |  | 0.68475
2020-05-02 16:00 | 2945 |  |  | 0.53424
2020-05-02 17:00 | 2946 |  |  | 0.32418
2020-05-02 18:00 | 2947 |  |  | 0.054582
2020-05-02 19:00 | 2948 |  |  | 0
2020-05-02 20:00 | 2949 |  |  | 0
2020-05-02 21:00 | 2950 |  |  | 0
2020-05-02 22:00 | 2951 |  |  | 0
2020-05-02 23:00 | 2952 |  |  | 0
2020-05-03 | 2953 |  |  | 0
2020-05-03 01:00 | 2954 |  |  | 0
2020-05-03 02:00 | 2955 |  |  | 0
2020-05-03 03:00 | 2956 |  |  | 0
2020-05-03 04:00 | 2957 |  |  | 0
2020-05-03 05:00 | 2958 |  |  | 0
2020-05-03 06:00 | 2959 |  |  | 0
2020-05-03 07:00 | 2960 |  |  | 0.095931
2020-05-03 08:00 | 2961 |  |  | 0.31095
2020-05-03 09:00 | 2962 |  |  | 0.4962
2020-05-03 10:00 | 2963 |  |  | 0.6434
2020-05-03 11:00 | 2964 |  |  | 0.72941
2020-05-03 12:00 | 2965 |  |  | 0.78234
2020-05-03 13:00 | 2966 |  |  | 0.80549
2020-05-03 14:00 | 2967 |  |  | 0.73437
2020-05-03 15:00 | 2968 |  |  | 0.65498
2020-05-03 16:00 | 2969 |  |  | 0.5177
2020-05-03 17:00 | 2970 |  |  | 0.33245
2020-05-03 18:00 | 2971 |  |  | 0.11578
2020-05-03 19:00 | 2972 |  |  | 0
2020-05-03 20:00 | 2973 |  |  | 0
2020-05-03 21:00 | 2974 |  |  | 0
2020-05-03 22:00 | 2975 |  |  | 0
2020-05-03 23:00 | 2976 |  |  | 0
2020-05-04 | 2977 |  |  | 0
2020-05-04 01:00 | 2978 |  |  | 0
2020-05-04 02:00 | 2979 |  |  | 0
2020-05-04 03:00 | 2980 |  |  | 0
2020-05-04 04:00 | 2981 |  |  | 0
2020-05-04 05:00 | 2982 |  |  | 0
2020-05-04 06:00 | 2983 |  |  | 0.036388
2020-05-04 07:00 | 2984 |  |  | 0.1257
2020-05-04 08:00 | 2985 |  |  | 0.22825
2020-05-04 09:00 | 2986 |  |  | 0.34403
2020-05-04 10:00 | 2987 |  |  | 0.57393
2020-05-04 11:00 | 2988 |  |  | 0.72279
2020-05-04 12:00 | 2989 |  |  | 0.81045
2020-05-04 13:00 | 2990 |  |  | 0.80549
2020-05-04 14:00 | 2991 |  |  | 0.71783
2020-05-04 15:00 | 2992 |  |  | 0.65663
2020-05-04 16:00 | 2993 |  |  | 0.51274
2020-05-04 17:00 | 2994 |  |  | 0.32914
2020-05-04 18:00 | 2995 |  |  | 0.11743
2020-05-04 19:00 | 2996 |  |  | 0
2020-05-04 20:00 | 2997 |  |  | 0
2020-05-04 21:00 | 2998 |  |  | 0
2020-05-04 22:00 | 2999 |  |  | 0
2020-05-04 23:00 | 3000 |  |  | 0
2020-05-05 | 3001 |  |  | 0
2020-05-05 01:00 | 3002 |  |  | 0
2020-05-05 02:00 | 3003 |  |  | 0
2020-05-05 03:00 | 3004 |  |  | 0
2020-05-05 04:00 | 3005 |  |  | 0
2020-05-05 05:00 | 3006 |  |  | 0
2020-05-05 06:00 | 3007 |  |  | 0.039696
2020-05-05 07:00 | 3008 |  |  | 0.15217
2020-05-05 08:00 | 3009 |  |  | 0.27622
2020-05-05 09:00 | 3010 |  |  | 0.45981
2020-05-05 10:00 | 3011 |  |  | 0.4962
2020-05-05 11:00 | 3012 |  |  | 0.66159
2020-05-05 12:00 | 3013 |  |  | 0.6831
2020-05-05 13:00 | 3014 |  |  | 0.72114
2020-05-05 14:00 | 3015 |  |  | 0.65829
2020-05-05 15:00 | 3016 |  |  | 0.4135
2020-05-05 16:00 | 3017 |  |  | 0.48793
2020-05-05 17:00 | 3018 |  |  | 0.31922
2020-05-05 18:00 | 3019 |  |  | 0.074429
2020-05-05 19:00 | 3020 |  |  | 0
2020-05-05 20:00 | 3021 |  |  | 0
2020-05-05 21:00 | 3022 |  |  | 0
2020-05-05 22:00 | 3023 |  |  | 0
2020-05-05 23:00 | 3024 |  |  | 0
2020-05-06 | 3025 |  |  | 0
2020-05-06 01:00 | 3026 |  |  | 0
2020-05-06 02:00 | 3027 |  |  | 0
2020-05-06 03:00 | 3028 |  |  | 0
2020-05-06 04:00 | 3029 |  |  | 0
2020-05-06 05:00 | 3030 |  |  | 0
2020-05-06 06:00 | 3031 |  |  | 0.004962
2020-05-06 07:00 | 3032 |  |  | 0.10916
2020-05-06 08:00 | 3033 |  |  | 0.29937
2020-05-06 09:00 | 3034 |  |  | 0.47469
2020-05-06 10:00 | 3035 |  |  | 0.54912
2020-05-06 11:00 | 3036 |  |  | 0.71452
2020-05-06 12:00 | 3037 |  |  | 0.61363
2020-05-06 13:00 | 3038 |  |  | 0.53258
2020-05-06 14:00 | 3039 |  |  | 0.60701
2020-05-06 15:00 | 3040 |  |  | 0.35065
2020-05-06 16:00 | 3041 |  |  | 0.2266
2020-05-06 17:00 | 3042 |  |  | 0.16374
2020-05-06 18:00 | 3043 |  |  | 0.04962
2020-05-06 19:00 | 3044 |  |  | 0
2020-05-06 20:00 | 3045 |  |  | 0
2020-05-06 21:00 | 3046 |  |  | 0
2020-05-06 22:00 | 3047 |  |  | 0
2020-05-06 23:00 | 3048 |  |  | 0
2020-05-07 | 3049 |  |  | 0
2020-05-07 01:00 | 3050 |  |  | 0
2020-05-07 02:00 | 3051 |  |  | 0
2020-05-07 03:00 | 3052 |  |  | 0
2020-05-07 04:00 | 3053 |  |  | 0
2020-05-07 05:00 | 3054 |  |  | 0
2020-05-07 06:00 | 3055 |  |  | 0.023156
2020-05-07 07:00 | 3056 |  |  | 0.094277
2020-05-07 08:00 | 3057 |  |  | 0.28118
2020-05-07 09:00 | 3058 |  |  | 0.48296
2020-05-07 10:00 | 3059 |  |  | 0.62686
2020-05-07 11:00 | 3060 |  |  | 0.72114
2020-05-07 12:00 | 3061 |  |  | 0.76745
2020-05-07 13:00 | 3062 |  |  | 0.77241
2020-05-07 14:00 | 3063 |  |  | 0.7261
2020-05-07 15:00 | 3064 |  |  | 0.63182
2020-05-07 16:00 | 3065 |  |  | 0.50116
2020-05-07 17:00 | 3066 |  |  | 0.30103
2020-05-07 18:00 | 3067 |  |  | 0.10586
2020-05-07 19:00 | 3068 |  |  | 0
2020-05-07 20:00 | 3069 |  |  | 0
2020-05-07 21:00 | 3070 |  |  | 0
2020-05-07 22:00 | 3071 |  |  | 0
2020-05-07 23:00 | 3072 |  |  | 0
2020-05-08 | 3073 |  |  | 0
2020-05-08 01:00 | 3074 |  |  | 0
2020-05-08 02:00 | 3075 |  |  | 0
2020-05-08 03:00 | 3076 |  |  | 0
2020-05-08 04:00 | 3077 |  |  | 0
2020-05-08 05:00 | 3078 |  |  | 0.0066159
2020-05-08 06:00 | 3079 |  |  | 0.043004
2020-05-08 07:00 | 3080 |  |  | 0.039696
2020-05-08 08:00 | 3081 |  |  | 0.084353
2020-05-08 09:00 | 3082 |  |  | 0.15382
2020-05-08 10:00 | 3083 |  |  | 0.20509
2020-05-08 11:00 | 3084 |  |  | 0.38538
2020-05-08 12:00 | 3085 |  |  | 0.60867
2020-05-08 13:00 | 3086 |  |  | 0.73602
2020-05-08 14:00 | 3087 |  |  | 0.70956
2020-05-08 15:00 | 3088 |  |  | 0.6037
2020-05-08 16:00 | 3089 |  |  | 0.35065
2020-05-08 17:00 | 3090 |  |  | 0.11909
2020-05-08 18:00 | 3091 |  |  | 0.052928
2020-05-08 19:00 | 3092 |  |  | 0
2020-05-08 20:00 | 3093 |  |  | 0
2020-05-08 21:00 | 3094 |  |  | 0
2020-05-08 22:00 | 3095 |  |  | 0
2020-05-08 23:00 | 3096 |  |  | 0
2020-05-09 | 3097 |  |  | 0
2020-05-09 01:00 | 3098 |  |  | 0
2020-05-09 02:00 | 3099 |  |  | 0
2020-05-09 03:00 | 3100 |  |  | 0
2020-05-09 04:00 | 3101 |  |  | 0
2020-05-09 05:00 | 3102 |  |  | 0
2020-05-09 06:00 | 3103 |  |  | 0.047966
2020-05-09 07:00 | 3104 |  |  | 0.15217
2020-05-09 08:00 | 3105 |  |  | 0.28614
2020-05-09 09:00 | 3106 |  |  | 0.48296
2020-05-09 10:00 | 3107 |  |  | 0.60867
2020-05-09 11:00 | 3108 |  |  | 0.41019
2020-05-09 12:00 | 3109 |  |  | 0
2020-05-09 13:00 | 3110 |  |  | 0.5177
2020-05-09 14:00 | 3111 |  |  | 0.57724
2020-05-09 15:00 | 3112 |  |  | 0.55739
2020-05-09 16:00 | 3113 |  |  | 0.3093
2020-05-09 17:00 | 3114 |  |  | 0.13232
2020-05-09 18:00 | 3115 |  |  | 0.001654
2020-05-09 19:00 | 3116 |  |  | 0
2020-05-09 20:00 | 3117 |  |  | 0
2020-05-09 21:00 | 3118 |  |  | 0
2020-05-09 22:00 | 3119 |  |  | 0
2020-05-09 23:00 | 3120 |  |  | 0
2020-05-10 | 3121 |  |  | 0
2020-05-10 01:00 | 3122 |  |  | 0
2020-05-10 02:00 | 3123 |  |  | 0
2020-05-10 03:00 | 3124 |  |  | 0
2020-05-10 04:00 | 3125 |  |  | 0
2020-05-10 05:00 | 3126 |  |  | 0
2020-05-10 06:00 | 3127 |  |  | 0.021502
2020-05-10 07:00 | 3128 |  |  | 0.10586
2020-05-10 08:00 | 3129 |  |  | 0.14059
2020-05-10 09:00 | 3130 |  |  | 0.39199
2020-05-10 10:00 | 3131 |  |  | 0.59874
2020-05-10 11:00 | 3132 |  |  | 0.63182
2020-05-10 12:00 | 3133 |  |  | 0.51439
2020-05-10 13:00 | 3134 |  |  | 0.24148
2020-05-10 14:00 | 3135 |  |  | 0.1654
2020-05-10 15:00 | 3136 |  |  | 0.089315
2020-05-10 16:00 | 3137 |  |  | 0.034734
2020-05-10 17:00 | 3138 |  |  | 0
2020-05-10 18:00 | 3139 |  |  | 0.004962
2020-05-10 19:00 | 3140 |  |  | 0
2020-05-10 20:00 | 3141 |  |  | 0
2020-05-10 21:00 | 3142 |  |  | 0
2020-05-10 22:00 | 3143 |  |  | 0
2020-05-10 23:00 | 3144 |  |  | 0
2020-05-11 | 3145 |  |  | 0
2020-05-11 01:00 | 3146 |  |  | 0
2020-05-11 02:00 | 3147 |  |  | 0
2020-05-11 03:00 | 3148 |  |  | 0
2020-05-11 04:00 | 3149 |  |  | 0
2020-05-11 05:00 | 3150 |  |  | 0
2020-05-11 06:00 | 3151 |  |  | 0.039696
2020-05-11 07:00 | 3152 |  |  | 0.12405
2020-05-11 08:00 | 3153 |  |  | 0.071121
2020-05-11 09:00 | 3154 |  |  | 0.21171
2020-05-11 10:00 | 3155 |  |  | 0.15051
2020-05-11 11:00 | 3156 |  |  | 0.12901
2020-05-11 12:00 | 3157 |  |  | 0.33245
2020-05-11 13:00 | 3158 |  |  | 0.55574
2020-05-11 14:00 | 3159 |  |  | 0.36388
2020-05-11 15:00 | 3160 |  |  | 0.25802
2020-05-11 16:00 | 3161 |  |  | 0.13728
2020-05-11 17:00 | 3162 |  |  | 0.11082
2020-05-11 18:00 | 3163 |  |  | 0.003308
2020-05-11 19:00 | 3164 |  |  | 0
2020-05-11 20:00 | 3165 |  |  | 0
2020-05-11 21:00 | 3166 |  |  | 0
2020-05-11 22:00 | 3167 |  |  | 0
2020-05-11 23:00 | 3168 |  |  | 0
2020-05-12 | 3169 |  |  | 0
2020-05-12 01:00 | 3170 |  |  | 0
2020-05-12 02:00 | 3171 |  |  | 0
2020-05-12 03:00 | 3172 |  |  | 0
2020-05-12 04:00 | 3173 |  |  | 0
2020-05-12 05:00 | 3174 |  |  | 0
2020-05-12 06:00 | 3175 |  |  | 0.044658
2020-05-12 07:00 | 3176 |  |  | 0.16374
2020-05-12 08:00 | 3177 |  |  | 0.19682
2020-05-12 09:00 | 3178 |  |  | 0.24314
2020-05-12 10:00 | 3179 |  |  | 0.29441
2020-05-12 11:00 | 3180 |  |  | 0.51439
2020-05-12 12:00 | 3181 |  |  | 0.72279
2020-05-12 13:00 | 3182 |  |  | 0.76745
2020-05-12 14:00 | 3183 |  |  | 0.31426
2020-05-12 15:00 | 3184 |  |  | 0.14555
2020-05-12 16:00 | 3185 |  |  | 0.077737
2020-05-12 17:00 | 3186 |  |  | 0
2020-05-12 18:00 | 3187 |  |  | 0.0099239
2020-05-12 19:00 | 3188 |  |  | 0
2020-05-12 20:00 | 3189 |  |  | 0
2020-05-12 21:00 | 3190 |  |  | 0
2020-05-12 22:00 | 3191 |  |  | 0
2020-05-12 23:00 | 3192 |  |  | 0
2020-05-13 | 3193 |  |  | 0
2020-05-13 01:00 | 3194 |  |  | 0
2020-05-13 02:00 | 3195 |  |  | 0
2020-05-13 03:00 | 3196 |  |  | 0
2020-05-13 04:00 | 3197 |  |  | 0
2020-05-13 05:00 | 3198 |  |  | 0
2020-05-13 06:00 | 3199 |  |  | 0
2020-05-13 07:00 | 3200 |  |  | 0
2020-05-13 08:00 | 3201 |  |  | 0.028118
2020-05-13 09:00 | 3202 |  |  | 0
2020-05-13 10:00 | 3203 |  |  | 0.023156
2020-05-13 11:00 | 3204 |  |  | 0.01654
2020-05-13 12:00 | 3205 |  |  | 0.044658
2020-05-13 13:00 | 3206 |  |  | 0.074429
2020-05-13 14:00 | 3207 |  |  | 0.014886
2020-05-13 15:00 | 3208 |  |  | 0.087661
2020-05-13 16:00 | 3209 |  |  | 0.034734
2020-05-13 17:00 | 3210 |  |  | 0.03308
2020-05-13 18:00 | 3211 |  |  | 0
2020-05-13 19:00 | 3212 |  |  | 0
2020-05-13 20:00 | 3213 |  |  | 0
2020-05-13 21:00 | 3214 |  |  | 0
2020-05-13 22:00 | 3215 |  |  | 0
2020-05-13 23:00 | 3216 |  |  | 0
2020-05-14 | 3217 |  |  | 0
2020-05-14 01:00 | 3218 |  |  | 0
2020-05-14 02:00 | 3219 |  |  | 0
2020-05-14 03:00 | 3220 |  |  | 0
2020-05-14 04:00 | 3221 |  |  | 0
2020-05-14 05:00 | 3222 |  |  | 0
2020-05-14 06:00 | 3223 |  |  | 0.038042
2020-05-14 07:00 | 3224 |  |  | 0.14224
2020-05-14 08:00 | 3225 |  |  | 0.18359
2020-05-14 09:00 | 3226 |  |  | 0.51604
2020-05-14 10:00 | 3227 |  |  | 0.36222
2020-05-14 11:00 | 3228 |  |  | 0.18194
2020-05-14 12:00 | 3229 |  |  | 0.29606
2020-05-14 13:00 | 3230 |  |  | 0.77737
2020-05-14 14:00 | 3231 |  |  | 0.6037
2020-05-14 15:00 | 3232 |  |  | 0.45981
2020-05-14 16:00 | 3233 |  |  | 0.35726
2020-05-14 17:00 | 3234 |  |  | 0.03308
2020-05-14 18:00 | 3235 |  |  | 0
2020-05-14 19:00 | 3236 |  |  | 0
2020-05-14 20:00 | 3237 |  |  | 0
2020-05-14 21:00 | 3238 |  |  | 0
2020-05-14 22:00 | 3239 |  |  | 0
2020-05-14 23:00 | 3240 |  |  | 0
2020-05-15 | 3241 |  |  | 0
2020-05-15 01:00 | 3242 |  |  | 0
2020-05-15 02:00 | 3243 |  |  | 0
2020-05-15 03:00 | 3244 |  |  | 0
2020-05-15 04:00 | 3245 |  |  | 0
2020-05-15 05:00 | 3246 |  |  | 0.001654
2020-05-15 06:00 | 3247 |  |  | 0.081045
2020-05-15 07:00 | 3248 |  |  | 0.14224
2020-05-15 08:00 | 3249 |  |  | 0.25802
2020-05-15 09:00 | 3250 |  |  | 0.43334
2020-05-15 10:00 | 3251 |  |  | 0.56236
2020-05-15 11:00 | 3252 |  |  | 0.44492
2020-05-15 12:00 | 3253 |  |  | 0.51439
2020-05-15 13:00 | 3254 |  |  | 0.435
2020-05-15 14:00 | 3255 |  |  | 0.65332
2020-05-15 15:00 | 3256 |  |  | 0.32253
2020-05-15 16:00 | 3257 |  |  | 0.18855
2020-05-15 17:00 | 3258 |  |  | 0.072775
2020-05-15 18:00 | 3259 |  |  | 0.077737
2020-05-15 19:00 | 3260 |  |  | 0
2020-05-15 20:00 | 3261 |  |  | 0
2020-05-15 21:00 | 3262 |  |  | 0
2020-05-15 22:00 | 3263 |  |  | 0
2020-05-15 23:00 | 3264 |  |  | 0
2020-05-16 | 3265 |  |  | 0
2020-05-16 01:00 | 3266 |  |  | 0
2020-05-16 02:00 | 3267 |  |  | 0
2020-05-16 03:00 | 3268 |  |  | 0
2020-05-16 04:00 | 3269 |  |  | 0
2020-05-16 05:00 | 3270 |  |  | 0
2020-05-16 06:00 | 3271 |  |  | 0.04962
2020-05-16 07:00 | 3272 |  |  | 0.074429
2020-05-16 08:00 | 3273 |  |  | 0.1439
2020-05-16 09:00 | 3274 |  |  | 0.18359
2020-05-16 10:00 | 3275 |  |  | 0.29606
2020-05-16 11:00 | 3276 |  |  | 0.52762
2020-05-16 12:00 | 3277 |  |  | 0.40357
2020-05-16 13:00 | 3278 |  |  | 0.478
2020-05-16 14:00 | 3279 |  |  | 0.082699
2020-05-16 15:00 | 3280 |  |  | 0.01654
2020-05-16 16:00 | 3281 |  |  | 0.086007
2020-05-16 17:00 | 3282 |  |  | 0.036388
2020-05-16 18:00 | 3283 |  |  | 0
2020-05-16 19:00 | 3284 |  |  | 0
2020-05-16 20:00 | 3285 |  |  | 0
2020-05-16 21:00 | 3286 |  |  | 0
2020-05-16 22:00 | 3287 |  |  | 0
2020-05-16 23:00 | 3288 |  |  | 0
2020-05-17 | 3289 |  |  | 0
2020-05-17 01:00 | 3290 |  |  | 0
2020-05-17 02:00 | 3291 |  |  | 0
2020-05-17 03:00 | 3292 |  |  | 0
2020-05-17 04:00 | 3293 |  |  | 0
2020-05-17 05:00 | 3294 |  |  | 0
2020-05-17 06:00 | 3295 |  |  | 0
2020-05-17 07:00 | 3296 |  |  | 0
2020-05-17 08:00 | 3297 |  |  | 0.099239
2020-05-17 09:00 | 3298 |  |  | 0.16871
2020-05-17 10:00 | 3299 |  |  | 0.39861
2020-05-17 11:00 | 3300 |  |  | 0.64175
2020-05-17 12:00 | 3301 |  |  | 0.75753
2020-05-17 13:00 | 3302 |  |  | 0.46642
2020-05-17 14:00 | 3303 |  |  | 0.63182
2020-05-17 15:00 | 3304 |  |  | 0.40688
2020-05-17 16:00 | 3305 |  |  | 0.26298
2020-05-17 17:00 | 3306 |  |  | 0.13563
2020-05-17 18:00 | 3307 |  |  | 0.047966
2020-05-17 19:00 | 3308 |  |  | 0
2020-05-17 20:00 | 3309 |  |  | 0
2020-05-17 21:00 | 3310 |  |  | 0
2020-05-17 22:00 | 3311 |  |  | 0
2020-05-17 23:00 | 3312 |  |  | 0
2020-05-18 | 3313 |  |  | 0
2020-05-18 01:00 | 3314 |  |  | 0
2020-05-18 02:00 | 3315 |  |  | 0
2020-05-18 03:00 | 3316 |  |  | 0
2020-05-18 04:00 | 3317 |  |  | 0
2020-05-18 05:00 | 3318 |  |  | 0.013232
2020-05-18 06:00 | 3319 |  |  | 0.046312
2020-05-18 07:00 | 3320 |  |  | 0.12736
2020-05-18 08:00 | 3321 |  |  | 0.30433
2020-05-18 09:00 | 3322 |  |  | 0.37711
2020-05-18 10:00 | 3323 |  |  | 0.57228
2020-05-18 11:00 | 3324 |  |  | 0.5177
2020-05-18 12:00 | 3325 |  |  | 0.41019
2020-05-18 13:00 | 3326 |  |  | 0.59543
2020-05-18 14:00 | 3327 |  |  | 0.52101
2020-05-18 15:00 | 3328 |  |  | 0.30764
2020-05-18 16:00 | 3329 |  |  | 0.24479
2020-05-18 17:00 | 3330 |  |  | 0.35726
2020-05-18 18:00 | 3331 |  |  | 0.15878
2020-05-18 19:00 | 3332 |  |  | 0.0066159
2020-05-18 20:00 | 3333 |  |  | 0
2020-05-18 21:00 | 3334 |  |  | 0
2020-05-18 22:00 | 3335 |  |  | 0
2020-05-18 23:00 | 3336 |  |  | 0
2020-05-19 | 3337 |  |  | 0
2020-05-19 01:00 | 3338 |  |  | 0
2020-05-19 02:00 | 3339 |  |  | 0
2020-05-19 03:00 | 3340 |  |  | 0
2020-05-19 04:00 | 3341 |  |  | 0
2020-05-19 05:00 | 3342 |  |  | 0
2020-05-19 06:00 | 3343 |  |  | 0.052928
2020-05-19 07:00 | 3344 |  |  | 0.13066
2020-05-19 08:00 | 3345 |  |  | 0.14224
2020-05-19 09:00 | 3346 |  |  | 0.42342
2020-05-19 10:00 | 3347 |  |  | 0.34568
2020-05-19 11:00 | 3348 |  |  | 0.40192
2020-05-19 12:00 | 3349 |  |  | 0.36388
2020-05-19 13:00 | 3350 |  |  | 0.55078
2020-05-19 14:00 | 3351 |  |  | 0.7476
2020-05-19 15:00 | 3352 |  |  | 0.32253
2020-05-19 16:00 | 3353 |  |  | 0.49123
2020-05-19 17:00 | 3354 |  |  | 0.21833
2020-05-19 18:00 | 3355 |  |  | 0.04135
2020-05-19 19:00 | 3356 |  |  | 0
2020-05-19 20:00 | 3357 |  |  | 0
2020-05-19 21:00 | 3358 |  |  | 0
2020-05-19 22:00 | 3359 |  |  | 0
2020-05-19 23:00 | 3360 |  |  | 0
2020-05-20 | 3361 |  |  | 0
2020-05-20 01:00 | 3362 |  |  | 0
2020-05-20 02:00 | 3363 |  |  | 0
2020-05-20 03:00 | 3364 |  |  | 0
2020-05-20 04:00 | 3365 |  |  | 0
2020-05-20 05:00 | 3366 |  |  | 0
2020-05-20 06:00 | 3367 |  |  | 0.0082699
2020-05-20 07:00 | 3368 |  |  | 0.13893
2020-05-20 08:00 | 3369 |  |  | 0.31426
2020-05-20 09:00 | 3370 |  |  | 0.50777
2020-05-20 10:00 | 3371 |  |  | 0.62851
2020-05-20 11:00 | 3372 |  |  | 0.7046
2020-05-20 12:00 | 3373 |  |  | 0.75422
2020-05-20 13:00 | 3374 |  |  | 0.75422
2020-05-20 14:00 | 3375 |  |  | 0.71618
2020-05-20 15:00 | 3376 |  |  | 0.63017
2020-05-20 16:00 | 3377 |  |  | 0.50612
2020-05-20 17:00 | 3378 |  |  | 0.33411
2020-05-20 18:00 | 3379 |  |  | 0.13893
2020-05-20 19:00 | 3380 |  |  | 0.0082699
2020-05-20 20:00 | 3381 |  |  | 0
2020-05-20 21:00 | 3382 |  |  | 0
2020-05-20 22:00 | 3383 |  |  | 0
2020-05-20 23:00 | 3384 |  |  | 0
2020-05-21 | 3385 |  |  | 0
2020-05-21 01:00 | 3386 |  |  | 0
2020-05-21 02:00 | 3387 |  |  | 0
2020-05-21 03:00 | 3388 |  |  | 0
2020-05-21 04:00 | 3389 |  |  | 0
2020-05-21 05:00 | 3390 |  |  | 0
2020-05-21 06:00 | 3391 |  |  | 0.029772
2020-05-21 07:00 | 3392 |  |  | 0.097585
2020-05-21 08:00 | 3393 |  |  | 0.2299
2020-05-21 09:00 | 3394 |  |  | 0.46312
2020-05-21 10:00 | 3395 |  |  | 0.59378
2020-05-21 11:00 | 3396 |  |  | 0.69798
2020-05-21 12:00 | 3397 |  |  | 0.67152
2020-05-21 13:00 | 3398 |  |  | 0.75091
2020-05-21 14:00 | 3399 |  |  | 0.67152
2020-05-21 15:00 | 3400 |  |  | 0.60536
2020-05-21 16:00 | 3401 |  |  | 0.48131
2020-05-21 17:00 | 3402 |  |  | 0.31426
2020-05-21 18:00 | 3403 |  |  | 0.13232
2020-05-21 19:00 | 3404 |  |  | 0.004962
2020-05-21 20:00 | 3405 |  |  | 0
2020-05-21 21:00 | 3406 |  |  | 0
2020-05-21 22:00 | 3407 |  |  | 0
2020-05-21 23:00 | 3408 |  |  | 0
2020-05-22 | 3409 |  |  | 0
2020-05-22 01:00 | 3410 |  |  | 0
2020-05-22 02:00 | 3411 |  |  | 0
2020-05-22 03:00 | 3412 |  |  | 0
2020-05-22 04:00 | 3413 |  |  | 0
2020-05-22 05:00 | 3414 |  |  | 0.001654
2020-05-22 06:00 | 3415 |  |  | 0.047966
2020-05-22 07:00 | 3416 |  |  | 0.14886
2020-05-22 08:00 | 3417 |  |  | 0.29772
2020-05-22 09:00 | 3418 |  |  | 0.42011
2020-05-22 10:00 | 3419 |  |  | 0.5392
2020-05-22 11:00 | 3420 |  |  | 0.62851
2020-05-22 12:00 | 3421 |  |  | 0.38042
2020-05-22 13:00 | 3422 |  |  | 0.21998
2020-05-22 14:00 | 3423 |  |  | 0.35395
2020-05-22 15:00 | 3424 |  |  | 0.28945
2020-05-22 16:00 | 3425 |  |  | 0.13397
2020-05-22 17:00 | 3426 |  |  | 0.069467
2020-05-22 18:00 | 3427 |  |  | 0
2020-05-22 19:00 | 3428 |  |  | 0
2020-05-22 20:00 | 3429 |  |  | 0
2020-05-22 21:00 | 3430 |  |  | 0
2020-05-22 22:00 | 3431 |  |  | 0
2020-05-22 23:00 | 3432 |  |  | 0
2020-05-23 | 3433 |  |  | 0
2020-05-23 01:00 | 3434 |  |  | 0
2020-05-23 02:00 | 3435 |  |  | 0
2020-05-23 03:00 | 3436 |  |  | 0
2020-05-23 04:00 | 3437 |  |  | 0
2020-05-23 05:00 | 3438 |  |  | 0
2020-05-23 06:00 | 3439 |  |  | 0.072775
2020-05-23 07:00 | 3440 |  |  | 0.16209
2020-05-23 08:00 | 3441 |  |  | 0.2696
2020-05-23 09:00 | 3442 |  |  | 0.39034
2020-05-23 10:00 | 3443 |  |  | 0.47139
2020-05-23 11:00 | 3444 |  |  | 0.55574
2020-05-23 12:00 | 3445 |  |  | 0.39365
2020-05-23 13:00 | 3446 |  |  | 0.31922
2020-05-23 14:00 | 3447 |  |  | 0.36222
2020-05-23 15:00 | 3448 |  |  | 0.12074
2020-05-23 16:00 | 3449 |  |  | 0.20675
2020-05-23 17:00 | 3450 |  |  | 0.094277
2020-05-23 18:00 | 3451 |  |  | 0.079391
2020-05-23 19:00 | 3452 |  |  | 0.013232
2020-05-23 20:00 | 3453 |  |  | 0
2020-05-23 21:00 | 3454 |  |  | 0
2020-05-23 22:00 | 3455 |  |  | 0
2020-05-23 23:00 | 3456 |  |  | 0
2020-05-24 | 3457 |  |  | 0
2020-05-24 01:00 | 3458 |  |  | 0
2020-05-24 02:00 | 3459 |  |  | 0
2020-05-24 03:00 | 3460 |  |  | 0
2020-05-24 04:00 | 3461 |  |  | 0
2020-05-24 05:00 | 3462 |  |  | 0.0066159
2020-05-24 06:00 | 3463 |  |  | 0.031426
2020-05-24 07:00 | 3464 |  |  | 0.11578
2020-05-24 08:00 | 3465 |  |  | 0.3308
2020-05-24 09:00 | 3466 |  |  | 0.50777
2020-05-24 10:00 | 3467 |  |  | 0.6434
2020-05-24 11:00 | 3468 |  |  | 0.72941
2020-05-24 12:00 | 3469 |  |  | 0.79061
2020-05-24 13:00 | 3470 |  |  | 0.79557
2020-05-24 14:00 | 3471 |  |  | 0.72941
2020-05-24 15:00 | 3472 |  |  | 0.64505
2020-05-24 16:00 | 3473 |  |  | 0.50943
2020-05-24 17:00 | 3474 |  |  | 0.33907
2020-05-24 18:00 | 3475 |  |  | 0.15878
2020-05-24 19:00 | 3476 |  |  | 0.013232
2020-05-24 20:00 | 3477 |  |  | 0
2020-05-24 21:00 | 3478 |  |  | 0
2020-05-24 22:00 | 3479 |  |  | 0
2020-05-24 23:00 | 3480 |  |  | 0
2020-05-25 | 3481 |  |  | 0
2020-05-25 01:00 | 3482 |  |  | 0
2020-05-25 02:00 | 3483 |  |  | 0
2020-05-25 03:00 | 3484 |  |  | 0
2020-05-25 04:00 | 3485 |  |  | 0
2020-05-25 05:00 | 3486 |  |  | 0
2020-05-25 06:00 | 3487 |  |  | 0.059543
2020-05-25 07:00 | 3488 |  |  | 0.15713
2020-05-25 08:00 | 3489 |  |  | 0.29937
2020-05-25 09:00 | 3490 |  |  | 0.49454
2020-05-25 10:00 | 3491 |  |  | 0.62521
2020-05-25 11:00 | 3492 |  |  | 0.70294
2020-05-25 12:00 | 3493 |  |  | 0.70625
2020-05-25 13:00 | 3494 |  |  | 0.74595
2020-05-25 14:00 | 3495 |  |  | 0.69137
2020-05-25 15:00 | 3496 |  |  | 0.57724
2020-05-25 16:00 | 3497 |  |  | 0.49123
2020-05-25 17:00 | 3498 |  |  | 0.33411
2020-05-25 18:00 | 3499 |  |  | 0.14224
2020-05-25 19:00 | 3500 |  |  | 0.0099239
2020-05-25 20:00 | 3501 |  |  | 0
2020-05-25 21:00 | 3502 |  |  | 0
2020-05-25 22:00 | 3503 |  |  | 0
2020-05-25 23:00 | 3504 |  |  | 0
2020-05-26 | 3505 |  |  | 0
2020-05-26 01:00 | 3506 |  |  | 0
2020-05-26 02:00 | 3507 |  |  | 0
2020-05-26 03:00 | 3508 |  |  | 0
2020-05-26 04:00 | 3509 |  |  | 0
2020-05-26 05:00 | 3510 |  |  | 0.0099239
2020-05-26 06:00 | 3511 |  |  | 0.094277
2020-05-26 07:00 | 3512 |  |  | 0.14555
2020-05-26 08:00 | 3513 |  |  | 0.3308
2020-05-26 09:00 | 3514 |  |  | 0.4995
2020-05-26 10:00 | 3515 |  |  | 0.62851
2020-05-26 11:00 | 3516 |  |  | 0.71452
2020-05-26 12:00 | 3517 |  |  | 0.75422
2020-05-26 13:00 | 3518 |  |  | 0.74926
2020-05-26 14:00 | 3519 |  |  | 0.63513
2020-05-26 15:00 | 3520 |  |  | 0.47966
2020-05-26 16:00 | 3521 |  |  | 0.36222
2020-05-26 17:00 | 3522 |  |  | 0.30599
2020-05-26 18:00 | 3523 |  |  | 0.13563
2020-05-26 19:00 | 3524 |  |  | 0.0066159
2020-05-26 20:00 | 3525 |  |  | 0
2020-05-26 21:00 | 3526 |  |  | 0
2020-05-26 22:00 | 3527 |  |  | 0
2020-05-26 23:00 | 3528 |  |  | 0
2020-05-27 | 3529 |  |  | 0
2020-05-27 01:00 | 3530 |  |  | 0
2020-05-27 02:00 | 3531 |  |  | 0
2020-05-27 03:00 | 3532 |  |  | 0
2020-05-27 04:00 | 3533 |  |  | 0
2020-05-27 05:00 | 3534 |  |  | 0
2020-05-27 06:00 | 3535 |  |  | 0.029772
2020-05-27 07:00 | 3536 |  |  | 0.13893
2020-05-27 08:00 | 3537 |  |  | 0.3308
2020-05-27 09:00 | 3538 |  |  | 0.46973
2020-05-27 10:00 | 3539 |  |  | 0.63348
2020-05-27 11:00 | 3540 |  |  | 0.71452
2020-05-27 12:00 | 3541 |  |  | 0.75422
2020-05-27 13:00 | 3542 |  |  | 0.75587
2020-05-27 14:00 | 3543 |  |  | 0.65994
2020-05-27 15:00 | 3544 |  |  | 0.65002
2020-05-27 16:00 | 3545 |  |  | 0.40357
2020-05-27 17:00 | 3546 |  |  | 0.3308
2020-05-27 18:00 | 3547 |  |  | 0.13232
2020-05-27 19:00 | 3548 |  |  | 0.0082699
2020-05-27 20:00 | 3549 |  |  | 0
2020-05-27 21:00 | 3550 |  |  | 0
2020-05-27 22:00 | 3551 |  |  | 0
2020-05-27 23:00 | 3552 |  |  | 0
2020-05-28 | 3553 |  |  | 0
2020-05-28 01:00 | 3554 |  |  | 0
2020-05-28 02:00 | 3555 |  |  | 0
2020-05-28 03:00 | 3556 |  |  | 0
2020-05-28 04:00 | 3557 |  |  | 0
2020-05-28 05:00 | 3558 |  |  | 0
2020-05-28 06:00 | 3559 |  |  | 0.031426
2020-05-28 07:00 | 3560 |  |  | 0.12901
2020-05-28 08:00 | 3561 |  |  | 0.3126
2020-05-28 09:00 | 3562 |  |  | 0.478
2020-05-28 10:00 | 3563 |  |  | 0.60867
2020-05-28 11:00 | 3564 |  |  | 0.59213
2020-05-28 12:00 | 3565 |  |  | 0.35065
2020-05-28 13:00 | 3566 |  |  | 0.57559
2020-05-28 14:00 | 3567 |  |  | 0.63678
2020-05-28 15:00 | 3568 |  |  | 0.44161
2020-05-28 16:00 | 3569 |  |  | 0.38869
2020-05-28 17:00 | 3570 |  |  | 0.21171
2020-05-28 18:00 | 3571 |  |  | 0.11247
2020-05-28 19:00 | 3572 |  |  | 0.004962
2020-05-28 20:00 | 3573 |  |  | 0
2020-05-28 21:00 | 3574 |  |  | 0
2020-05-28 22:00 | 3575 |  |  | 0
2020-05-28 23:00 | 3576 |  |  | 0
2020-05-29 | 3577 |  |  | 0
2020-05-29 01:00 | 3578 |  |  | 0
2020-05-29 02:00 | 3579 |  |  | 0
2020-05-29 03:00 | 3580 |  |  | 0
2020-05-29 04:00 | 3581 |  |  | 0
2020-05-29 05:00 | 3582 |  |  | 0
2020-05-29 06:00 | 3583 |  |  | 0
2020-05-29 07:00 | 3584 |  |  | 0.018194
2020-05-29 08:00 | 3585 |  |  | 0.036388
2020-05-29 09:00 | 3586 |  |  | 0.069467
2020-05-29 10:00 | 3587 |  |  | 0.21833
2020-05-29 11:00 | 3588 |  |  | 0.32418
2020-05-29 12:00 | 3589 |  |  | 0.44658
2020-05-29 13:00 | 3590 |  |  | 0.45815
2020-05-29 14:00 | 3591 |  |  | 0.45154
2020-05-29 15:00 | 3592 |  |  | 0.6434
2020-05-29 16:00 | 3593 |  |  | 0.53093
2020-05-29 17:00 | 3594 |  |  | 0.38207
2020-05-29 18:00 | 3595 |  |  | 0.16209
2020-05-29 19:00 | 3596 |  |  | 0.013232
2020-05-29 20:00 | 3597 |  |  | 0
2020-05-29 21:00 | 3598 |  |  | 0
2020-05-29 22:00 | 3599 |  |  | 0
2020-05-29 23:00 | 3600 |  |  | 0
2020-05-30 | 3601 |  |  | 0
2020-05-30 01:00 | 3602 |  |  | 0
2020-05-30 02:00 | 3603 |  |  | 0
2020-05-30 03:00 | 3604 |  |  | 0
2020-05-30 04:00 | 3605 |  |  | 0
2020-05-30 05:00 | 3606 |  |  | 0
2020-05-30 06:00 | 3607 |  |  | 0.03308
2020-05-30 07:00 | 3608 |  |  | 0.12736
2020-05-30 08:00 | 3609 |  |  | 0.31757
2020-05-30 09:00 | 3610 |  |  | 0.49454
2020-05-30 10:00 | 3611 |  |  | 0.62355
2020-05-30 11:00 | 3612 |  |  | 0.71287
2020-05-30 12:00 | 3613 |  |  | 0.77407
2020-05-30 13:00 | 3614 |  |  | 0.65663
2020-05-30 14:00 | 3615 |  |  | 0.71783
2020-05-30 15:00 | 3616 |  |  | 0.63017
2020-05-30 16:00 | 3617 |  |  | 0.36222
2020-05-30 17:00 | 3618 |  |  | 0.034734
2020-05-30 18:00 | 3619 |  |  | 0.066159
2020-05-30 19:00 | 3620 |  |  | 0.01654
2020-05-30 20:00 | 3621 |  |  | 0
2020-05-30 21:00 | 3622 |  |  | 0
2020-05-30 22:00 | 3623 |  |  | 0
2020-05-30 23:00 | 3624 |  |  | 0
2020-05-31 | 3625 |  |  | 0
2020-05-31 01:00 | 3626 |  |  | 0
2020-05-31 02:00 | 3627 |  |  | 0
2020-05-31 03:00 | 3628 |  |  | 0
2020-05-31 04:00 | 3629 |  |  | 0
2020-05-31 05:00 | 3630 |  |  | 0
2020-05-31 06:00 | 3631 |  |  | 0.028118
2020-05-31 07:00 | 3632 |  |  | 0.046312
2020-05-31 08:00 | 3633 |  |  | 0.13232
2020-05-31 09:00 | 3634 |  |  | 0.32914
2020-05-31 10:00 | 3635 |  |  | 0.56236
2020-05-31 11:00 | 3636 |  |  | 0.52101
2020-05-31 12:00 | 3637 |  |  | 0.41515
2020-05-31 13:00 | 3638 |  |  | 0.66325
2020-05-31 14:00 | 3639 |  |  | 0.43169
2020-05-31 15:00 | 3640 |  |  | 0.20013
2020-05-31 16:00 | 3641 |  |  | 0.15382
2020-05-31 17:00 | 3642 |  |  | 0.34568
2020-05-31 18:00 | 3643 |  |  | 0.1472
2020-05-31 19:00 | 3644 |  |  | 0.011578
2020-05-31 20:00 | 3645 |  |  | 0
2020-05-31 21:00 | 3646 |  |  | 0
2020-05-31 22:00 | 3647 |  |  | 0
2020-05-31 23:00 | 3648 |  |  | 0
2020-06-01 | 3649 |  |  | 0
2020-06-01 01:00 | 3650 |  |  | 0
2020-06-01 02:00 | 3651 |  |  | 0
2020-06-01 03:00 | 3652 |  |  | 0
2020-06-01 04:00 | 3653 |  |  | 0
2020-06-01 05:00 | 3654 |  |  | 0
2020-06-01 06:00 | 3655 |  |  | 0.05789
2020-06-01 07:00 | 3656 |  |  | 0.1654
2020-06-01 08:00 | 3657 |  |  | 0.27456
2020-06-01 09:00 | 3658 |  |  | 0.435
2020-06-01 10:00 | 3659 |  |  | 0.47469
2020-06-01 11:00 | 3660 |  |  | 0.6037
2020-06-01 12:00 | 3661 |  |  | 0.71948
2020-06-01 13:00 | 3662 |  |  | 0.74099
2020-06-01 14:00 | 3663 |  |  | 0.7046
2020-06-01 15:00 | 3664 |  |  | 0.59543
2020-06-01 16:00 | 3665 |  |  | 0.25306
2020-06-01 17:00 | 3666 |  |  | 0.12736
2020-06-01 18:00 | 3667 |  |  | 0.089315
2020-06-01 19:00 | 3668 |  |  | 0
2020-06-01 20:00 | 3669 |  |  | 0
2020-06-01 21:00 | 3670 |  |  | 0
2020-06-01 22:00 | 3671 |  |  | 0
2020-06-01 23:00 | 3672 |  |  | 0
2020-06-02 | 3673 |  |  | 0
2020-06-02 01:00 | 3674 |  |  | 0
2020-06-02 02:00 | 3675 |  |  | 0
2020-06-02 03:00 | 3676 |  |  | 0
2020-06-02 04:00 | 3677 |  |  | 0
2020-06-02 05:00 | 3678 |  |  | 0
2020-06-02 06:00 | 3679 |  |  | 0.04135
2020-06-02 07:00 | 3680 |  |  | 0.13232
2020-06-02 08:00 | 3681 |  |  | 0.3093
2020-06-02 09:00 | 3682 |  |  | 0.47469
2020-06-02 10:00 | 3683 |  |  | 0.6004
2020-06-02 11:00 | 3684 |  |  | 0.70129
2020-06-02 12:00 | 3685 |  |  | 0.73272
2020-06-02 13:00 | 3686 |  |  | 0.75256
2020-06-02 14:00 | 3687 |  |  | 0.71452
2020-06-02 15:00 | 3688 |  |  | 0.49785
2020-06-02 16:00 | 3689 |  |  | 0.10586
2020-06-02 17:00 | 3690 |  |  | 0.23156
2020-06-02 18:00 | 3691 |  |  | 0.16705
2020-06-02 19:00 | 3692 |  |  | 0.011578
2020-06-02 20:00 | 3693 |  |  | 0
2020-06-02 21:00 | 3694 |  |  | 0
2020-06-02 22:00 | 3695 |  |  | 0
2020-06-02 23:00 | 3696 |  |  | 0
2020-06-03 | 3697 |  |  | 0
2020-06-03 01:00 | 3698 |  |  | 0
2020-06-03 02:00 | 3699 |  |  | 0
2020-06-03 03:00 | 3700 |  |  | 0
2020-06-03 04:00 | 3701 |  |  | 0
2020-06-03 05:00 | 3702 |  |  | 0
2020-06-03 06:00 | 3703 |  |  | 0.023156
2020-06-03 07:00 | 3704 |  |  | 0.12239
2020-06-03 08:00 | 3705 |  |  | 0.30103
2020-06-03 09:00 | 3706 |  |  | 0.46973
2020-06-03 10:00 | 3707 |  |  | 0.60205
2020-06-03 11:00 | 3708 |  |  | 0.61694
2020-06-03 12:00 | 3709 |  |  | 0.77407
2020-06-03 13:00 | 3710 |  |  | 0.51604
2020-06-03 14:00 | 3711 |  |  | 0.44658
2020-06-03 15:00 | 3712 |  |  | 0.34568
2020-06-03 16:00 | 3713 |  |  | 0.014886
2020-06-03 17:00 | 3714 |  |  | 0
2020-06-03 18:00 | 3715 |  |  | 0
2020-06-03 19:00 | 3716 |  |  | 0
2020-06-03 20:00 | 3717 |  |  | 0
2020-06-03 21:00 | 3718 |  |  | 0
2020-06-03 22:00 | 3719 |  |  | 0
2020-06-03 23:00 | 3720 |  |  | 0
2020-06-04 | 3721 |  |  | 0
2020-06-04 01:00 | 3722 |  |  | 0
2020-06-04 02:00 | 3723 |  |  | 0
2020-06-04 03:00 | 3724 |  |  | 0
2020-06-04 04:00 | 3725 |  |  | 0
2020-06-04 05:00 | 3726 |  |  | 0
2020-06-04 06:00 | 3727 |  |  | 0.003308
2020-06-04 07:00 | 3728 |  |  | 0.067813
2020-06-04 08:00 | 3729 |  |  | 0.13893
2020-06-04 09:00 | 3730 |  |  | 0.20675
2020-06-04 10:00 | 3731 |  |  | 0.25306
2020-06-04 11:00 | 3732 |  |  | 0.31426
2020-06-04 12:00 | 3733 |  |  | 0.22825
2020-06-04 13:00 | 3734 |  |  | 0.17532
2020-06-04 14:00 | 3735 |  |  | 0.20344
2020-06-04 15:00 | 3736 |  |  | 0.12239
2020-06-04 16:00 | 3737 |  |  | 0.04962
2020-06-04 17:00 | 3738 |  |  | 0.011578
2020-06-04 18:00 | 3739 |  |  | 0.001654
2020-06-04 19:00 | 3740 |  |  | 0
2020-06-04 20:00 | 3741 |  |  | 0
2020-06-04 21:00 | 3742 |  |  | 0
2020-06-04 22:00 | 3743 |  |  | 0
2020-06-04 23:00 | 3744 |  |  | 0
2020-06-05 | 3745 |  |  | 0
2020-06-05 01:00 | 3746 |  |  | 0
2020-06-05 02:00 | 3747 |  |  | 0
2020-06-05 03:00 | 3748 |  |  | 0
2020-06-05 04:00 | 3749 |  |  | 0
2020-06-05 05:00 | 3750 |  |  | 0
2020-06-05 06:00 | 3751 |  |  | 0.019848
2020-06-05 07:00 | 3752 |  |  | 0.12901
2020-06-05 08:00 | 3753 |  |  | 0.32749
2020-06-05 09:00 | 3754 |  |  | 0.51108
2020-06-05 10:00 | 3755 |  |  | 0.58882
2020-06-05 11:00 | 3756 |  |  | 0.54416
2020-06-05 12:00 | 3757 |  |  | 0.71783
2020-06-05 13:00 | 3758 |  |  | 0.71121
2020-06-05 14:00 | 3759 |  |  | 0.72941
2020-06-05 15:00 | 3760 |  |  | 0.68806
2020-06-05 16:00 | 3761 |  |  | 0.55574
2020-06-05 17:00 | 3762 |  |  | 0.38538
2020-06-05 18:00 | 3763 |  |  | 0.1869
2020-06-05 19:00 | 3764 |  |  | 0.01654
2020-06-05 20:00 | 3765 |  |  | 0
2020-06-05 21:00 | 3766 |  |  | 0
2020-06-05 22:00 | 3767 |  |  | 0
2020-06-05 23:00 | 3768 |  |  | 0
2020-06-06 | 3769 |  |  | 0
2020-06-06 01:00 | 3770 |  |  | 0
2020-06-06 02:00 | 3771 |  |  | 0
2020-06-06 03:00 | 3772 |  |  | 0
2020-06-06 04:00 | 3773 |  |  | 0
2020-06-06 05:00 | 3774 |  |  | 0
2020-06-06 06:00 | 3775 |  |  | 0.0099239
2020-06-06 07:00 | 3776 |  |  | 0.13563
2020-06-06 08:00 | 3777 |  |  | 0.31922
2020-06-06 09:00 | 3778 |  |  | 0.4995
2020-06-06 10:00 | 3779 |  |  | 0.63348
2020-06-06 11:00 | 3780 |  |  | 0.72279
2020-06-06 12:00 | 3781 |  |  | 0.39365
2020-06-06 13:00 | 3782 |  |  | 0.26133
2020-06-06 14:00 | 3783 |  |  | 0.44988
2020-06-06 15:00 | 3784 |  |  | 0.16374
2020-06-06 16:00 | 3785 |  |  | 0.051274
2020-06-06 17:00 | 3786 |  |  | 0.10916
2020-06-06 18:00 | 3787 |  |  | 0.056236
2020-06-06 19:00 | 3788 |  |  | 0
2020-06-06 20:00 | 3789 |  |  | 0
2020-06-06 21:00 | 3790 |  |  | 0
2020-06-06 22:00 | 3791 |  |  | 0
2020-06-06 23:00 | 3792 |  |  | 0
2020-06-07 | 3793 |  |  | 0
2020-06-07 01:00 | 3794 |  |  | 0
2020-06-07 02:00 | 3795 |  |  | 0
2020-06-07 03:00 | 3796 |  |  | 0
2020-06-07 04:00 | 3797 |  |  | 0
2020-06-07 05:00 | 3798 |  |  | 0.0082699
2020-06-07 06:00 | 3799 |  |  | 0
2020-06-07 07:00 | 3800 |  |  | 0.0082699
2020-06-07 08:00 | 3801 |  |  | 0.12239
2020-06-07 09:00 | 3802 |  |  | 0.19021
2020-06-07 10:00 | 3803 |  |  | 0.3308
2020-06-07 11:00 | 3804 |  |  | 0.5789
2020-06-07 12:00 | 3805 |  |  | 0.37876
2020-06-07 13:00 | 3806 |  |  | 0.70625
2020-06-07 14:00 | 3807 |  |  | 0.65829
2020-06-07 15:00 | 3808 |  |  | 0.4565
2020-06-07 16:00 | 3809 |  |  | 0.10089
2020-06-07 17:00 | 3810 |  |  | 0.051274
2020-06-07 18:00 | 3811 |  |  | 0.15713
2020-06-07 19:00 | 3812 |  |  | 0.0066159
2020-06-07 20:00 | 3813 |  |  | 0
2020-06-07 21:00 | 3814 |  |  | 0
2020-06-07 22:00 | 3815 |  |  | 0
2020-06-07 23:00 | 3816 |  |  | 0
2020-06-08 | 3817 |  |  | 0
2020-06-08 01:00 | 3818 |  |  | 0
2020-06-08 02:00 | 3819 |  |  | 0
2020-06-08 03:00 | 3820 |  |  | 0
2020-06-08 04:00 | 3821 |  |  | 0
2020-06-08 05:00 | 3822 |  |  | 0.023156
2020-06-08 06:00 | 3823 |  |  | 0.072775
2020-06-08 07:00 | 3824 |  |  | 0.14886
2020-06-08 08:00 | 3825 |  |  | 0.20675
2020-06-08 09:00 | 3826 |  |  | 0.36884
2020-06-08 10:00 | 3827 |  |  | 0.36553
2020-06-08 11:00 | 3828 |  |  | 0.4565
2020-06-08 12:00 | 3829 |  |  | 0.23983
2020-06-08 13:00 | 3830 |  |  | 0.081045
2020-06-08 14:00 | 3831 |  |  | 0.004962
2020-06-08 15:00 | 3832 |  |  | 0
2020-06-08 16:00 | 3833 |  |  | 0.072775
2020-06-08 17:00 | 3834 |  |  | 0.13397
2020-06-08 18:00 | 3835 |  |  | 0.19352
2020-06-08 19:00 | 3836 |  |  | 0.01654
2020-06-08 20:00 | 3837 |  |  | 0
2020-06-08 21:00 | 3838 |  |  | 0
2020-06-08 22:00 | 3839 |  |  | 0
2020-06-08 23:00 | 3840 |  |  | 0
2020-06-09 | 3841 |  |  | 0
2020-06-09 01:00 | 3842 |  |  | 0
2020-06-09 02:00 | 3843 |  |  | 0
2020-06-09 03:00 | 3844 |  |  | 0
2020-06-09 04:00 | 3845 |  |  | 0
2020-06-09 05:00 | 3846 |  |  | 0
2020-06-09 06:00 | 3847 |  |  | 0.023156
2020-06-09 07:00 | 3848 |  |  | 0.1472
2020-06-09 08:00 | 3849 |  |  | 0.32087
2020-06-09 09:00 | 3850 |  |  | 0.35726
2020-06-09 10:00 | 3851 |  |  | 0.51108
2020-06-09 11:00 | 3852 |  |  | 0.54416
2020-06-09 12:00 | 3853 |  |  | 0.70294
2020-06-09 13:00 | 3854 |  |  | 0.21006
2020-06-09 14:00 | 3855 |  |  | 0.12239
2020-06-09 15:00 | 3856 |  |  | 0
2020-06-09 16:00 | 3857 |  |  | 0
2020-06-09 17:00 | 3858 |  |  | 0.003308
2020-06-09 18:00 | 3859 |  |  | 0.043004
2020-06-09 19:00 | 3860 |  |  | 0.0066159
2020-06-09 20:00 | 3861 |  |  | 0
2020-06-09 21:00 | 3862 |  |  | 0
2020-06-09 22:00 | 3863 |  |  | 0
2020-06-09 23:00 | 3864 |  |  | 0
2020-06-10 | 3865 |  |  | 0
2020-06-10 01:00 | 3866 |  |  | 0
2020-06-10 02:00 | 3867 |  |  | 0
2020-06-10 03:00 | 3868 |  |  | 0
2020-06-10 04:00 | 3869 |  |  | 0
2020-06-10 05:00 | 3870 |  |  | 0.014886
2020-06-10 06:00 | 3871 |  |  | 0.069467
2020-06-10 07:00 | 3872 |  |  | 0.1472
2020-06-10 08:00 | 3873 |  |  | 0.33411
2020-06-10 09:00 | 3874 |  |  | 0.42342
2020-06-10 10:00 | 3875 |  |  | 0.31426
2020-06-10 11:00 | 3876 |  |  | 0.099239
2020-06-10 12:00 | 3877 |  |  | 0.46477
2020-06-10 13:00 | 3878 |  |  | 0.77076
2020-06-10 14:00 | 3879 |  |  | 0.46477
2020-06-10 15:00 | 3880 |  |  | 0.22329
2020-06-10 16:00 | 3881 |  |  | 0.21833
2020-06-10 17:00 | 3882 |  |  | 0.15547
2020-06-10 18:00 | 3883 |  |  | 0.043004
2020-06-10 19:00 | 3884 |  |  | 0.003308
2020-06-10 20:00 | 3885 |  |  | 0
2020-06-10 21:00 | 3886 |  |  | 0
2020-06-10 22:00 | 3887 |  |  | 0
2020-06-10 23:00 | 3888 |  |  | 0
2020-06-11 | 3889 |  |  | 0
2020-06-11 01:00 | 3890 |  |  | 0
2020-06-11 02:00 | 3891 |  |  | 0
2020-06-11 03:00 | 3892 |  |  | 0
2020-06-11 04:00 | 3893 |  |  | 0
2020-06-11 05:00 | 3894 |  |  | 0
2020-06-11 06:00 | 3895 |  |  | 0.01654
2020-06-11 07:00 | 3896 |  |  | 0.11743
2020-06-11 08:00 | 3897 |  |  | 0.16705
2020-06-11 09:00 | 3898 |  |  | 0.11578
2020-06-11 10:00 | 3899 |  |  | 0.10586
2020-06-11 11:00 | 3900 |  |  | 0.056236
2020-06-11 12:00 | 3901 |  |  | 0.13066
2020-06-11 13:00 | 3902 |  |  | 0.3308
2020-06-11 14:00 | 3903 |  |  | 0.20013
2020-06-11 15:00 | 3904 |  |  | 0.54085
2020-06-11 16:00 | 3905 |  |  | 0.17036
2020-06-11 17:00 | 3906 |  |  | 0.0082699
2020-06-11 18:00 | 3907 |  |  | 0.001654
2020-06-11 19:00 | 3908 |  |  | 0
2020-06-11 20:00 | 3909 |  |  | 0
2020-06-11 21:00 | 3910 |  |  | 0
2020-06-11 22:00 | 3911 |  |  | 0
2020-06-11 23:00 | 3912 |  |  | 0
2020-06-12 | 3913 |  |  | 0
2020-06-12 01:00 | 3914 |  |  | 0
2020-06-12 02:00 | 3915 |  |  | 0
2020-06-12 03:00 | 3916 |  |  | 0
2020-06-12 04:00 | 3917 |  |  | 0
2020-06-12 05:00 | 3918 |  |  | 0
2020-06-12 06:00 | 3919 |  |  | 0
2020-06-12 07:00 | 3920 |  |  | 0.084353
2020-06-12 08:00 | 3921 |  |  | 0.14224
2020-06-12 09:00 | 3922 |  |  | 0.18525
2020-06-12 10:00 | 3923 |  |  | 0.21171
2020-06-12 11:00 | 3924 |  |  | 0.14555
2020-06-12 12:00 | 3925 |  |  | 0.33907
2020-06-12 13:00 | 3926 |  |  | 0.19186
2020-06-12 14:00 | 3927 |  |  | 0.097585
2020-06-12 15:00 | 3928 |  |  | 0.084353
2020-06-12 16:00 | 3929 |  |  | 0.029772
2020-06-12 17:00 | 3930 |  |  | 0
2020-06-12 18:00 | 3931 |  |  | 0.013232
2020-06-12 19:00 | 3932 |  |  | 0
2020-06-12 20:00 | 3933 |  |  | 0
2020-06-12 21:00 | 3934 |  |  | 0
2020-06-12 22:00 | 3935 |  |  | 0
2020-06-12 23:00 | 3936 |  |  | 0
2020-06-13 | 3937 |  |  | 0
2020-06-13 01:00 | 3938 |  |  | 0
2020-06-13 02:00 | 3939 |  |  | 0
2020-06-13 03:00 | 3940 |  |  | 0
2020-06-13 04:00 | 3941 |  |  | 0
2020-06-13 05:00 | 3942 |  |  | 0
2020-06-13 06:00 | 3943 |  |  | 0.05789
2020-06-13 07:00 | 3944 |  |  | 0.17201
2020-06-13 08:00 | 3945 |  |  | 0.29606
2020-06-13 09:00 | 3946 |  |  | 0.41846
2020-06-13 10:00 | 3947 |  |  | 0.49123
2020-06-13 11:00 | 3948 |  |  | 0.40192
2020-06-13 12:00 | 3949 |  |  | 0.1654
2020-06-13 13:00 | 3950 |  |  | 0.039696
2020-06-13 14:00 | 3951 |  |  | 0.054582
2020-06-13 15:00 | 3952 |  |  | 0.084353
2020-06-13 16:00 | 3953 |  |  | 0.004962
2020-06-13 17:00 | 3954 |  |  | 0.14555
2020-06-13 18:00 | 3955 |  |  | 0.13397
2020-06-13 19:00 | 3956 |  |  | 0.023156
2020-06-13 20:00 | 3957 |  |  | 0
2020-06-13 21:00 | 3958 |  |  | 0
2020-06-13 22:00 | 3959 |  |  | 0
2020-06-13 23:00 | 3960 |  |  | 0
2020-06-14 | 3961 |  |  | 0
2020-06-14 01:00 | 3962 |  |  | 0
2020-06-14 02:00 | 3963 |  |  | 0
2020-06-14 03:00 | 3964 |  |  | 0
2020-06-14 04:00 | 3965 |  |  | 0
2020-06-14 05:00 | 3966 |  |  | 0.004962
2020-06-14 06:00 | 3967 |  |  | 0.043004
2020-06-14 07:00 | 3968 |  |  | 0.11413
2020-06-14 08:00 | 3969 |  |  | 0.32418
2020-06-14 09:00 | 3970 |  |  | 0.49123
2020-06-14 10:00 | 3971 |  |  | 0.62355
2020-06-14 11:00 | 3972 |  |  | 0.71121
2020-06-14 12:00 | 3973 |  |  | 0.73768
2020-06-14 13:00 | 3974 |  |  | 0.75422
2020-06-14 14:00 | 3975 |  |  | 0.71948
2020-06-14 15:00 | 3976 |  |  | 0.65167
2020-06-14 16:00 | 3977 |  |  | 0.55078
2020-06-14 17:00 | 3978 |  |  | 0.38207
2020-06-14 18:00 | 3979 |  |  | 0.1654
2020-06-14 19:00 | 3980 |  |  | 0.034734
2020-06-14 20:00 | 3981 |  |  | 0
2020-06-14 21:00 | 3982 |  |  | 0
2020-06-14 22:00 | 3983 |  |  | 0
2020-06-14 23:00 | 3984 |  |  | 0
2020-06-15 | 3985 |  |  | 0
2020-06-15 01:00 | 3986 |  |  | 0
2020-06-15 02:00 | 3987 |  |  | 0
2020-06-15 03:00 | 3988 |  |  | 0
2020-06-15 04:00 | 3989 |  |  | 0
2020-06-15 05:00 | 3990 |  |  | 0.021502
2020-06-15 06:00 | 3991 |  |  | 0.044658
2020-06-15 07:00 | 3992 |  |  | 0.13893
2020-06-15 08:00 | 3993 |  |  | 0.16871
2020-06-15 09:00 | 3994 |  |  | 0.43665
2020-06-15 10:00 | 3995 |  |  | 0.61859
2020-06-15 11:00 | 3996 |  |  | 0.66821
2020-06-15 12:00 | 3997 |  |  | 0.73933
2020-06-15 13:00 | 3998 |  |  | 0.75256
2020-06-15 14:00 | 3999 |  |  | 0.59213
2020-06-15 15:00 | 4000 |  |  | 0.27787
2020-06-15 16:00 | 4001 |  |  | 0.15217
2020-06-15 17:00 | 4002 |  |  | 0.11909
2020-06-15 18:00 | 4003 |  |  | 0.04962
2020-06-15 19:00 | 4004 |  |  | 0
2020-06-15 20:00 | 4005 |  |  | 0
2020-06-15 21:00 | 4006 |  |  | 0
2020-06-15 22:00 | 4007 |  |  | 0
2020-06-15 23:00 | 4008 |  |  | 0
2020-06-16 | 4009 |  |  | 0
2020-06-16 01:00 | 4010 |  |  | 0
2020-06-16 02:00 | 4011 |  |  | 0
2020-06-16 03:00 | 4012 |  |  | 0
2020-06-16 04:00 | 4013 |  |  | 0
2020-06-16 05:00 | 4014 |  |  | 0
2020-06-16 06:00 | 4015 |  |  | 0.031426
2020-06-16 07:00 | 4016 |  |  | 0.11909
2020-06-16 08:00 | 4017 |  |  | 0.31922
2020-06-16 09:00 | 4018 |  |  | 0.48131
2020-06-16 10:00 | 4019 |  |  | 0.57228
2020-06-16 11:00 | 4020 |  |  | 0.6649
2020-06-16 12:00 | 4021 |  |  | 0.77572
2020-06-16 13:00 | 4022 |  |  | 0.54912
2020-06-16 14:00 | 4023 |  |  | 0.13728
2020-06-16 15:00 | 4024 |  |  | 0.038042
2020-06-16 16:00 | 4025 |  |  | 0.11578
2020-06-16 17:00 | 4026 |  |  | 0.10089
2020-06-16 18:00 | 4027 |  |  | 0.079391
2020-06-16 19:00 | 4028 |  |  | 0
2020-06-16 20:00 | 4029 |  |  | 0
2020-06-16 21:00 | 4030 |  |  | 0
2020-06-16 22:00 | 4031 |  |  | 0
2020-06-16 23:00 | 4032 |  |  | 0
2020-06-17 | 4033 |  |  | 0
2020-06-17 01:00 | 4034 |  |  | 0
2020-06-17 02:00 | 4035 |  |  | 0
2020-06-17 03:00 | 4036 |  |  | 0
2020-06-17 04:00 | 4037 |  |  | 0
2020-06-17 05:00 | 4038 |  |  | 0
2020-06-17 06:00 | 4039 |  |  | 0.028118
2020-06-17 07:00 | 4040 |  |  | 0.10089
2020-06-17 08:00 | 4041 |  |  | 0.31922
2020-06-17 09:00 | 4042 |  |  | 0.4135
2020-06-17 10:00 | 4043 |  |  | 0.38538
2020-06-17 11:00 | 4044 |  |  | 0.53755
2020-06-17 12:00 | 4045 |  |  | 0.17201
2020-06-17 13:00 | 4046 |  |  | 0.45154
2020-06-17 14:00 | 4047 |  |  | 0.29937
2020-06-17 15:00 | 4048 |  |  | 0.089315
2020-06-17 16:00 | 4049 |  |  | 0
2020-06-17 17:00 | 4050 |  |  | 0.03308
2020-06-17 18:00 | 4051 |  |  | 0.044658
2020-06-17 19:00 | 4052 |  |  | 0.01654
2020-06-17 20:00 | 4053 |  |  | 0
2020-06-17 21:00 | 4054 |  |  | 0
2020-06-17 22:00 | 4055 |  |  | 0
2020-06-17 23:00 | 4056 |  |  | 0
2020-06-18 | 4057 |  |  | 0
2020-06-18 01:00 | 4058 |  |  | 0
2020-06-18 02:00 | 4059 |  |  | 0
2020-06-18 03:00 | 4060 |  |  | 0
2020-06-18 04:00 | 4061 |  |  | 0
2020-06-18 05:00 | 4062 |  |  | 0
2020-06-18 06:00 | 4063 |  |  | 0.028118
2020-06-18 07:00 | 4064 |  |  | 0.15878
2020-06-18 08:00 | 4065 |  |  | 0.31591
2020-06-18 09:00 | 4066 |  |  | 0.50116
2020-06-18 10:00 | 4067 |  |  | 0.56566
2020-06-18 11:00 | 4068 |  |  | 0.71618
2020-06-18 12:00 | 4069 |  |  | 0.65002
2020-06-18 13:00 | 4070 |  |  | 0.50777
2020-06-18 14:00 | 4071 |  |  | 0.23487
2020-06-18 15:00 | 4072 |  |  | 0.15051
2020-06-18 16:00 | 4073 |  |  | 0.26629
2020-06-18 17:00 | 4074 |  |  | 0.02481
2020-06-18 18:00 | 4075 |  |  | 0.023156
2020-06-18 19:00 | 4076 |  |  | 0
2020-06-18 20:00 | 4077 |  |  | 0
2020-06-18 21:00 | 4078 |  |  | 0
2020-06-18 22:00 | 4079 |  |  | 0
2020-06-18 23:00 | 4080 |  |  | 0
2020-06-19 | 4081 |  |  | 0
2020-06-19 01:00 | 4082 |  |  | 0
2020-06-19 02:00 | 4083 |  |  | 0
2020-06-19 03:00 | 4084 |  |  | 0
2020-06-19 04:00 | 4085 |  |  | 0
2020-06-19 05:00 | 4086 |  |  | 0
2020-06-19 06:00 | 4087 |  |  | 0.0066159
2020-06-19 07:00 | 4088 |  |  | 0.11743
2020-06-19 08:00 | 4089 |  |  | 0.31757
2020-06-19 09:00 | 4090 |  |  | 0.50116
2020-06-19 10:00 | 4091 |  |  | 0.63348
2020-06-19 11:00 | 4092 |  |  | 0.7261
2020-06-19 12:00 | 4093 |  |  | 0.70791
2020-06-19 13:00 | 4094 |  |  | 0.36057
2020-06-19 14:00 | 4095 |  |  | 0.33245
2020-06-19 15:00 | 4096 |  |  | 0.37545
2020-06-19 16:00 | 4097 |  |  | 0.54251
2020-06-19 17:00 | 4098 |  |  | 0.36388
2020-06-19 18:00 | 4099 |  |  | 0.19021
2020-06-19 19:00 | 4100 |  |  | 0.001654
2020-06-19 20:00 | 4101 |  |  | 0
2020-06-19 21:00 | 4102 |  |  | 0
2020-06-19 22:00 | 4103 |  |  | 0
2020-06-19 23:00 | 4104 |  |  | 0
2020-06-20 | 4105 |  |  | 0
2020-06-20 01:00 | 4106 |  |  | 0
2020-06-20 02:00 | 4107 |  |  | 0
2020-06-20 03:00 | 4108 |  |  | 0
2020-06-20 04:00 | 4109 |  |  | 0
2020-06-20 05:00 | 4110 |  |  | 0.023156
2020-06-20 06:00 | 4111 |  |  | 0.089315
2020-06-20 07:00 | 4112 |  |  | 0.17201
2020-06-20 08:00 | 4113 |  |  | 0.3093
2020-06-20 09:00 | 4114 |  |  | 0.48627
2020-06-20 10:00 | 4115 |  |  | 0.61859
2020-06-20 11:00 | 4116 |  |  | 0.6831
2020-06-20 12:00 | 4117 |  |  | 0.77903
2020-06-20 13:00 | 4118 |  |  | 0.79226
2020-06-20 14:00 | 4119 |  |  | 0.73272
2020-06-20 15:00 | 4120 |  |  | 0.64505
2020-06-20 16:00 | 4121 |  |  | 0.28779
2020-06-20 17:00 | 4122 |  |  | 0.37215
2020-06-20 18:00 | 4123 |  |  | 0.17863
2020-06-20 19:00 | 4124 |  |  | 0.019848
2020-06-20 20:00 | 4125 |  |  | 0
2020-06-20 21:00 | 4126 |  |  | 0
2020-06-20 22:00 | 4127 |  |  | 0
2020-06-20 23:00 | 4128 |  |  | 0
2020-06-21 | 4129 |  |  | 0
2020-06-21 01:00 | 4130 |  |  | 0
2020-06-21 02:00 | 4131 |  |  | 0
2020-06-21 03:00 | 4132 |  |  | 0
2020-06-21 04:00 | 4133 |  |  | 0
2020-06-21 05:00 | 4134 |  |  | 0
2020-06-21 06:00 | 4135 |  |  | 0.004962
2020-06-21 07:00 | 4136 |  |  | 0.11247
2020-06-21 08:00 | 4137 |  |  | 0.29772
2020-06-21 09:00 | 4138 |  |  | 0.4962
2020-06-21 10:00 | 4139 |  |  | 0.63182
2020-06-21 11:00 | 4140 |  |  | 0.70791
2020-06-21 12:00 | 4141 |  |  | 0.6864
2020-06-21 13:00 | 4142 |  |  | 0.75091
2020-06-21 14:00 | 4143 |  |  | 0.71618
2020-06-21 15:00 | 4144 |  |  | 0.65498
2020-06-21 16:00 | 4145 |  |  | 0.53589
2020-06-21 17:00 | 4146 |  |  | 0.36222
2020-06-21 18:00 | 4147 |  |  | 0.18855
2020-06-21 19:00 | 4148 |  |  | 0.019848
2020-06-21 20:00 | 4149 |  |  | 0
2020-06-21 21:00 | 4150 |  |  | 0
2020-06-21 22:00 | 4151 |  |  | 0
2020-06-21 23:00 | 4152 |  |  | 0
2020-06-22 | 4153 |  |  | 0
2020-06-22 01:00 | 4154 |  |  | 0
2020-06-22 02:00 | 4155 |  |  | 0
2020-06-22 03:00 | 4156 |  |  | 0
2020-06-22 04:00 | 4157 |  |  | 0
2020-06-22 05:00 | 4158 |  |  | 0
2020-06-22 06:00 | 4159 |  |  | 0.001654
2020-06-22 07:00 | 4160 |  |  | 0.11247
2020-06-22 08:00 | 4161 |  |  | 0.31095
2020-06-22 09:00 | 4162 |  |  | 0.48131
2020-06-22 10:00 | 4163 |  |  | 0.60867
2020-06-22 11:00 | 4164 |  |  | 0.70791
2020-06-22 12:00 | 4165 |  |  | 0.74429
2020-06-22 13:00 | 4166 |  |  | 0.73768
2020-06-22 14:00 | 4167 |  |  | 0.71121
2020-06-22 15:00 | 4168 |  |  | 0.64175
2020-06-22 16:00 | 4169 |  |  | 0.51439
2020-06-22 17:00 | 4170 |  |  | 0.35395
2020-06-22 18:00 | 4171 |  |  | 0.1439
2020-06-22 19:00 | 4172 |  |  | 0
2020-06-22 20:00 | 4173 |  |  | 0
2020-06-22 21:00 | 4174 |  |  | 0
2020-06-22 22:00 | 4175 |  |  | 0
2020-06-22 23:00 | 4176 |  |  | 0
2020-06-23 | 4177 |  |  | 0
2020-06-23 01:00 | 4178 |  |  | 0
2020-06-23 02:00 | 4179 |  |  | 0
2020-06-23 03:00 | 4180 |  |  | 0
2020-06-23 04:00 | 4181 |  |  | 0
2020-06-23 05:00 | 4182 |  |  | 0
2020-06-23 06:00 | 4183 |  |  | 0.0066159
2020-06-23 07:00 | 4184 |  |  | 0.11413
2020-06-23 08:00 | 4185 |  |  | 0.30103
2020-06-23 09:00 | 4186 |  |  | 0.46146
2020-06-23 10:00 | 4187 |  |  | 0.59378
2020-06-23 11:00 | 4188 |  |  | 0.70294
2020-06-23 12:00 | 4189 |  |  | 0.70294
2020-06-23 13:00 | 4190 |  |  | 0.7261
2020-06-23 14:00 | 4191 |  |  | 0.70294
2020-06-23 15:00 | 4192 |  |  | 0.61694
2020-06-23 16:00 | 4193 |  |  | 0.52266
2020-06-23 17:00 | 4194 |  |  | 0.36388
2020-06-23 18:00 | 4195 |  |  | 0.18194
2020-06-23 19:00 | 4196 |  |  | 0.018194
2020-06-23 20:00 | 4197 |  |  | 0
2020-06-23 21:00 | 4198 |  |  | 0
2020-06-23 22:00 | 4199 |  |  | 0
2020-06-23 23:00 | 4200 |  |  | 0
2020-06-24 | 4201 |  |  | 0
2020-06-24 01:00 | 4202 |  |  | 0
2020-06-24 02:00 | 4203 |  |  | 0
2020-06-24 03:00 | 4204 |  |  | 0
2020-06-24 04:00 | 4205 |  |  | 0
2020-06-24 05:00 | 4206 |  |  | 0
2020-06-24 06:00 | 4207 |  |  | 0.004962
2020-06-24 07:00 | 4208 |  |  | 0.081045
2020-06-24 08:00 | 4209 |  |  | 0.24644
2020-06-24 09:00 | 4210 |  |  | 0.47469
2020-06-24 10:00 | 4211 |  |  | 0.6037
2020-06-24 11:00 | 4212 |  |  | 0.69633
2020-06-24 12:00 | 4213 |  |  | 0.69798
2020-06-24 13:00 | 4214 |  |  | 0.60867
2020-06-24 14:00 | 4215 |  |  | 0.52762
2020-06-24 15:00 | 4216 |  |  | 0.44327
2020-06-24 16:00 | 4217 |  |  | 0.27291
2020-06-24 17:00 | 4218 |  |  | 0.31922
2020-06-24 18:00 | 4219 |  |  | 0.12239
2020-06-24 19:00 | 4220 |  |  | 0.0099239
2020-06-24 20:00 | 4221 |  |  | 0
2020-06-24 21:00 | 4222 |  |  | 0
2020-06-24 22:00 | 4223 |  |  | 0
2020-06-24 23:00 | 4224 |  |  | 0
2020-06-25 | 4225 |  |  | 0
2020-06-25 01:00 | 4226 |  |  | 0
2020-06-25 02:00 | 4227 |  |  | 0
2020-06-25 03:00 | 4228 |  |  | 0
2020-06-25 04:00 | 4229 |  |  | 0
2020-06-25 05:00 | 4230 |  |  | 0
2020-06-25 06:00 | 4231 |  |  | 0.0066159
2020-06-25 07:00 | 4232 |  |  | 0.072775
2020-06-25 08:00 | 4233 |  |  | 0.19848
2020-06-25 09:00 | 4234 |  |  | 0.38703
2020-06-25 10:00 | 4235 |  |  | 0.54582
2020-06-25 11:00 | 4236 |  |  | 0.65829
2020-06-25 12:00 | 4237 |  |  | 0.7261
2020-06-25 13:00 | 4238 |  |  | 0.54912
2020-06-25 14:00 | 4239 |  |  | 0.4565
2020-06-25 15:00 | 4240 |  |  | 0.1654
2020-06-25 16:00 | 4241 |  |  | 0.1042
2020-06-25 17:00 | 4242 |  |  | 0.14555
2020-06-25 18:00 | 4243 |  |  | 0.003308
2020-06-25 19:00 | 4244 |  |  | 0
2020-06-25 20:00 | 4245 |  |  | 0
2020-06-25 21:00 | 4246 |  |  | 0
2020-06-25 22:00 | 4247 |  |  | 0
2020-06-25 23:00 | 4248 |  |  | 0
2020-06-26 | 4249 |  |  | 0
2020-06-26 01:00 | 4250 |  |  | 0
2020-06-26 02:00 | 4251 |  |  | 0
2020-06-26 03:00 | 4252 |  |  | 0
2020-06-26 04:00 | 4253 |  |  | 0
2020-06-26 05:00 | 4254 |  |  | 0
2020-06-26 06:00 | 4255 |  |  | 0.043004
2020-06-26 07:00 | 4256 |  |  | 0.1042
2020-06-26 08:00 | 4257 |  |  | 0.19352
2020-06-26 09:00 | 4258 |  |  | 0.20013
2020-06-26 10:00 | 4259 |  |  | 0.47469
2020-06-26 11:00 | 4260 |  |  | 0.63678
2020-06-26 12:00 | 4261 |  |  | 0.23321
2020-06-26 13:00 | 4262 |  |  | 0.30599
2020-06-26 14:00 | 4263 |  |  | 0.39034
2020-06-26 15:00 | 4264 |  |  | 0.30599
2020-06-26 16:00 | 4265 |  |  | 0.17036
2020-06-26 17:00 | 4266 |  |  | 0.077737
2020-06-26 18:00 | 4267 |  |  | 0.021502
2020-06-26 19:00 | 4268 |  |  | 0.034734
2020-06-26 20:00 | 4269 |  |  | 0
2020-06-26 21:00 | 4270 |  |  | 0
2020-06-26 22:00 | 4271 |  |  | 0
2020-06-26 23:00 | 4272 |  |  | 0
2020-06-27 | 4273 |  |  | 0
2020-06-27 01:00 | 4274 |  |  | 0
2020-06-27 02:00 | 4275 |  |  | 0
2020-06-27 03:00 | 4276 |  |  | 0
2020-06-27 04:00 | 4277 |  |  | 0
2020-06-27 05:00 | 4278 |  |  | 0.011578
2020-06-27 06:00 | 4279 |  |  | 0.064505
2020-06-27 07:00 | 4280 |  |  | 0.13728
2020-06-27 08:00 | 4281 |  |  | 0.2911
2020-06-27 09:00 | 4282 |  |  | 0.435
2020-06-27 10:00 | 4283 |  |  | 0.58055
2020-06-27 11:00 | 4284 |  |  | 0.69302
2020-06-27 12:00 | 4285 |  |  | 0.70294
2020-06-27 13:00 | 4286 |  |  | 0.61363
2020-06-27 14:00 | 4287 |  |  | 0.24314
2020-06-27 15:00 | 4288 |  |  | 0.0082699
2020-06-27 16:00 | 4289 |  |  | 0.046312
2020-06-27 17:00 | 4290 |  |  | 0.043004
2020-06-27 18:00 | 4291 |  |  | 0.046312
2020-06-27 19:00 | 4292 |  |  | 0.011578
2020-06-27 20:00 | 4293 |  |  | 0
2020-06-27 21:00 | 4294 |  |  | 0
2020-06-27 22:00 | 4295 |  |  | 0
2020-06-27 23:00 | 4296 |  |  | 0
2020-06-28 | 4297 |  |  | 0
2020-06-28 01:00 | 4298 |  |  | 0
2020-06-28 02:00 | 4299 |  |  | 0
2020-06-28 03:00 | 4300 |  |  | 0
2020-06-28 04:00 | 4301 |  |  | 0
2020-06-28 05:00 | 4302 |  |  | 0
2020-06-28 06:00 | 4303 |  |  | 0.03308
2020-06-28 07:00 | 4304 |  |  | 0.1042
2020-06-28 08:00 | 4305 |  |  | 0.29606
2020-06-28 09:00 | 4306 |  |  | 0.46973
2020-06-28 10:00 | 4307 |  |  | 0.58551
2020-06-28 11:00 | 4308 |  |  | 0.69137
2020-06-28 12:00 | 4309 |  |  | 0.72279
2020-06-28 13:00 | 4310 |  |  | 0.59709
2020-06-28 14:00 | 4311 |  |  | 0.63182
2020-06-28 15:00 | 4312 |  |  | 0.39696
2020-06-28 16:00 | 4313 |  |  | 0.33907
2020-06-28 17:00 | 4314 |  |  | 0.2266
2020-06-28 18:00 | 4315 |  |  | 0.17863
2020-06-28 19:00 | 4316 |  |  | 0.013232
2020-06-28 20:00 | 4317 |  |  | 0
2020-06-28 21:00 | 4318 |  |  | 0
2020-06-28 22:00 | 4319 |  |  | 0
2020-06-28 23:00 | 4320 |  |  | 0
2020-06-29 | 4321 |  |  | 0
2020-06-29 01:00 | 4322 |  |  | 0
2020-06-29 02:00 | 4323 |  |  | 0
2020-06-29 03:00 | 4324 |  |  | 0
2020-06-29 04:00 | 4325 |  |  | 0
2020-06-29 05:00 | 4326 |  |  | 0
2020-06-29 06:00 | 4327 |  |  | 0.01654
2020-06-29 07:00 | 4328 |  |  | 0.12405
2020-06-29 08:00 | 4329 |  |  | 0.37049
2020-06-29 09:00 | 4330 |  |  | 0.53258
2020-06-29 10:00 | 4331 |  |  | 0.6649
2020-06-29 11:00 | 4332 |  |  | 0.65332
2020-06-29 12:00 | 4333 |  |  | 0.7261
2020-06-29 13:00 | 4334 |  |  | 0.66656
2020-06-29 14:00 | 4335 |  |  | 0.68806
2020-06-29 15:00 | 4336 |  |  | 0.62024
2020-06-29 16:00 | 4337 |  |  | 0.52266
2020-06-29 17:00 | 4338 |  |  | 0.35726
2020-06-29 18:00 | 4339 |  |  | 0.18194
2020-06-29 19:00 | 4340 |  |  | 0.028118
2020-06-29 20:00 | 4341 |  |  | 0
2020-06-29 21:00 | 4342 |  |  | 0
2020-06-29 22:00 | 4343 |  |  | 0
2020-06-29 23:00 | 4344 |  |  | 0
2020-06-30 | 4345 |  |  | 0
2020-06-30 01:00 | 4346 |  |  | 0
2020-06-30 02:00 | 4347 |  |  | 0
2020-06-30 03:00 | 4348 |  |  | 0
2020-06-30 04:00 | 4349 |  |  | 0
2020-06-30 05:00 | 4350 |  |  | 0
2020-06-30 06:00 | 4351 |  |  | 0.028118
2020-06-30 07:00 | 4352 |  |  | 0.15713
2020-06-30 08:00 | 4353 |  |  | 0.21667
2020-06-30 09:00 | 4354 |  |  | 0.26464
2020-06-30 10:00 | 4355 |  |  | 0.34899
2020-06-30 11:00 | 4356 |  |  | 0.52762
2020-06-30 12:00 | 4357 |  |  | 0.46808
2020-06-30 13:00 | 4358 |  |  | 0.4565
2020-06-30 14:00 | 4359 |  |  | 0.26464
2020-06-30 15:00 | 4360 |  |  | 0.20344
2020-06-30 16:00 | 4361 |  |  | 0.13232
2020-06-30 17:00 | 4362 |  |  | 0.13397
2020-06-30 18:00 | 4363 |  |  | 0.038042
2020-06-30 19:00 | 4364 |  |  | 0
2020-06-30 20:00 | 4365 |  |  | 0
2020-06-30 21:00 | 4366 |  |  | 0
2020-06-30 22:00 | 4367 |  |  | 0
2020-06-30 23:00 | 4368 |  |  | 0
2020-07-01 | 4369 |  |  | 0
2020-07-01 01:00 | 4370 |  |  | 0
2020-07-01 02:00 | 4371 |  |  | 0
2020-07-01 03:00 | 4372 |  |  | 0
2020-07-01 04:00 | 4373 |  |  | 0
2020-07-01 05:00 | 4374 |  |  | 0.01654
2020-07-01 06:00 | 4375 |  |  | 0.069467
2020-07-01 07:00 | 4376 |  |  | 0.14224
2020-07-01 08:00 | 4377 |  |  | 0.25471
2020-07-01 09:00 | 4378 |  |  | 0.43831
2020-07-01 10:00 | 4379 |  |  | 0.40523
2020-07-01 11:00 | 4380 |  |  | 0.31095
2020-07-01 12:00 | 4381 |  |  | 0.20344
2020-07-01 13:00 | 4382 |  |  | 0.27456
2020-07-01 14:00 | 4383 |  |  | 0.12405
2020-07-01 15:00 | 4384 |  |  | 0.38869
2020-07-01 16:00 | 4385 |  |  | 0.19682
2020-07-01 17:00 | 4386 |  |  | 0.021502
2020-07-01 18:00 | 4387 |  |  | 0.056236
2020-07-01 19:00 | 4388 |  |  | 0
2020-07-01 20:00 | 4389 |  |  | 0
2020-07-01 21:00 | 4390 |  |  | 0
2020-07-01 22:00 | 4391 |  |  | 0
2020-07-01 23:00 | 4392 |  |  | 0
2020-07-02 | 4393 |  |  | 0
2020-07-02 01:00 | 4394 |  |  | 0
2020-07-02 02:00 | 4395 |  |  | 0
2020-07-02 03:00 | 4396 |  |  | 0
2020-07-02 04:00 | 4397 |  |  | 0
2020-07-02 05:00 | 4398 |  |  | 0
2020-07-02 06:00 | 4399 |  |  | 0.013232
2020-07-02 07:00 | 4400 |  |  | 0.11082
2020-07-02 08:00 | 4401 |  |  | 0.25306
2020-07-02 09:00 | 4402 |  |  | 0.33907
2020-07-02 10:00 | 4403 |  |  | 0.59709
2020-07-02 11:00 | 4404 |  |  | 0.70129
2020-07-02 12:00 | 4405 |  |  | 0.71287
2020-07-02 13:00 | 4406 |  |  | 0.60205
2020-07-02 14:00 | 4407 |  |  | 0.42838
2020-07-02 15:00 | 4408 |  |  | 0.42342
2020-07-02 16:00 | 4409 |  |  | 0.16044
2020-07-02 17:00 | 4410 |  |  | 0.038042
2020-07-02 18:00 | 4411 |  |  | 0.13728
2020-07-02 19:00 | 4412 |  |  | 0.021502
2020-07-02 20:00 | 4413 |  |  | 0
2020-07-02 21:00 | 4414 |  |  | 0
2020-07-02 22:00 | 4415 |  |  | 0
2020-07-02 23:00 | 4416 |  |  | 0
2020-07-03 | 4417 |  |  | 0
2020-07-03 01:00 | 4418 |  |  | 0
2020-07-03 02:00 | 4419 |  |  | 0
2020-07-03 03:00 | 4420 |  |  | 0
2020-07-03 04:00 | 4421 |  |  | 0
2020-07-03 05:00 | 4422 |  |  | 0
2020-07-03 06:00 | 4423 |  |  | 0.0082699
2020-07-03 07:00 | 4424 |  |  | 0.11082
2020-07-03 08:00 | 4425 |  |  | 0.28614
2020-07-03 09:00 | 4426 |  |  | 0.46312
2020-07-03 10:00 | 4427 |  |  | 0.59709
2020-07-03 11:00 | 4428 |  |  | 0.69633
2020-07-03 12:00 | 4429 |  |  | 0.54251
2020-07-03 13:00 | 4430 |  |  | 0.43334
2020-07-03 14:00 | 4431 |  |  | 0.062851
2020-07-03 15:00 | 4432 |  |  | 0.026464
2020-07-03 16:00 | 4433 |  |  | 0
2020-07-03 17:00 | 4434 |  |  | 0
2020-07-03 18:00 | 4435 |  |  | 0
2020-07-03 19:00 | 4436 |  |  | 0
2020-07-03 20:00 | 4437 |  |  | 0
2020-07-03 21:00 | 4438 |  |  | 0
2020-07-03 22:00 | 4439 |  |  | 0
2020-07-03 23:00 | 4440 |  |  | 0
2020-07-04 | 4441 |  |  | 0
2020-07-04 01:00 | 4442 |  |  | 0
2020-07-04 02:00 | 4443 |  |  | 0
2020-07-04 03:00 | 4444 |  |  | 0
2020-07-04 04:00 | 4445 |  |  | 0
2020-07-04 05:00 | 4446 |  |  | 0
2020-07-04 06:00 | 4447 |  |  | 0
2020-07-04 07:00 | 4448 |  |  | 0.10089
2020-07-04 08:00 | 4449 |  |  | 0.29276
2020-07-04 09:00 | 4450 |  |  | 0.478
2020-07-04 10:00 | 4451 |  |  | 0.59709
2020-07-04 11:00 | 4452 |  |  | 0.70294
2020-07-04 12:00 | 4453 |  |  | 0.74099
2020-07-04 13:00 | 4454 |  |  | 0.74429
2020-07-04 14:00 | 4455 |  |  | 0.71618
2020-07-04 15:00 | 4456 |  |  | 0.63513
2020-07-04 16:00 | 4457 |  |  | 0.52762
2020-07-04 17:00 | 4458 |  |  | 0.36718
2020-07-04 18:00 | 4459 |  |  | 0.18855
2020-07-04 19:00 | 4460 |  |  | 0.021502
2020-07-04 20:00 | 4461 |  |  | 0
2020-07-04 21:00 | 4462 |  |  | 0
2020-07-04 22:00 | 4463 |  |  | 0
2020-07-04 23:00 | 4464 |  |  | 0
2020-07-05 | 4465 |  |  | 0
2020-07-05 01:00 | 4466 |  |  | 0
2020-07-05 02:00 | 4467 |  |  | 0
2020-07-05 03:00 | 4468 |  |  | 0
2020-07-05 04:00 | 4469 |  |  | 0
2020-07-05 05:00 | 4470 |  |  | 0
2020-07-05 06:00 | 4471 |  |  | 0
2020-07-05 07:00 | 4472 |  |  | 0.10255
2020-07-05 08:00 | 4473 |  |  | 0.2911
2020-07-05 09:00 | 4474 |  |  | 0.46312
2020-07-05 10:00 | 4475 |  |  | 0.59378
2020-07-05 11:00 | 4476 |  |  | 0.69798
2020-07-05 12:00 | 4477 |  |  | 0.71783
2020-07-05 13:00 | 4478 |  |  | 0.70294
2020-07-05 14:00 | 4479 |  |  | 0.71121
2020-07-05 15:00 | 4480 |  |  | 0.64175
2020-07-05 16:00 | 4481 |  |  | 0.52762
2020-07-05 17:00 | 4482 |  |  | 0.36884
2020-07-05 18:00 | 4483 |  |  | 0.18194
2020-07-05 19:00 | 4484 |  |  | 0.019848
2020-07-05 20:00 | 4485 |  |  | 0
2020-07-05 21:00 | 4486 |  |  | 0
2020-07-05 22:00 | 4487 |  |  | 0
2020-07-05 23:00 | 4488 |  |  | 0
2020-07-06 | 4489 |  |  | 0
2020-07-06 01:00 | 4490 |  |  | 0
2020-07-06 02:00 | 4491 |  |  | 0
2020-07-06 03:00 | 4492 |  |  | 0
2020-07-06 04:00 | 4493 |  |  | 0
2020-07-06 05:00 | 4494 |  |  | 0
2020-07-06 06:00 | 4495 |  |  | 0.001654
2020-07-06 07:00 | 4496 |  |  | 0.10255
2020-07-06 08:00 | 4497 |  |  | 0.28449
2020-07-06 09:00 | 4498 |  |  | 0.4565
2020-07-06 10:00 | 4499 |  |  | 0.58551
2020-07-06 11:00 | 4500 |  |  | 0.68144
2020-07-06 12:00 | 4501 |  |  | 0.70294
2020-07-06 13:00 | 4502 |  |  | 0.71618
2020-07-06 14:00 | 4503 |  |  | 0.68971
2020-07-06 15:00 | 4504 |  |  | 0.61032
2020-07-06 16:00 | 4505 |  |  | 0.50447
2020-07-06 17:00 | 4506 |  |  | 0.34734
2020-07-06 18:00 | 4507 |  |  | 0.17698
2020-07-06 19:00 | 4508 |  |  | 0.021502
2020-07-06 20:00 | 4509 |  |  | 0
2020-07-06 21:00 | 4510 |  |  | 0
2020-07-06 22:00 | 4511 |  |  | 0
2020-07-06 23:00 | 4512 |  |  | 0
2020-07-07 | 4513 |  |  | 0
2020-07-07 01:00 | 4514 |  |  | 0
2020-07-07 02:00 | 4515 |  |  | 0
2020-07-07 03:00 | 4516 |  |  | 0
2020-07-07 04:00 | 4517 |  |  | 0
2020-07-07 05:00 | 4518 |  |  | 0
2020-07-07 06:00 | 4519 |  |  | 0.001654
2020-07-07 07:00 | 4520 |  |  | 0.10751
2020-07-07 08:00 | 4521 |  |  | 0.30433
2020-07-07 09:00 | 4522 |  |  | 0.45319
2020-07-07 10:00 | 4523 |  |  | 0.63182
2020-07-07 11:00 | 4524 |  |  | 0.67483
2020-07-07 12:00 | 4525 |  |  | 0.63182
2020-07-07 13:00 | 4526 |  |  | 0.21502
2020-07-07 14:00 | 4527 |  |  | 0.33576
2020-07-07 15:00 | 4528 |  |  | 0.27291
2020-07-07 16:00 | 4529 |  |  | 0.1654
2020-07-07 17:00 | 4530 |  |  | 0.13728
2020-07-07 18:00 | 4531 |  |  | 0.069467
2020-07-07 19:00 | 4532 |  |  | 0
2020-07-07 20:00 | 4533 |  |  | 0
2020-07-07 21:00 | 4534 |  |  | 0
2020-07-07 22:00 | 4535 |  |  | 0
2020-07-07 23:00 | 4536 |  |  | 0
2020-07-08 | 4537 |  |  | 0
2020-07-08 01:00 | 4538 |  |  | 0
2020-07-08 02:00 | 4539 |  |  | 0
2020-07-08 03:00 | 4540 |  |  | 0
2020-07-08 04:00 | 4541 |  |  | 0
2020-07-08 05:00 | 4542 |  |  | 0
2020-07-08 06:00 | 4543 |  |  | 0.066159
2020-07-08 07:00 | 4544 |  |  | 0.13397
2020-07-08 08:00 | 4545 |  |  | 0.2911
2020-07-08 09:00 | 4546 |  |  | 0.43334
2020-07-08 10:00 | 4547 |  |  | 0.6004
2020-07-08 11:00 | 4548 |  |  | 0.67648
2020-07-08 12:00 | 4549 |  |  | 0.72775
2020-07-08 13:00 | 4550 |  |  | 0.74595
2020-07-08 14:00 | 4551 |  |  | 0.64836
2020-07-08 15:00 | 4552 |  |  | 0.63844
2020-07-08 16:00 | 4553 |  |  | 0.5177
2020-07-08 17:00 | 4554 |  |  | 0.35065
2020-07-08 18:00 | 4555 |  |  | 0.17698
2020-07-08 19:00 | 4556 |  |  | 0.019848
2020-07-08 20:00 | 4557 |  |  | 0
2020-07-08 21:00 | 4558 |  |  | 0
2020-07-08 22:00 | 4559 |  |  | 0
2020-07-08 23:00 | 4560 |  |  | 0
2020-07-09 | 4561 |  |  | 0
2020-07-09 01:00 | 4562 |  |  | 0
2020-07-09 02:00 | 4563 |  |  | 0
2020-07-09 03:00 | 4564 |  |  | 0
2020-07-09 04:00 | 4565 |  |  | 0
2020-07-09 05:00 | 4566 |  |  | 0
2020-07-09 06:00 | 4567 |  |  | 0.011578
2020-07-09 07:00 | 4568 |  |  | 0.1042
2020-07-09 08:00 | 4569 |  |  | 0.28614
2020-07-09 09:00 | 4570 |  |  | 0.46146
2020-07-09 10:00 | 4571 |  |  | 0.58882
2020-07-09 11:00 | 4572 |  |  | 0.61528
2020-07-09 12:00 | 4573 |  |  | 0.66821
2020-07-09 13:00 | 4574 |  |  | 0.7046
2020-07-09 14:00 | 4575 |  |  | 0.69964
2020-07-09 15:00 | 4576 |  |  | 0.62024
2020-07-09 16:00 | 4577 |  |  | 0.49454
2020-07-09 17:00 | 4578 |  |  | 0.34568
2020-07-09 18:00 | 4579 |  |  | 0.1654
2020-07-09 19:00 | 4580 |  |  | 0.014886
2020-07-09 20:00 | 4581 |  |  | 0
2020-07-09 21:00 | 4582 |  |  | 0
2020-07-09 22:00 | 4583 |  |  | 0
2020-07-09 23:00 | 4584 |  |  | 0
2020-07-10 | 4585 |  |  | 0
2020-07-10 01:00 | 4586 |  |  | 0
2020-07-10 02:00 | 4587 |  |  | 0
2020-07-10 03:00 | 4588 |  |  | 0
2020-07-10 04:00 | 4589 |  |  | 0
2020-07-10 05:00 | 4590 |  |  | 0
2020-07-10 06:00 | 4591 |  |  | 0.036388
2020-07-10 07:00 | 4592 |  |  | 0.13066
2020-07-10 08:00 | 4593 |  |  | 0.27125
2020-07-10 09:00 | 4594 |  |  | 0.41184
2020-07-10 10:00 | 4595 |  |  | 0.42838
2020-07-10 11:00 | 4596 |  |  | 0.58551
2020-07-10 12:00 | 4597 |  |  | 0.68475
2020-07-10 13:00 | 4598 |  |  | 0.71452
2020-07-10 14:00 | 4599 |  |  | 0.26133
2020-07-10 15:00 | 4600 |  |  | 0.35891
2020-07-10 16:00 | 4601 |  |  | 0.34238
2020-07-10 17:00 | 4602 |  |  | 0.17201
2020-07-10 18:00 | 4603 |  |  | 0.003308
2020-07-10 19:00 | 4604 |  |  | 0
2020-07-10 20:00 | 4605 |  |  | 0
2020-07-10 21:00 | 4606 |  |  | 0
2020-07-10 22:00 | 4607 |  |  | 0
2020-07-10 23:00 | 4608 |  |  | 0
2020-07-11 | 4609 |  |  | 0
2020-07-11 01:00 | 4610 |  |  | 0
2020-07-11 02:00 | 4611 |  |  | 0
2020-07-11 03:00 | 4612 |  |  | 0
2020-07-11 04:00 | 4613 |  |  | 0
2020-07-11 05:00 | 4614 |  |  | 0
2020-07-11 06:00 | 4615 |  |  | 0.026464
2020-07-11 07:00 | 4616 |  |  | 0.10089
2020-07-11 08:00 | 4617 |  |  | 0.27787
2020-07-11 09:00 | 4618 |  |  | 0.45154
2020-07-11 10:00 | 4619 |  |  | 0.54912
2020-07-11 11:00 | 4620 |  |  | 0.40026
2020-07-11 12:00 | 4621 |  |  | 0.35561
2020-07-11 13:00 | 4622 |  |  | 0.65829
2020-07-11 14:00 | 4623 |  |  | 0.29441
2020-07-11 15:00 | 4624 |  |  | 0.25141
2020-07-11 16:00 | 4625 |  |  | 0.1472
2020-07-11 17:00 | 4626 |  |  | 0.051274
2020-07-11 18:00 | 4627 |  |  | 0.082699
2020-07-11 19:00 | 4628 |  |  | 0.013232
2020-07-11 20:00 | 4629 |  |  | 0
2020-07-11 21:00 | 4630 |  |  | 0
2020-07-11 22:00 | 4631 |  |  | 0
2020-07-11 23:00 | 4632 |  |  | 0
2020-07-12 | 4633 |  |  | 0
2020-07-12 01:00 | 4634 |  |  | 0
2020-07-12 02:00 | 4635 |  |  | 0
2020-07-12 03:00 | 4636 |  |  | 0
2020-07-12 04:00 | 4637 |  |  | 0
2020-07-12 05:00 | 4638 |  |  | 0
2020-07-12 06:00 | 4639 |  |  | 0.0082699
2020-07-12 07:00 | 4640 |  |  | 0.12736
2020-07-12 08:00 | 4641 |  |  | 0.26133
2020-07-12 09:00 | 4642 |  |  | 0.42673
2020-07-12 10:00 | 4643 |  |  | 0.56236
2020-07-12 11:00 | 4644 |  |  | 0.52762
2020-07-12 12:00 | 4645 |  |  | 0.1869
2020-07-12 13:00 | 4646 |  |  | 0.33245
2020-07-12 14:00 | 4647 |  |  | 0.22825
2020-07-12 15:00 | 4648 |  |  | 0.11909
2020-07-12 16:00 | 4649 |  |  | 0.14059
2020-07-12 17:00 | 4650 |  |  | 0.13066
2020-07-12 18:00 | 4651 |  |  | 0.061197
2020-07-12 19:00 | 4652 |  |  | 0.0066159
2020-07-12 20:00 | 4653 |  |  | 0
2020-07-12 21:00 | 4654 |  |  | 0
2020-07-12 22:00 | 4655 |  |  | 0
2020-07-12 23:00 | 4656 |  |  | 0
2020-07-13 | 4657 |  |  | 0
2020-07-13 01:00 | 4658 |  |  | 0
2020-07-13 02:00 | 4659 |  |  | 0
2020-07-13 03:00 | 4660 |  |  | 0
2020-07-13 04:00 | 4661 |  |  | 0
2020-07-13 05:00 | 4662 |  |  | 0
2020-07-13 06:00 | 4663 |  |  | 0.046312
2020-07-13 07:00 | 4664 |  |  | 0.097585
2020-07-13 08:00 | 4665 |  |  | 0.15713
2020-07-13 09:00 | 4666 |  |  | 0.2696
2020-07-13 10:00 | 4667 |  |  | 0.45981
2020-07-13 11:00 | 4668 |  |  | 0.40853
2020-07-13 12:00 | 4669 |  |  | 0.47966
2020-07-13 13:00 | 4670 |  |  | 0.54416
2020-07-13 14:00 | 4671 |  |  | 0.53755
2020-07-13 15:00 | 4672 |  |  | 0.21502
2020-07-13 16:00 | 4673 |  |  | 0.20179
2020-07-13 17:00 | 4674 |  |  | 0.14886
2020-07-13 18:00 | 4675 |  |  | 0.1472
2020-07-13 19:00 | 4676 |  |  | 0.019848
2020-07-13 20:00 | 4677 |  |  | 0
2020-07-13 21:00 | 4678 |  |  | 0
2020-07-13 22:00 | 4679 |  |  | 0
2020-07-13 23:00 | 4680 |  |  | 0
2020-07-14 | 4681 |  |  | 0
2020-07-14 01:00 | 4682 |  |  | 0
2020-07-14 02:00 | 4683 |  |  | 0
2020-07-14 03:00 | 4684 |  |  | 0
2020-07-14 04:00 | 4685 |  |  | 0
2020-07-14 05:00 | 4686 |  |  | 0
2020-07-14 06:00 | 4687 |  |  | 0.019848
2020-07-14 07:00 | 4688 |  |  | 0.052928
2020-07-14 08:00 | 4689 |  |  | 0.15547
2020-07-14 09:00 | 4690 |  |  | 0.42838
2020-07-14 10:00 | 4691 |  |  | 0.61363
2020-07-14 11:00 | 4692 |  |  | 0.63017
2020-07-14 12:00 | 4693 |  |  | 0.52928
2020-07-14 13:00 | 4694 |  |  | 0.49123
2020-07-14 14:00 | 4695 |  |  | 0.26298
2020-07-14 15:00 | 4696 |  |  | 0.1869
2020-07-14 16:00 | 4697 |  |  | 0.074429
2020-07-14 17:00 | 4698 |  |  | 0.17532
2020-07-14 18:00 | 4699 |  |  | 0.059543
2020-07-14 19:00 | 4700 |  |  | 0.0082699
2020-07-14 20:00 | 4701 |  |  | 0
2020-07-14 21:00 | 4702 |  |  | 0
2020-07-14 22:00 | 4703 |  |  | 0
2020-07-14 23:00 | 4704 |  |  | 0
2020-07-15 | 4705 |  |  | 0
2020-07-15 01:00 | 4706 |  |  | 0
2020-07-15 02:00 | 4707 |  |  | 0
2020-07-15 03:00 | 4708 |  |  | 0
2020-07-15 04:00 | 4709 |  |  | 0
2020-07-15 05:00 | 4710 |  |  | 0.011578
2020-07-15 06:00 | 4711 |  |  | 0.044658
2020-07-15 07:00 | 4712 |  |  | 0.14886
2020-07-15 08:00 | 4713 |  |  | 0.21006
2020-07-15 09:00 | 4714 |  |  | 0.40688
2020-07-15 10:00 | 4715 |  |  | 0.44823
2020-07-15 11:00 | 4716 |  |  | 0.38703
2020-07-15 12:00 | 4717 |  |  | 0.34568
2020-07-15 13:00 | 4718 |  |  | 0.25637
2020-07-15 14:00 | 4719 |  |  | 0.2299
2020-07-15 15:00 | 4720 |  |  | 0.51108
2020-07-15 16:00 | 4721 |  |  | 0.13893
2020-07-15 17:00 | 4722 |  |  | 0.13728
2020-07-15 18:00 | 4723 |  |  | 0.11909
2020-07-15 19:00 | 4724 |  |  | 0.0066159
2020-07-15 20:00 | 4725 |  |  | 0
2020-07-15 21:00 | 4726 |  |  | 0
2020-07-15 22:00 | 4727 |  |  | 0
2020-07-15 23:00 | 4728 |  |  | 0
2020-07-16 | 4729 |  |  | 0
2020-07-16 01:00 | 4730 |  |  | 0
2020-07-16 02:00 | 4731 |  |  | 0
2020-07-16 03:00 | 4732 |  |  | 0
2020-07-16 04:00 | 4733 |  |  | 0
2020-07-16 05:00 | 4734 |  |  | 0
2020-07-16 06:00 | 4735 |  |  | 0.028118
2020-07-16 07:00 | 4736 |  |  | 0.10751
2020-07-16 08:00 | 4737 |  |  | 0.26629
2020-07-16 09:00 | 4738 |  |  | 0.44161
2020-07-16 10:00 | 4739 |  |  | 0.60701
2020-07-16 11:00 | 4740 |  |  | 0.57063
2020-07-16 12:00 | 4741 |  |  | 0.6831
2020-07-16 13:00 | 4742 |  |  | 0.61032
2020-07-16 14:00 | 4743 |  |  | 0.58717
2020-07-16 15:00 | 4744 |  |  | 0.44161
2020-07-16 16:00 | 4745 |  |  | 0.49454
2020-07-16 17:00 | 4746 |  |  | 0.34734
2020-07-16 18:00 | 4747 |  |  | 0.16044
2020-07-16 19:00 | 4748 |  |  | 0.014886
2020-07-16 20:00 | 4749 |  |  | 0
2020-07-16 21:00 | 4750 |  |  | 0
2020-07-16 22:00 | 4751 |  |  | 0
2020-07-16 23:00 | 4752 |  |  | 0
2020-07-17 | 4753 |  |  | 0
2020-07-17 01:00 | 4754 |  |  | 0
2020-07-17 02:00 | 4755 |  |  | 0
2020-07-17 03:00 | 4756 |  |  | 0
2020-07-17 04:00 | 4757 |  |  | 0
2020-07-17 05:00 | 4758 |  |  | 0
2020-07-17 06:00 | 4759 |  |  | 0.0099239
2020-07-17 07:00 | 4760 |  |  | 0.10089
2020-07-17 08:00 | 4761 |  |  | 0.27291
2020-07-17 09:00 | 4762 |  |  | 0.44988
2020-07-17 10:00 | 4763 |  |  | 0.57559
2020-07-17 11:00 | 4764 |  |  | 0.69467
2020-07-17 12:00 | 4765 |  |  | 0.64505
2020-07-17 13:00 | 4766 |  |  | 0.25968
2020-07-17 14:00 | 4767 |  |  | 0.2299
2020-07-17 15:00 | 4768 |  |  | 0.38042
2020-07-17 16:00 | 4769 |  |  | 0.18194
2020-07-17 17:00 | 4770 |  |  | 0.036388
2020-07-17 18:00 | 4771 |  |  | 0.031426
2020-07-17 19:00 | 4772 |  |  | 0
2020-07-17 20:00 | 4773 |  |  | 0
2020-07-17 21:00 | 4774 |  |  | 0
2020-07-17 22:00 | 4775 |  |  | 0
2020-07-17 23:00 | 4776 |  |  | 0
2020-07-18 | 4777 |  |  | 0
2020-07-18 01:00 | 4778 |  |  | 0
2020-07-18 02:00 | 4779 |  |  | 0
2020-07-18 03:00 | 4780 |  |  | 0
2020-07-18 04:00 | 4781 |  |  | 0
2020-07-18 05:00 | 4782 |  |  | 0.0066159
2020-07-18 06:00 | 4783 |  |  | 0.038042
2020-07-18 07:00 | 4784 |  |  | 0.062851
2020-07-18 08:00 | 4785 |  |  | 0.14224
2020-07-18 09:00 | 4786 |  |  | 0.23817
2020-07-18 10:00 | 4787 |  |  | 0.39861
2020-07-18 11:00 | 4788 |  |  | 0.65994
2020-07-18 12:00 | 4789 |  |  | 0.48462
2020-07-18 13:00 | 4790 |  |  | 0.46477
2020-07-18 14:00 | 4791 |  |  | 0.38703
2020-07-18 15:00 | 4792 |  |  | 0.36553
2020-07-18 16:00 | 4793 |  |  | 0.44658
2020-07-18 17:00 | 4794 |  |  | 0.36057
2020-07-18 18:00 | 4795 |  |  | 0.15382
2020-07-18 19:00 | 4796 |  |  | 0.018194
2020-07-18 20:00 | 4797 |  |  | 0
2020-07-18 21:00 | 4798 |  |  | 0
2020-07-18 22:00 | 4799 |  |  | 0
2020-07-18 23:00 | 4800 |  |  | 0
2020-07-19 | 4801 |  |  | 0
2020-07-19 01:00 | 4802 |  |  | 0
2020-07-19 02:00 | 4803 |  |  | 0
2020-07-19 03:00 | 4804 |  |  | 0
2020-07-19 04:00 | 4805 |  |  | 0
2020-07-19 05:00 | 4806 |  |  | 0
2020-07-19 06:00 | 4807 |  |  | 0.026464
2020-07-19 07:00 | 4808 |  |  | 0.1042
2020-07-19 08:00 | 4809 |  |  | 0.27952
2020-07-19 09:00 | 4810 |  |  | 0.45319
2020-07-19 10:00 | 4811 |  |  | 0.60867
2020-07-19 11:00 | 4812 |  |  | 0.63182
2020-07-19 12:00 | 4813 |  |  | 0.71783
2020-07-19 13:00 | 4814 |  |  | 0.69633
2020-07-19 14:00 | 4815 |  |  | 0.6649
2020-07-19 15:00 | 4816 |  |  | 0.64009
2020-07-19 16:00 | 4817 |  |  | 0.52762
2020-07-19 17:00 | 4818 |  |  | 0.35891
2020-07-19 18:00 | 4819 |  |  | 0.16871
2020-07-19 19:00 | 4820 |  |  | 0.013232
2020-07-19 20:00 | 4821 |  |  | 0
2020-07-19 21:00 | 4822 |  |  | 0
2020-07-19 22:00 | 4823 |  |  | 0
2020-07-19 23:00 | 4824 |  |  | 0
2020-07-20 | 4825 |  |  | 0
2020-07-20 01:00 | 4826 |  |  | 0
2020-07-20 02:00 | 4827 |  |  | 0
2020-07-20 03:00 | 4828 |  |  | 0
2020-07-20 04:00 | 4829 |  |  | 0
2020-07-20 05:00 | 4830 |  |  | 0
2020-07-20 06:00 | 4831 |  |  | 0.031426
2020-07-20 07:00 | 4832 |  |  | 0.082699
2020-07-20 08:00 | 4833 |  |  | 0.27456
2020-07-20 09:00 | 4834 |  |  | 0.39034
2020-07-20 10:00 | 4835 |  |  | 0.53258
2020-07-20 11:00 | 4836 |  |  | 0.53258
2020-07-20 12:00 | 4837 |  |  | 0.55078
2020-07-20 13:00 | 4838 |  |  | 0.61032
2020-07-20 14:00 | 4839 |  |  | 0.17698
2020-07-20 15:00 | 4840 |  |  | 0.42507
2020-07-20 16:00 | 4841 |  |  | 0.24975
2020-07-20 17:00 | 4842 |  |  | 0.1869
2020-07-20 18:00 | 4843 |  |  | 0.16871
2020-07-20 19:00 | 4844 |  |  | 0.018194
2020-07-20 20:00 | 4845 |  |  | 0
2020-07-20 21:00 | 4846 |  |  | 0
2020-07-20 22:00 | 4847 |  |  | 0
2020-07-20 23:00 | 4848 |  |  | 0
2020-07-21 | 4849 |  |  | 0
2020-07-21 01:00 | 4850 |  |  | 0
2020-07-21 02:00 | 4851 |  |  | 0
2020-07-21 03:00 | 4852 |  |  | 0
2020-07-21 04:00 | 4853 |  |  | 0
2020-07-21 05:00 | 4854 |  |  | 0
2020-07-21 06:00 | 4855 |  |  | 0.051274
2020-07-21 07:00 | 4856 |  |  | 0.11082
2020-07-21 08:00 | 4857 |  |  | 0.22825
2020-07-21 09:00 | 4858 |  |  | 0.43004
2020-07-21 10:00 | 4859 |  |  | 0.52762
2020-07-21 11:00 | 4860 |  |  | 0.57063
2020-07-21 12:00 | 4861 |  |  | 0.26464
2020-07-21 13:00 | 4862 |  |  | 0.27291
2020-07-21 14:00 | 4863 |  |  | 0.3126
2020-07-21 15:00 | 4864 |  |  | 0.16044
2020-07-21 16:00 | 4865 |  |  | 0.29441
2020-07-21 17:00 | 4866 |  |  | 0.21171
2020-07-21 18:00 | 4867 |  |  | 0.064505
2020-07-21 19:00 | 4868 |  |  | 0.021502
2020-07-21 20:00 | 4869 |  |  | 0
2020-07-21 21:00 | 4870 |  |  | 0
2020-07-21 22:00 | 4871 |  |  | 0
2020-07-21 23:00 | 4872 |  |  | 0
2020-07-22 | 4873 |  |  | 0
2020-07-22 01:00 | 4874 |  |  | 0
2020-07-22 02:00 | 4875 |  |  | 0
2020-07-22 03:00 | 4876 |  |  | 0
2020-07-22 04:00 | 4877 |  |  | 0
2020-07-22 05:00 | 4878 |  |  | 0
2020-07-22 06:00 | 4879 |  |  | 0.01654
2020-07-22 07:00 | 4880 |  |  | 0.099239
2020-07-22 08:00 | 4881 |  |  | 0.26133
2020-07-22 09:00 | 4882 |  |  | 0.43996
2020-07-22 10:00 | 4883 |  |  | 0.50777
2020-07-22 11:00 | 4884 |  |  | 0.67317
2020-07-22 12:00 | 4885 |  |  | 0.60536
2020-07-22 13:00 | 4886 |  |  | 0.47635
2020-07-22 14:00 | 4887 |  |  | 0.55905
2020-07-22 15:00 | 4888 |  |  | 0.082699
2020-07-22 16:00 | 4889 |  |  | 0.25141
2020-07-22 17:00 | 4890 |  |  | 0.076083
2020-07-22 18:00 | 4891 |  |  | 0.001654
2020-07-22 19:00 | 4892 |  |  | 0
2020-07-22 20:00 | 4893 |  |  | 0
2020-07-22 21:00 | 4894 |  |  | 0
2020-07-22 22:00 | 4895 |  |  | 0
2020-07-22 23:00 | 4896 |  |  | 0
2020-07-23 | 4897 |  |  | 0
2020-07-23 01:00 | 4898 |  |  | 0
2020-07-23 02:00 | 4899 |  |  | 0
2020-07-23 03:00 | 4900 |  |  | 0
2020-07-23 04:00 | 4901 |  |  | 0
2020-07-23 05:00 | 4902 |  |  | 0
2020-07-23 06:00 | 4903 |  |  | 0.004962
2020-07-23 07:00 | 4904 |  |  | 0.092623
2020-07-23 08:00 | 4905 |  |  | 0.2696
2020-07-23 09:00 | 4906 |  |  | 0.44658
2020-07-23 10:00 | 4907 |  |  | 0.5822
2020-07-23 11:00 | 4908 |  |  | 0.69798
2020-07-23 12:00 | 4909 |  |  | 0.70294
2020-07-23 13:00 | 4910 |  |  | 0.70129
2020-07-23 14:00 | 4911 |  |  | 0.63017
2020-07-23 15:00 | 4912 |  |  | 0.61859
2020-07-23 16:00 | 4913 |  |  | 0.50777
2020-07-23 17:00 | 4914 |  |  | 0.30599
2020-07-23 18:00 | 4915 |  |  | 0.16705
2020-07-23 19:00 | 4916 |  |  | 0.031426
2020-07-23 20:00 | 4917 |  |  | 0
2020-07-23 21:00 | 4918 |  |  | 0
2020-07-23 22:00 | 4919 |  |  | 0
2020-07-23 23:00 | 4920 |  |  | 0
2020-07-24 | 4921 |  |  | 0
2020-07-24 01:00 | 4922 |  |  | 0
2020-07-24 02:00 | 4923 |  |  | 0
2020-07-24 03:00 | 4924 |  |  | 0
2020-07-24 04:00 | 4925 |  |  | 0
2020-07-24 05:00 | 4926 |  |  | 0.003308
2020-07-24 06:00 | 4927 |  |  | 0.067813
2020-07-24 07:00 | 4928 |  |  | 0.11743
2020-07-24 08:00 | 4929 |  |  | 0.29606
2020-07-24 09:00 | 4930 |  |  | 0.11578
2020-07-24 10:00 | 4931 |  |  | 0.33245
2020-07-24 11:00 | 4932 |  |  | 0.50943
2020-07-24 12:00 | 4933 |  |  | 0.46808
2020-07-24 13:00 | 4934 |  |  | 0.42673
2020-07-24 14:00 | 4935 |  |  | 0.54416
2020-07-24 15:00 | 4936 |  |  | 0.61032
2020-07-24 16:00 | 4937 |  |  | 0.54747
2020-07-24 17:00 | 4938 |  |  | 0.38042
2020-07-24 18:00 | 4939 |  |  | 0.17698
2020-07-24 19:00 | 4940 |  |  | 0.014886
2020-07-24 20:00 | 4941 |  |  | 0
2020-07-24 21:00 | 4942 |  |  | 0
2020-07-24 22:00 | 4943 |  |  | 0
2020-07-24 23:00 | 4944 |  |  | 0
2020-07-25 | 4945 |  |  | 0
2020-07-25 01:00 | 4946 |  |  | 0
2020-07-25 02:00 | 4947 |  |  | 0
2020-07-25 03:00 | 4948 |  |  | 0
2020-07-25 04:00 | 4949 |  |  | 0
2020-07-25 05:00 | 4950 |  |  | 0
2020-07-25 06:00 | 4951 |  |  | 0
2020-07-25 07:00 | 4952 |  |  | 0.086007
2020-07-25 08:00 | 4953 |  |  | 0.27291
2020-07-25 09:00 | 4954 |  |  | 0.45981
2020-07-25 10:00 | 4955 |  |  | 0.58882
2020-07-25 11:00 | 4956 |  |  | 0.69302
2020-07-25 12:00 | 4957 |  |  | 0.72941
2020-07-25 13:00 | 4958 |  |  | 0.75091
2020-07-25 14:00 | 4959 |  |  | 0.69798
2020-07-25 15:00 | 4960 |  |  | 0.63182
2020-07-25 16:00 | 4961 |  |  | 0.50116
2020-07-25 17:00 | 4962 |  |  | 0.25306
2020-07-25 18:00 | 4963 |  |  | 0.1439
2020-07-25 19:00 | 4964 |  |  | 0.023156
2020-07-25 20:00 | 4965 |  |  | 0
2020-07-25 21:00 | 4966 |  |  | 0
2020-07-25 22:00 | 4967 |  |  | 0
2020-07-25 23:00 | 4968 |  |  | 0
2020-07-26 | 4969 |  |  | 0
2020-07-26 01:00 | 4970 |  |  | 0
2020-07-26 02:00 | 4971 |  |  | 0
2020-07-26 03:00 | 4972 |  |  | 0
2020-07-26 04:00 | 4973 |  |  | 0
2020-07-26 05:00 | 4974 |  |  | 0
2020-07-26 06:00 | 4975 |  |  | 0.054582
2020-07-26 07:00 | 4976 |  |  | 0.089315
2020-07-26 08:00 | 4977 |  |  | 0.26464
2020-07-26 09:00 | 4978 |  |  | 0.4168
2020-07-26 10:00 | 4979 |  |  | 0.51439
2020-07-26 11:00 | 4980 |  |  | 0.68806
2020-07-26 12:00 | 4981 |  |  | 0.72941
2020-07-26 13:00 | 4982 |  |  | 0.73768
2020-07-26 14:00 | 4983 |  |  | 0.65167
2020-07-26 15:00 | 4984 |  |  | 0.61859
2020-07-26 16:00 | 4985 |  |  | 0.29937
2020-07-26 17:00 | 4986 |  |  | 0.19021
2020-07-26 18:00 | 4987 |  |  | 0.11413
2020-07-26 19:00 | 4988 |  |  | 0.013232
2020-07-26 20:00 | 4989 |  |  | 0
2020-07-26 21:00 | 4990 |  |  | 0
2020-07-26 22:00 | 4991 |  |  | 0
2020-07-26 23:00 | 4992 |  |  | 0
2020-07-27 | 4993 |  |  | 0
2020-07-27 01:00 | 4994 |  |  | 0
2020-07-27 02:00 | 4995 |  |  | 0
2020-07-27 03:00 | 4996 |  |  | 0
2020-07-27 04:00 | 4997 |  |  | 0
2020-07-27 05:00 | 4998 |  |  | 0
2020-07-27 06:00 | 4999 |  |  | 0.019848
2020-07-27 07:00 | 5000 |  |  | 0.1042
2020-07-27 08:00 | 5001 |  |  | 0.30599
2020-07-27 09:00 | 5002 |  |  | 0.43831
2020-07-27 10:00 | 5003 |  |  | 0.57724
2020-07-27 11:00 | 5004 |  |  | 0.36884
2020-07-27 12:00 | 5005 |  |  | 0.34899
2020-07-27 13:00 | 5006 |  |  | 0.41019
2020-07-27 14:00 | 5007 |  |  | 0.24314
2020-07-27 15:00 | 5008 |  |  | 0.18525
2020-07-27 16:00 | 5009 |  |  | 0.21998
2020-07-27 17:00 | 5010 |  |  | 0.12736
2020-07-27 18:00 | 5011 |  |  | 0.018194
2020-07-27 19:00 | 5012 |  |  | 0
2020-07-27 20:00 | 5013 |  |  | 0
2020-07-27 21:00 | 5014 |  |  | 0
2020-07-27 22:00 | 5015 |  |  | 0
2020-07-27 23:00 | 5016 |  |  | 0
2020-07-28 | 5017 |  |  | 0
2020-07-28 01:00 | 5018 |  |  | 0
2020-07-28 02:00 | 5019 |  |  | 0
2020-07-28 03:00 | 5020 |  |  | 0
2020-07-28 04:00 | 5021 |  |  | 0
2020-07-28 05:00 | 5022 |  |  | 0.004962
2020-07-28 06:00 | 5023 |  |  | 0.043004
2020-07-28 07:00 | 5024 |  |  | 0.13563
2020-07-28 08:00 | 5025 |  |  | 0.29441
2020-07-28 09:00 | 5026 |  |  | 0.30268
2020-07-28 10:00 | 5027 |  |  | 0.48958
2020-07-28 11:00 | 5028 |  |  | 0.5789
2020-07-28 12:00 | 5029 |  |  | 0.4565
2020-07-28 13:00 | 5030 |  |  | 0.67648
2020-07-28 14:00 | 5031 |  |  | 0.48958
2020-07-28 15:00 | 5032 |  |  | 0.32584
2020-07-28 16:00 | 5033 |  |  | 0.25306
2020-07-28 17:00 | 5034 |  |  | 0.17698
2020-07-28 18:00 | 5035 |  |  | 0.0082699
2020-07-28 19:00 | 5036 |  |  | 0
2020-07-28 20:00 | 5037 |  |  | 0
2020-07-28 21:00 | 5038 |  |  | 0
2020-07-28 22:00 | 5039 |  |  | 0
2020-07-28 23:00 | 5040 |  |  | 0
2020-07-29 | 5041 |  |  | 0
2020-07-29 01:00 | 5042 |  |  | 0
2020-07-29 02:00 | 5043 |  |  | 0
2020-07-29 03:00 | 5044 |  |  | 0
2020-07-29 04:00 | 5045 |  |  | 0
2020-07-29 05:00 | 5046 |  |  | 0
2020-07-29 06:00 | 5047 |  |  | 0.054582
2020-07-29 07:00 | 5048 |  |  | 0.12239
2020-07-29 08:00 | 5049 |  |  | 0.2481
2020-07-29 09:00 | 5050 |  |  | 0.41184
2020-07-29 10:00 | 5051 |  |  | 0.56401
2020-07-29 11:00 | 5052 |  |  | 0.58551
2020-07-29 12:00 | 5053 |  |  | 0.21006
2020-07-29 13:00 | 5054 |  |  | 0.21502
2020-07-29 14:00 | 5055 |  |  | 0.25471
2020-07-29 15:00 | 5056 |  |  | 0.21833
2020-07-29 16:00 | 5057 |  |  | 0.1869
2020-07-29 17:00 | 5058 |  |  | 0.19352
2020-07-29 18:00 | 5059 |  |  | 0.043004
2020-07-29 19:00 | 5060 |  |  | 0.018194
2020-07-29 20:00 | 5061 |  |  | 0
2020-07-29 21:00 | 5062 |  |  | 0
2020-07-29 22:00 | 5063 |  |  | 0
2020-07-29 23:00 | 5064 |  |  | 0
2020-07-30 | 5065 |  |  | 0
2020-07-30 01:00 | 5066 |  |  | 0
2020-07-30 02:00 | 5067 |  |  | 0
2020-07-30 03:00 | 5068 |  |  | 0
2020-07-30 04:00 | 5069 |  |  | 0
2020-07-30 05:00 | 5070 |  |  | 0
2020-07-30 06:00 | 5071 |  |  | 0.028118
2020-07-30 07:00 | 5072 |  |  | 0.12239
2020-07-30 08:00 | 5073 |  |  | 0.23817
2020-07-30 09:00 | 5074 |  |  | 0.37545
2020-07-30 10:00 | 5075 |  |  | 0.53258
2020-07-30 11:00 | 5076 |  |  | 0.6004
2020-07-30 12:00 | 5077 |  |  | 0.45485
2020-07-30 13:00 | 5078 |  |  | 0.63844
2020-07-30 14:00 | 5079 |  |  | 0.66159
2020-07-30 15:00 | 5080 |  |  | 0.24975
2020-07-30 16:00 | 5081 |  |  | 0.1472
2020-07-30 17:00 | 5082 |  |  | 0.094277
2020-07-30 18:00 | 5083 |  |  | 0.01654
2020-07-30 19:00 | 5084 |  |  | 0
2020-07-30 20:00 | 5085 |  |  | 0
2020-07-30 21:00 | 5086 |  |  | 0
2020-07-30 22:00 | 5087 |  |  | 0
2020-07-30 23:00 | 5088 |  |  | 0
2020-07-31 | 5089 |  |  | 0
2020-07-31 01:00 | 5090 |  |  | 0
2020-07-31 02:00 | 5091 |  |  | 0
2020-07-31 03:00 | 5092 |  |  | 0
2020-07-31 04:00 | 5093 |  |  | 0
2020-07-31 05:00 | 5094 |  |  | 0
2020-07-31 06:00 | 5095 |  |  | 0.023156
2020-07-31 07:00 | 5096 |  |  | 0.094277
2020-07-31 08:00 | 5097 |  |  | 0.25141
2020-07-31 09:00 | 5098 |  |  | 0.4135
2020-07-31 10:00 | 5099 |  |  | 0.54251
2020-07-31 11:00 | 5100 |  |  | 0.65002
2020-07-31 12:00 | 5101 |  |  | 0.71121
2020-07-31 13:00 | 5102 |  |  | 0.70294
2020-07-31 14:00 | 5103 |  |  | 0.67152
2020-07-31 15:00 | 5104 |  |  | 0.58386
2020-07-31 16:00 | 5105 |  |  | 0.46312
2020-07-31 17:00 | 5106 |  |  | 0.30599
2020-07-31 18:00 | 5107 |  |  | 0.13232
2020-07-31 19:00 | 5108 |  |  | 0.004962
2020-07-31 20:00 | 5109 |  |  | 0
2020-07-31 21:00 | 5110 |  |  | 0
2020-07-31 22:00 | 5111 |  |  | 0
2020-07-31 23:00 | 5112 |  |  | 0
2020-08-01 | 5113 |  |  | 0
2020-08-01 01:00 | 5114 |  |  | 0
2020-08-01 02:00 | 5115 |  |  | 0
2020-08-01 03:00 | 5116 |  |  | 0
2020-08-01 04:00 | 5117 |  |  | 0
2020-08-01 05:00 | 5118 |  |  | 0
2020-08-01 06:00 | 5119 |  |  | 0.018194
2020-08-01 07:00 | 5120 |  |  | 0.094277
2020-08-01 08:00 | 5121 |  |  | 0.24644
2020-08-01 09:00 | 5122 |  |  | 0.40357
2020-08-01 10:00 | 5123 |  |  | 0.54912
2020-08-01 11:00 | 5124 |  |  | 0.63348
2020-08-01 12:00 | 5125 |  |  | 0.70129
2020-08-01 13:00 | 5126 |  |  | 0.71121
2020-08-01 14:00 | 5127 |  |  | 0.65332
2020-08-01 15:00 | 5128 |  |  | 0.32584
2020-08-01 16:00 | 5129 |  |  | 0.11743
2020-08-01 17:00 | 5130 |  |  | 0.031426
2020-08-01 18:00 | 5131 |  |  | 0.072775
2020-08-01 19:00 | 5132 |  |  | 0
2020-08-01 20:00 | 5133 |  |  | 0
2020-08-01 21:00 | 5134 |  |  | 0
2020-08-01 22:00 | 5135 |  |  | 0
2020-08-01 23:00 | 5136 |  |  | 0
2020-08-02 | 5137 |  |  | 0
2020-08-02 01:00 | 5138 |  |  | 0
2020-08-02 02:00 | 5139 |  |  | 0
2020-08-02 03:00 | 5140 |  |  | 0
2020-08-02 04:00 | 5141 |  |  | 0
2020-08-02 05:00 | 5142 |  |  | 0
2020-08-02 06:00 | 5143 |  |  | 0
2020-08-02 07:00 | 5144 |  |  | 0.087661
2020-08-02 08:00 | 5145 |  |  | 0.25141
2020-08-02 09:00 | 5146 |  |  | 0.44327
2020-08-02 10:00 | 5147 |  |  | 0.57559
2020-08-02 11:00 | 5148 |  |  | 0.65663
2020-08-02 12:00 | 5149 |  |  | 0.65663
2020-08-02 13:00 | 5150 |  |  | 0.71121
2020-08-02 14:00 | 5151 |  |  | 0.48793
2020-08-02 15:00 | 5152 |  |  | 0.21006
2020-08-02 16:00 | 5153 |  |  | 0.23321
2020-08-02 17:00 | 5154 |  |  | 0.18359
2020-08-02 18:00 | 5155 |  |  | 0.052928
2020-08-02 19:00 | 5156 |  |  | 0.001654
2020-08-02 20:00 | 5157 |  |  | 0
2020-08-02 21:00 | 5158 |  |  | 0
2020-08-02 22:00 | 5159 |  |  | 0
2020-08-02 23:00 | 5160 |  |  | 0
2020-08-03 | 5161 |  |  | 0
2020-08-03 01:00 | 5162 |  |  | 0
2020-08-03 02:00 | 5163 |  |  | 0
2020-08-03 03:00 | 5164 |  |  | 0
2020-08-03 04:00 | 5165 |  |  | 0
2020-08-03 05:00 | 5166 |  |  | 0
2020-08-03 06:00 | 5167 |  |  | 0.003308
2020-08-03 07:00 | 5168 |  |  | 0.028118
2020-08-03 08:00 | 5169 |  |  | 0.074429
2020-08-03 09:00 | 5170 |  |  | 0.11413
2020-08-03 10:00 | 5171 |  |  | 0.089315
2020-08-03 11:00 | 5172 |  |  | 0.17367
2020-08-03 12:00 | 5173 |  |  | 0.11578
2020-08-03 13:00 | 5174 |  |  | 0.076083
2020-08-03 14:00 | 5175 |  |  | 0.067813
2020-08-03 15:00 | 5176 |  |  | 0.099239
2020-08-03 16:00 | 5177 |  |  | 0.03308
2020-08-03 17:00 | 5178 |  |  | 0.39861
2020-08-03 18:00 | 5179 |  |  | 0.19517
2020-08-03 19:00 | 5180 |  |  | 0.014886
2020-08-03 20:00 | 5181 |  |  | 0
2020-08-03 21:00 | 5182 |  |  | 0
2020-08-03 22:00 | 5183 |  |  | 0
2020-08-03 23:00 | 5184 |  |  | 0
2020-08-04 | 5185 |  |  | 0
2020-08-04 01:00 | 5186 |  |  | 0
2020-08-04 02:00 | 5187 |  |  | 0
2020-08-04 03:00 | 5188 |  |  | 0
2020-08-04 04:00 | 5189 |  |  | 0
2020-08-04 05:00 | 5190 |  |  | 0
2020-08-04 06:00 | 5191 |  |  | 0.023156
2020-08-04 07:00 | 5192 |  |  | 0.082699
2020-08-04 08:00 | 5193 |  |  | 0.27952
2020-08-04 09:00 | 5194 |  |  | 0.45319
2020-08-04 10:00 | 5195 |  |  | 0.57063
2020-08-04 11:00 | 5196 |  |  | 0.49289
2020-08-04 12:00 | 5197 |  |  | 0.75091
2020-08-04 13:00 | 5198 |  |  | 0.74595
2020-08-04 14:00 | 5199 |  |  | 0.72279
2020-08-04 15:00 | 5200 |  |  | 0.65829
2020-08-04 16:00 | 5201 |  |  | 0.53755
2020-08-04 17:00 | 5202 |  |  | 0.35891
2020-08-04 18:00 | 5203 |  |  | 0.1654
2020-08-04 19:00 | 5204 |  |  | 0.0066159
2020-08-04 20:00 | 5205 |  |  | 0
2020-08-04 21:00 | 5206 |  |  | 0
2020-08-04 22:00 | 5207 |  |  | 0
2020-08-04 23:00 | 5208 |  |  | 0
2020-08-05 | 5209 |  |  | 0
2020-08-05 01:00 | 5210 |  |  | 0
2020-08-05 02:00 | 5211 |  |  | 0
2020-08-05 03:00 | 5212 |  |  | 0
2020-08-05 04:00 | 5213 |  |  | 0
2020-08-05 05:00 | 5214 |  |  | 0
2020-08-05 06:00 | 5215 |  |  | 0
2020-08-05 07:00 | 5216 |  |  | 0.071121
2020-08-05 08:00 | 5217 |  |  | 0.2696
2020-08-05 09:00 | 5218 |  |  | 0.46146
2020-08-05 10:00 | 5219 |  |  | 0.59709
2020-08-05 11:00 | 5220 |  |  | 0.7046
2020-08-05 12:00 | 5221 |  |  | 0.72279
2020-08-05 13:00 | 5222 |  |  | 0.75091
2020-08-05 14:00 | 5223 |  |  | 0.71121
2020-08-05 15:00 | 5224 |  |  | 0.6434
2020-08-05 16:00 | 5225 |  |  | 0.51604
2020-08-05 17:00 | 5226 |  |  | 0.3523
2020-08-05 18:00 | 5227 |  |  | 0.1472
2020-08-05 19:00 | 5228 |  |  | 0.004962
2020-08-05 20:00 | 5229 |  |  | 0
2020-08-05 21:00 | 5230 |  |  | 0
2020-08-05 22:00 | 5231 |  |  | 0
2020-08-05 23:00 | 5232 |  |  | 0
2020-08-06 | 5233 |  |  | 0
2020-08-06 01:00 | 5234 |  |  | 0
2020-08-06 02:00 | 5235 |  |  | 0
2020-08-06 03:00 | 5236 |  |  | 0
2020-08-06 04:00 | 5237 |  |  | 0
2020-08-06 05:00 | 5238 |  |  | 0
2020-08-06 06:00 | 5239 |  |  | 0
2020-08-06 07:00 | 5240 |  |  | 0.074429
2020-08-06 08:00 | 5241 |  |  | 0.25802
2020-08-06 09:00 | 5242 |  |  | 0.45154
2020-08-06 10:00 | 5243 |  |  | 0.58551
2020-08-06 11:00 | 5244 |  |  | 0.69964
2020-08-06 12:00 | 5245 |  |  | 0.70791
2020-08-06 13:00 | 5246 |  |  | 0.72941
2020-08-06 14:00 | 5247 |  |  | 0.71121
2020-08-06 15:00 | 5248 |  |  | 0.6219
2020-08-06 16:00 | 5249 |  |  | 0.51604
2020-08-06 17:00 | 5250 |  |  | 0.34238
2020-08-06 18:00 | 5251 |  |  | 0.13728
2020-08-06 19:00 | 5252 |  |  | 0.004962
2020-08-06 20:00 | 5253 |  |  | 0
2020-08-06 21:00 | 5254 |  |  | 0
2020-08-06 22:00 | 5255 |  |  | 0
2020-08-06 23:00 | 5256 |  |  | 0
2020-08-07 | 5257 |  |  | 0
2020-08-07 01:00 | 5258 |  |  | 0
2020-08-07 02:00 | 5259 |  |  | 0
2020-08-07 03:00 | 5260 |  |  | 0
2020-08-07 04:00 | 5261 |  |  | 0
2020-08-07 05:00 | 5262 |  |  | 0
2020-08-07 06:00 | 5263 |  |  | 0
2020-08-07 07:00 | 5264 |  |  | 0.076083
2020-08-07 08:00 | 5265 |  |  | 0.25306
2020-08-07 09:00 | 5266 |  |  | 0.44492
2020-08-07 10:00 | 5267 |  |  | 0.5789
2020-08-07 11:00 | 5268 |  |  | 0.68144
2020-08-07 12:00 | 5269 |  |  | 0.71287
2020-08-07 13:00 | 5270 |  |  | 0.71287
2020-08-07 14:00 | 5271 |  |  | 0.70294
2020-08-07 15:00 | 5272 |  |  | 0.61032
2020-08-07 16:00 | 5273 |  |  | 0.45981
2020-08-07 17:00 | 5274 |  |  | 0.31426
2020-08-07 18:00 | 5275 |  |  | 0.1257
2020-08-07 19:00 | 5276 |  |  | 0.003308
2020-08-07 20:00 | 5277 |  |  | 0
2020-08-07 21:00 | 5278 |  |  | 0
2020-08-07 22:00 | 5279 |  |  | 0
2020-08-07 23:00 | 5280 |  |  | 0
2020-08-08 | 5281 |  |  | 0
2020-08-08 01:00 | 5282 |  |  | 0
2020-08-08 02:00 | 5283 |  |  | 0
2020-08-08 03:00 | 5284 |  |  | 0
2020-08-08 04:00 | 5285 |  |  | 0
2020-08-08 05:00 | 5286 |  |  | 0
2020-08-08 06:00 | 5287 |  |  | 0
2020-08-08 07:00 | 5288 |  |  | 0.082699
2020-08-08 08:00 | 5289 |  |  | 0.2481
2020-08-08 09:00 | 5290 |  |  | 0.43004
2020-08-08 10:00 | 5291 |  |  | 0.56236
2020-08-08 11:00 | 5292 |  |  | 0.67317
2020-08-08 12:00 | 5293 |  |  | 0.71121
2020-08-08 13:00 | 5294 |  |  | 0.71618
2020-08-08 14:00 | 5295 |  |  | 0.69467
2020-08-08 15:00 | 5296 |  |  | 0.60536
2020-08-08 16:00 | 5297 |  |  | 0.48131
2020-08-08 17:00 | 5298 |  |  | 0.3126
2020-08-08 18:00 | 5299 |  |  | 0.1257
2020-08-08 19:00 | 5300 |  |  | 0.001654
2020-08-08 20:00 | 5301 |  |  | 0
2020-08-08 21:00 | 5302 |  |  | 0
2020-08-08 22:00 | 5303 |  |  | 0
2020-08-08 23:00 | 5304 |  |  | 0
2020-08-09 | 5305 |  |  | 0
2020-08-09 01:00 | 5306 |  |  | 0
2020-08-09 02:00 | 5307 |  |  | 0
2020-08-09 03:00 | 5308 |  |  | 0
2020-08-09 04:00 | 5309 |  |  | 0
2020-08-09 05:00 | 5310 |  |  | 0
2020-08-09 06:00 | 5311 |  |  | 0.0099239
2020-08-09 07:00 | 5312 |  |  | 0.062851
2020-08-09 08:00 | 5313 |  |  | 0
2020-08-09 09:00 | 5314 |  |  | 0
2020-08-09 10:00 | 5315 |  |  | 0
2020-08-09 11:00 | 5316 |  |  | 0.41846
2020-08-09 12:00 | 5317 |  |  | 0.70294
2020-08-09 13:00 | 5318 |  |  | 0.71121
2020-08-09 14:00 | 5319 |  |  | 0.70129
2020-08-09 15:00 | 5320 |  |  | 0.60205
2020-08-09 16:00 | 5321 |  |  | 0.47469
2020-08-09 17:00 | 5322 |  |  | 0.29441
2020-08-09 18:00 | 5323 |  |  | 0.090969
2020-08-09 19:00 | 5324 |  |  | 0
2020-08-09 20:00 | 5325 |  |  | 0
2020-08-09 21:00 | 5326 |  |  | 0
2020-08-09 22:00 | 5327 |  |  | 0
2020-08-09 23:00 | 5328 |  |  | 0
2020-08-10 | 5329 |  |  | 0
2020-08-10 01:00 | 5330 |  |  | 0
2020-08-10 02:00 | 5331 |  |  | 0
2020-08-10 03:00 | 5332 |  |  | 0
2020-08-10 04:00 | 5333 |  |  | 0
2020-08-10 05:00 | 5334 |  |  | 0
2020-08-10 06:00 | 5335 |  |  | 0.082699
2020-08-10 07:00 | 5336 |  |  | 0.092623
2020-08-10 08:00 | 5337 |  |  | 0.14059
2020-08-10 09:00 | 5338 |  |  | 0.34238
2020-08-10 10:00 | 5339 |  |  | 0.5392
2020-08-10 11:00 | 5340 |  |  | 0.65332
2020-08-10 12:00 | 5341 |  |  | 0.68475
2020-08-10 13:00 | 5342 |  |  | 0.478
2020-08-10 14:00 | 5343 |  |  | 0.14224
2020-08-10 15:00 | 5344 |  |  | 0.17698
2020-08-10 16:00 | 5345 |  |  | 0.26133
2020-08-10 17:00 | 5346 |  |  | 0.17532
2020-08-10 18:00 | 5347 |  |  | 0.019848
2020-08-10 19:00 | 5348 |  |  | 0
2020-08-10 20:00 | 5349 |  |  | 0
2020-08-10 21:00 | 5350 |  |  | 0
2020-08-10 22:00 | 5351 |  |  | 0
2020-08-10 23:00 | 5352 |  |  | 0
2020-08-11 | 5353 |  |  | 0
2020-08-11 01:00 | 5354 |  |  | 0
2020-08-11 02:00 | 5355 |  |  | 0
2020-08-11 03:00 | 5356 |  |  | 0
2020-08-11 04:00 | 5357 |  |  | 0
2020-08-11 05:00 | 5358 |  |  | 0
2020-08-11 06:00 | 5359 |  |  | 0.0082699
2020-08-11 07:00 | 5360 |  |  | 0.12074
2020-08-11 08:00 | 5361 |  |  | 0.24148
2020-08-11 09:00 | 5362 |  |  | 0.40523
2020-08-11 10:00 | 5363 |  |  | 0.55574
2020-08-11 11:00 | 5364 |  |  | 0.6004
2020-08-11 12:00 | 5365 |  |  | 0.67483
2020-08-11 13:00 | 5366 |  |  | 0.69798
2020-08-11 14:00 | 5367 |  |  | 0.61528
2020-08-11 15:00 | 5368 |  |  | 0.44161
2020-08-11 16:00 | 5369 |  |  | 0.34568
2020-08-11 17:00 | 5370 |  |  | 0.12901
2020-08-11 18:00 | 5371 |  |  | 0.10255
2020-08-11 19:00 | 5372 |  |  | 0
2020-08-11 20:00 | 5373 |  |  | 0
2020-08-11 21:00 | 5374 |  |  | 0
2020-08-11 22:00 | 5375 |  |  | 0
2020-08-11 23:00 | 5376 |  |  | 0
2020-08-12 | 5377 |  |  | 0
2020-08-12 01:00 | 5378 |  |  | 0
2020-08-12 02:00 | 5379 |  |  | 0
2020-08-12 03:00 | 5380 |  |  | 0
2020-08-12 04:00 | 5381 |  |  | 0
2020-08-12 05:00 | 5382 |  |  | 0
2020-08-12 06:00 | 5383 |  |  | 0.0099239
2020-08-12 07:00 | 5384 |  |  | 0.086007
2020-08-12 08:00 | 5385 |  |  | 0.23321
2020-08-12 09:00 | 5386 |  |  | 0.41019
2020-08-12 10:00 | 5387 |  |  | 0.50777
2020-08-12 11:00 | 5388 |  |  | 0.63513
2020-08-12 12:00 | 5389 |  |  | 0.50943
2020-08-12 13:00 | 5390 |  |  | 0.50612
2020-08-12 14:00 | 5391 |  |  | 0.48793
2020-08-12 15:00 | 5392 |  |  | 0.51439
2020-08-12 16:00 | 5393 |  |  | 0.21171
2020-08-12 17:00 | 5394 |  |  | 0.034734
2020-08-12 18:00 | 5395 |  |  | 0
2020-08-12 19:00 | 5396 |  |  | 0
2020-08-12 20:00 | 5397 |  |  | 0
2020-08-12 21:00 | 5398 |  |  | 0
2020-08-12 22:00 | 5399 |  |  | 0
2020-08-12 23:00 | 5400 |  |  | 0
2020-08-13 | 5401 |  |  | 0
2020-08-13 01:00 | 5402 |  |  | 0
2020-08-13 02:00 | 5403 |  |  | 0
2020-08-13 03:00 | 5404 |  |  | 0
2020-08-13 04:00 | 5405 |  |  | 0
2020-08-13 05:00 | 5406 |  |  | 0
2020-08-13 06:00 | 5407 |  |  | 0.04962
2020-08-13 07:00 | 5408 |  |  | 0.086007
2020-08-13 08:00 | 5409 |  |  | 0.16209
2020-08-13 09:00 | 5410 |  |  | 0.41184
2020-08-13 10:00 | 5411 |  |  | 0.56566
2020-08-13 11:00 | 5412 |  |  | 0.58386
2020-08-13 12:00 | 5413 |  |  | 0.39199
2020-08-13 13:00 | 5414 |  |  | 0.30103
2020-08-13 14:00 | 5415 |  |  | 0.29937
2020-08-13 15:00 | 5416 |  |  | 0.29772
2020-08-13 16:00 | 5417 |  |  | 0.14224
2020-08-13 17:00 | 5418 |  |  | 0.13563
2020-08-13 18:00 | 5419 |  |  | 0.023156
2020-08-13 19:00 | 5420 |  |  | 0
2020-08-13 20:00 | 5421 |  |  | 0
2020-08-13 21:00 | 5422 |  |  | 0
2020-08-13 22:00 | 5423 |  |  | 0
2020-08-13 23:00 | 5424 |  |  | 0
2020-08-14 | 5425 |  |  | 0
2020-08-14 01:00 | 5426 |  |  | 0
2020-08-14 02:00 | 5427 |  |  | 0
2020-08-14 03:00 | 5428 |  |  | 0
2020-08-14 04:00 | 5429 |  |  | 0
2020-08-14 05:00 | 5430 |  |  | 0
2020-08-14 06:00 | 5431 |  |  | 0
2020-08-14 07:00 | 5432 |  |  | 0.067813
2020-08-14 08:00 | 5433 |  |  | 0.25141
2020-08-14 09:00 | 5434 |  |  | 0.43169
2020-08-14 10:00 | 5435 |  |  | 0.57724
2020-08-14 11:00 | 5436 |  |  | 0.69302
2020-08-14 12:00 | 5437 |  |  | 0.70294
2020-08-14 13:00 | 5438 |  |  | 0.71121
2020-08-14 14:00 | 5439 |  |  | 0.7046
2020-08-14 15:00 | 5440 |  |  | 0.60205
2020-08-14 16:00 | 5441 |  |  | 0.38869
2020-08-14 17:00 | 5442 |  |  | 0.3126
2020-08-14 18:00 | 5443 |  |  | 0.099239
2020-08-14 19:00 | 5444 |  |  | 0
2020-08-14 20:00 | 5445 |  |  | 0
2020-08-14 21:00 | 5446 |  |  | 0
2020-08-14 22:00 | 5447 |  |  | 0
2020-08-14 23:00 | 5448 |  |  | 0
2020-08-15 | 5449 |  |  | 0
2020-08-15 01:00 | 5450 |  |  | 0
2020-08-15 02:00 | 5451 |  |  | 0
2020-08-15 03:00 | 5452 |  |  | 0
2020-08-15 04:00 | 5453 |  |  | 0
2020-08-15 05:00 | 5454 |  |  | 0
2020-08-15 06:00 | 5455 |  |  | 0.029772
2020-08-15 07:00 | 5456 |  |  | 0.10916
2020-08-15 08:00 | 5457 |  |  | 0.23652
2020-08-15 09:00 | 5458 |  |  | 0.42342
2020-08-15 10:00 | 5459 |  |  | 0.56401
2020-08-15 11:00 | 5460 |  |  | 0.65498
2020-08-15 12:00 | 5461 |  |  | 0.59047
2020-08-15 13:00 | 5462 |  |  | 0.7691
2020-08-15 14:00 | 5463 |  |  | 0.50447
2020-08-15 15:00 | 5464 |  |  | 0.13893
2020-08-15 16:00 | 5465 |  |  | 0.10751
2020-08-15 17:00 | 5466 |  |  | 0.01654
2020-08-15 18:00 | 5467 |  |  | 0.003308
2020-08-15 19:00 | 5468 |  |  | 0.021502
2020-08-15 20:00 | 5469 |  |  | 0
2020-08-15 21:00 | 5470 |  |  | 0
2020-08-15 22:00 | 5471 |  |  | 0
2020-08-15 23:00 | 5472 |  |  | 0
2020-08-16 | 5473 |  |  | 0
2020-08-16 01:00 | 5474 |  |  | 0
2020-08-16 02:00 | 5475 |  |  | 0
2020-08-16 03:00 | 5476 |  |  | 0
2020-08-16 04:00 | 5477 |  |  | 0
2020-08-16 05:00 | 5478 |  |  | 0
2020-08-16 06:00 | 5479 |  |  | 0.023156
2020-08-16 07:00 | 5480 |  |  | 0.099239
2020-08-16 08:00 | 5481 |  |  | 0.24314
2020-08-16 09:00 | 5482 |  |  | 0.37711
2020-08-16 10:00 | 5483 |  |  | 0.51274
2020-08-16 11:00 | 5484 |  |  | 0.57393
2020-08-16 12:00 | 5485 |  |  | 0.51439
2020-08-16 13:00 | 5486 |  |  | 0.44327
2020-08-16 14:00 | 5487 |  |  | 0.33245
2020-08-16 15:00 | 5488 |  |  | 0.34238
2020-08-16 16:00 | 5489 |  |  | 0.028118
2020-08-16 17:00 | 5490 |  |  | 0.001654
2020-08-16 18:00 | 5491 |  |  | 0
2020-08-16 19:00 | 5492 |  |  | 0
2020-08-16 20:00 | 5493 |  |  | 0
2020-08-16 21:00 | 5494 |  |  | 0
2020-08-16 22:00 | 5495 |  |  | 0
2020-08-16 23:00 | 5496 |  |  | 0
2020-08-17 | 5497 |  |  | 0
2020-08-17 01:00 | 5498 |  |  | 0
2020-08-17 02:00 | 5499 |  |  | 0
2020-08-17 03:00 | 5500 |  |  | 0
2020-08-17 04:00 | 5501 |  |  | 0
2020-08-17 05:00 | 5502 |  |  | 0
2020-08-17 06:00 | 5503 |  |  | 0.039696
2020-08-17 07:00 | 5504 |  |  | 0.12736
2020-08-17 08:00 | 5505 |  |  | 0.004962
2020-08-17 09:00 | 5506 |  |  | 0.51185
2020-08-17 10:00 | 5507 |  |  | 0.55983
2020-08-17 11:00 | 5508 |  |  | 0.56924
2020-08-17 12:00 | 5509 |  |  | 0.51091
2020-08-17 13:00 | 5510 |  |  | 0.23321
2020-08-17 14:00 | 5511 |  |  | 0.011578
2020-08-17 15:00 | 5512 |  |  | 0.35891
2020-08-17 16:00 | 5513 |  |  | 0.25637
2020-08-17 17:00 | 5514 |  |  | 0.27456
2020-08-17 18:00 | 5515 |  |  | 0.036388
2020-08-17 19:00 | 5516 |  |  | 0
2020-08-17 20:00 | 5517 |  |  | 0
2020-08-17 21:00 | 5518 |  |  | 0
2020-08-17 22:00 | 5519 |  |  | 0
2020-08-17 23:00 | 5520 |  |  | 0
2020-08-18 | 5521 |  |  | 0
2020-08-18 01:00 | 5522 |  |  | 0
2020-08-18 02:00 | 5523 |  |  | 0
2020-08-18 03:00 | 5524 |  |  | 0
2020-08-18 04:00 | 5525 |  |  | 0
2020-08-18 05:00 | 5526 |  |  | 0
2020-08-18 06:00 | 5527 |  |  | 0
2020-08-18 07:00 | 5528 |  |  | 0.076083
2020-08-18 08:00 | 5529 |  |  | 0.24644
2020-08-18 09:00 | 5530 |  |  | 0.43996
2020-08-18 10:00 | 5531 |  |  | 0.478
2020-08-18 11:00 | 5532 |  |  | 0.66325
2020-08-18 12:00 | 5533 |  |  | 0.71618
2020-08-18 13:00 | 5534 |  |  | 0.7046
2020-08-18 14:00 | 5535 |  |  | 0.48958
2020-08-18 15:00 | 5536 |  |  | 0.52266
2020-08-18 16:00 | 5537 |  |  | 0.44988
2020-08-18 17:00 | 5538 |  |  | 0.30599
2020-08-18 18:00 | 5539 |  |  | 0.10255
2020-08-18 19:00 | 5540 |  |  | 0
2020-08-18 20:00 | 5541 |  |  | 0
2020-08-18 21:00 | 5542 |  |  | 0
2020-08-18 22:00 | 5543 |  |  | 0
2020-08-18 23:00 | 5544 |  |  | 0
2020-08-19 | 5545 |  |  | 0
2020-08-19 01:00 | 5546 |  |  | 0
2020-08-19 02:00 | 5547 |  |  | 0
2020-08-19 03:00 | 5548 |  |  | 0
2020-08-19 04:00 | 5549 |  |  | 0
2020-08-19 05:00 | 5550 |  |  | 0
2020-08-19 06:00 | 5551 |  |  | 0.01654
2020-08-19 07:00 | 5552 |  |  | 0.084353
2020-08-19 08:00 | 5553 |  |  | 0.2481
2020-08-19 09:00 | 5554 |  |  | 0.43831
2020-08-19 10:00 | 5555 |  |  | 0.57724
2020-08-19 11:00 | 5556 |  |  | 0.32584
2020-08-19 12:00 | 5557 |  |  | 0.42673
2020-08-19 13:00 | 5558 |  |  | 0.60536
2020-08-19 14:00 | 5559 |  |  | 0.63513
2020-08-19 15:00 | 5560 |  |  | 0.45154
2020-08-19 16:00 | 5561 |  |  | 0.35561
2020-08-19 17:00 | 5562 |  |  | 0.32418
2020-08-19 18:00 | 5563 |  |  | 0.097585
2020-08-19 19:00 | 5564 |  |  | 0
2020-08-19 20:00 | 5565 |  |  | 0
2020-08-19 21:00 | 5566 |  |  | 0
2020-08-19 22:00 | 5567 |  |  | 0
2020-08-19 23:00 | 5568 |  |  | 0
2020-08-20 | 5569 |  |  | 0
2020-08-20 01:00 | 5570 |  |  | 0
2020-08-20 02:00 | 5571 |  |  | 0
2020-08-20 03:00 | 5572 |  |  | 0
2020-08-20 04:00 | 5573 |  |  | 0
2020-08-20 05:00 | 5574 |  |  | 0
2020-08-20 06:00 | 5575 |  |  | 0.0066159
2020-08-20 07:00 | 5576 |  |  | 0.077737
2020-08-20 08:00 | 5577 |  |  | 0.21171
2020-08-20 09:00 | 5578 |  |  | 0.38042
2020-08-20 10:00 | 5579 |  |  | 0.55905
2020-08-20 11:00 | 5580 |  |  | 0.61528
2020-08-20 12:00 | 5581 |  |  | 0.48793
2020-08-20 13:00 | 5582 |  |  | 0.26133
2020-08-20 14:00 | 5583 |  |  | 0.1472
2020-08-20 15:00 | 5584 |  |  | 0.25637
2020-08-20 16:00 | 5585 |  |  | 0.13066
2020-08-20 17:00 | 5586 |  |  | 0.029772
2020-08-20 18:00 | 5587 |  |  | 0
2020-08-20 19:00 | 5588 |  |  | 0
2020-08-20 20:00 | 5589 |  |  | 0
2020-08-20 21:00 | 5590 |  |  | 0
2020-08-20 22:00 | 5591 |  |  | 0
2020-08-20 23:00 | 5592 |  |  | 0
2020-08-21 | 5593 |  |  | 0
2020-08-21 01:00 | 5594 |  |  | 0
2020-08-21 02:00 | 5595 |  |  | 0
2020-08-21 03:00 | 5596 |  |  | 0
2020-08-21 04:00 | 5597 |  |  | 0
2020-08-21 05:00 | 5598 |  |  | 0
2020-08-21 06:00 | 5599 |  |  | 0.0082699
2020-08-21 07:00 | 5600 |  |  | 0.087661
2020-08-21 08:00 | 5601 |  |  | 0.22825
2020-08-21 09:00 | 5602 |  |  | 0.37711
2020-08-21 10:00 | 5603 |  |  | 0.55409
2020-08-21 11:00 | 5604 |  |  | 0.66986
2020-08-21 12:00 | 5605 |  |  | 0.60536
2020-08-21 13:00 | 5606 |  |  | 0.36718
2020-08-21 14:00 | 5607 |  |  | 0.36718
2020-08-21 15:00 | 5608 |  |  | 0.38538
2020-08-21 16:00 | 5609 |  |  | 0.23983
2020-08-21 17:00 | 5610 |  |  | 0.13066
2020-08-21 18:00 | 5611 |  |  | 0.056236
2020-08-21 19:00 | 5612 |  |  | 0
2020-08-21 20:00 | 5613 |  |  | 0
2020-08-21 21:00 | 5614 |  |  | 0
2020-08-21 22:00 | 5615 |  |  | 0
2020-08-21 23:00 | 5616 |  |  | 0
2020-08-22 | 5617 |  |  | 0
2020-08-22 01:00 | 5618 |  |  | 0
2020-08-22 02:00 | 5619 |  |  | 0
2020-08-22 03:00 | 5620 |  |  | 0
2020-08-22 04:00 | 5621 |  |  | 0
2020-08-22 05:00 | 5622 |  |  | 0
2020-08-22 06:00 | 5623 |  |  | 0.011578
2020-08-22 07:00 | 5624 |  |  | 0.087661
2020-08-22 08:00 | 5625 |  |  | 0.23321
2020-08-22 09:00 | 5626 |  |  | 0.40853
2020-08-22 10:00 | 5627 |  |  | 0.56732
2020-08-22 11:00 | 5628 |  |  | 0.66821
2020-08-22 12:00 | 5629 |  |  | 0.70294
2020-08-22 13:00 | 5630 |  |  | 0.71121
2020-08-22 14:00 | 5631 |  |  | 0.69467
2020-08-22 15:00 | 5632 |  |  | 0.58386
2020-08-22 16:00 | 5633 |  |  | 0.46808
2020-08-22 17:00 | 5634 |  |  | 0.27787
2020-08-22 18:00 | 5635 |  |  | 0.059543
2020-08-22 19:00 | 5636 |  |  | 0
2020-08-22 20:00 | 5637 |  |  | 0
2020-08-22 21:00 | 5638 |  |  | 0
2020-08-22 22:00 | 5639 |  |  | 0
2020-08-22 23:00 | 5640 |  |  | 0
2020-08-23 | 5641 |  |  | 0
2020-08-23 01:00 | 5642 |  |  | 0
2020-08-23 02:00 | 5643 |  |  | 0
2020-08-23 03:00 | 5644 |  |  | 0
2020-08-23 04:00 | 5645 |  |  | 0
2020-08-23 05:00 | 5646 |  |  | 0
2020-08-23 06:00 | 5647 |  |  | 0.0066159
2020-08-23 07:00 | 5648 |  |  | 0.067813
2020-08-23 08:00 | 5649 |  |  | 0.27291
2020-08-23 09:00 | 5650 |  |  | 0.44492
2020-08-23 10:00 | 5651 |  |  | 0.57724
2020-08-23 11:00 | 5652 |  |  | 0.63513
2020-08-23 12:00 | 5653 |  |  | 0.48462
2020-08-23 13:00 | 5654 |  |  | 0.71783
2020-08-23 14:00 | 5655 |  |  | 0.70294
2020-08-23 15:00 | 5656 |  |  | 0.61032
2020-08-23 16:00 | 5657 |  |  | 0.48296
2020-08-23 17:00 | 5658 |  |  | 0.28945
2020-08-23 18:00 | 5659 |  |  | 0.079391
2020-08-23 19:00 | 5660 |  |  | 0
2020-08-23 20:00 | 5661 |  |  | 0
2020-08-23 21:00 | 5662 |  |  | 0
2020-08-23 22:00 | 5663 |  |  | 0
2020-08-23 23:00 | 5664 |  |  | 0
2020-08-24 | 5665 |  |  | 0
2020-08-24 01:00 | 5666 |  |  | 0
2020-08-24 02:00 | 5667 |  |  | 0
2020-08-24 03:00 | 5668 |  |  | 0
2020-08-24 04:00 | 5669 |  |  | 0
2020-08-24 05:00 | 5670 |  |  | 0
2020-08-24 06:00 | 5671 |  |  | 0.028118
2020-08-24 07:00 | 5672 |  |  | 0.1257
2020-08-24 08:00 | 5673 |  |  | 0.15547
2020-08-24 09:00 | 5674 |  |  | 0.36222
2020-08-24 10:00 | 5675 |  |  | 0.4168
2020-08-24 11:00 | 5676 |  |  | 0.60205
2020-08-24 12:00 | 5677 |  |  | 0.45154
2020-08-24 13:00 | 5678 |  |  | 0.46146
2020-08-24 14:00 | 5679 |  |  | 0.34403
2020-08-24 15:00 | 5680 |  |  | 0.55574
2020-08-24 16:00 | 5681 |  |  | 0.15051
2020-08-24 17:00 | 5682 |  |  | 0.081045
2020-08-24 18:00 | 5683 |  |  | 0.028118
2020-08-24 19:00 | 5684 |  |  | 0
2020-08-24 20:00 | 5685 |  |  | 0
2020-08-24 21:00 | 5686 |  |  | 0
2020-08-24 22:00 | 5687 |  |  | 0
2020-08-24 23:00 | 5688 |  |  | 0
2020-08-25 | 5689 |  |  | 0
2020-08-25 01:00 | 5690 |  |  | 0
2020-08-25 02:00 | 5691 |  |  | 0
2020-08-25 03:00 | 5692 |  |  | 0
2020-08-25 04:00 | 5693 |  |  | 0
2020-08-25 05:00 | 5694 |  |  | 0
2020-08-25 06:00 | 5695 |  |  | 0.011578
2020-08-25 07:00 | 5696 |  |  | 0.099239
2020-08-25 08:00 | 5697 |  |  | 0.27952
2020-08-25 09:00 | 5698 |  |  | 0.43665
2020-08-25 10:00 | 5699 |  |  | 0.58386
2020-08-25 11:00 | 5700 |  |  | 0.59709
2020-08-25 12:00 | 5701 |  |  | 0.73768
2020-08-25 13:00 | 5702 |  |  | 0.37545
2020-08-25 14:00 | 5703 |  |  | 0.40357
2020-08-25 15:00 | 5704 |  |  | 0.44327
2020-08-25 16:00 | 5705 |  |  | 0.3738
2020-08-25 17:00 | 5706 |  |  | 0.13728
2020-08-25 18:00 | 5707 |  |  | 0.029772
2020-08-25 19:00 | 5708 |  |  | 0
2020-08-25 20:00 | 5709 |  |  | 0
2020-08-25 21:00 | 5710 |  |  | 0
2020-08-25 22:00 | 5711 |  |  | 0
2020-08-25 23:00 | 5712 |  |  | 0
2020-08-26 | 5713 |  |  | 0
2020-08-26 01:00 | 5714 |  |  | 0
2020-08-26 02:00 | 5715 |  |  | 0
2020-08-26 03:00 | 5716 |  |  | 0
2020-08-26 04:00 | 5717 |  |  | 0
2020-08-26 05:00 | 5718 |  |  | 0
2020-08-26 06:00 | 5719 |  |  | 0
2020-08-26 07:00 | 5720 |  |  | 0.077737
2020-08-26 08:00 | 5721 |  |  | 0.20509
2020-08-26 09:00 | 5722 |  |  | 0.31426
2020-08-26 10:00 | 5723 |  |  | 0.5822
2020-08-26 11:00 | 5724 |  |  | 0.67813
2020-08-26 12:00 | 5725 |  |  | 0.68806
2020-08-26 13:00 | 5726 |  |  | 0.57724
2020-08-26 14:00 | 5727 |  |  | 0.63513
2020-08-26 15:00 | 5728 |  |  | 0.59543
2020-08-26 16:00 | 5729 |  |  | 0.47304
2020-08-26 17:00 | 5730 |  |  | 0.26464
2020-08-26 18:00 | 5731 |  |  | 0.051274
2020-08-26 19:00 | 5732 |  |  | 0
2020-08-26 20:00 | 5733 |  |  | 0
2020-08-26 21:00 | 5734 |  |  | 0
2020-08-26 22:00 | 5735 |  |  | 0
2020-08-26 23:00 | 5736 |  |  | 0
2020-08-27 | 5737 |  |  | 0
2020-08-27 01:00 | 5738 |  |  | 0
2020-08-27 02:00 | 5739 |  |  | 0
2020-08-27 03:00 | 5740 |  |  | 0
2020-08-27 04:00 | 5741 |  |  | 0
2020-08-27 05:00 | 5742 |  |  | 0
2020-08-27 06:00 | 5743 |  |  | 0
2020-08-27 07:00 | 5744 |  |  | 0.061197
2020-08-27 08:00 | 5745 |  |  | 0.23983
2020-08-27 09:00 | 5746 |  |  | 0.43169
2020-08-27 10:00 | 5747 |  |  | 0.57559
2020-08-27 11:00 | 5748 |  |  | 0.47635
2020-08-27 12:00 | 5749 |  |  | 0.64836
2020-08-27 13:00 | 5750 |  |  | 0.46973
2020-08-27 14:00 | 5751 |  |  | 0.43004
2020-08-27 15:00 | 5752 |  |  | 0.20509
2020-08-27 16:00 | 5753 |  |  | 0.22163
2020-08-27 17:00 | 5754 |  |  | 0.097585
2020-08-27 18:00 | 5755 |  |  | 0.02481
2020-08-27 19:00 | 5756 |  |  | 0
2020-08-27 20:00 | 5757 |  |  | 0
2020-08-27 21:00 | 5758 |  |  | 0
2020-08-27 22:00 | 5759 |  |  | 0
2020-08-27 23:00 | 5760 |  |  | 0
2020-08-28 | 5761 |  |  | 0
2020-08-28 01:00 | 5762 |  |  | 0
2020-08-28 02:00 | 5763 |  |  | 0
2020-08-28 03:00 | 5764 |  |  | 0
2020-08-28 04:00 | 5765 |  |  | 0
2020-08-28 05:00 | 5766 |  |  | 0
2020-08-28 06:00 | 5767 |  |  | 0.023156
2020-08-28 07:00 | 5768 |  |  | 0.12901
2020-08-28 08:00 | 5769 |  |  | 0.20013
2020-08-28 09:00 | 5770 |  |  | 0.17863
2020-08-28 10:00 | 5771 |  |  | 0.48462
2020-08-28 11:00 | 5772 |  |  | 0.34072
2020-08-28 12:00 | 5773 |  |  | 0.46642
2020-08-28 13:00 | 5774 |  |  | 0.28614
2020-08-28 14:00 | 5775 |  |  | 0.038042
2020-08-28 15:00 | 5776 |  |  | 0.18525
2020-08-28 16:00 | 5777 |  |  | 0.1869
2020-08-28 17:00 | 5778 |  |  | 0.039696
2020-08-28 18:00 | 5779 |  |  | 0.0099239
2020-08-28 19:00 | 5780 |  |  | 0
2020-08-28 20:00 | 5781 |  |  | 0
2020-08-28 21:00 | 5782 |  |  | 0
2020-08-28 22:00 | 5783 |  |  | 0
2020-08-28 23:00 | 5784 |  |  | 0
2020-08-29 | 5785 |  |  | 0
2020-08-29 01:00 | 5786 |  |  | 0
2020-08-29 02:00 | 5787 |  |  | 0
2020-08-29 03:00 | 5788 |  |  | 0
2020-08-29 04:00 | 5789 |  |  | 0
2020-08-29 05:00 | 5790 |  |  | 0
2020-08-29 06:00 | 5791 |  |  | 0
2020-08-29 07:00 | 5792 |  |  | 0.019848
2020-08-29 08:00 | 5793 |  |  | 0.044658
2020-08-29 09:00 | 5794 |  |  | 0.13232
2020-08-29 10:00 | 5795 |  |  | 0.18525
2020-08-29 11:00 | 5796 |  |  | 0.23817
2020-08-29 12:00 | 5797 |  |  | 0.32749
2020-08-29 13:00 | 5798 |  |  | 0.13893
2020-08-29 14:00 | 5799 |  |  | 0.14224
2020-08-29 15:00 | 5800 |  |  | 0.1472
2020-08-29 16:00 | 5801 |  |  | 0.11743
2020-08-29 17:00 | 5802 |  |  | 0.02481
2020-08-29 18:00 | 5803 |  |  | 0.001654
2020-08-29 19:00 | 5804 |  |  | 0
2020-08-29 20:00 | 5805 |  |  | 0
2020-08-29 21:00 | 5806 |  |  | 0
2020-08-29 22:00 | 5807 |  |  | 0
2020-08-29 23:00 | 5808 |  |  | 0
2020-08-30 | 5809 |  |  | 0
2020-08-30 01:00 | 5810 |  |  | 0
2020-08-30 02:00 | 5811 |  |  | 0
2020-08-30 03:00 | 5812 |  |  | 0
2020-08-30 04:00 | 5813 |  |  | 0
2020-08-30 05:00 | 5814 |  |  | 0
2020-08-30 06:00 | 5815 |  |  | 0
2020-08-30 07:00 | 5816 |  |  | 0.004962
2020-08-30 08:00 | 5817 |  |  | 0.25141
2020-08-30 09:00 | 5818 |  |  | 0.45981
2020-08-30 10:00 | 5819 |  |  | 0.60205
2020-08-30 11:00 | 5820 |  |  | 0.70956
2020-08-30 12:00 | 5821 |  |  | 0.74429
2020-08-30 13:00 | 5822 |  |  | 0.75422
2020-08-30 14:00 | 5823 |  |  | 0.71287
2020-08-30 15:00 | 5824 |  |  | 0.62024
2020-08-30 16:00 | 5825 |  |  | 0.47139
2020-08-30 17:00 | 5826 |  |  | 0.2911
2020-08-30 18:00 | 5827 |  |  | 0.011578
2020-08-30 19:00 | 5828 |  |  | 0
2020-08-30 20:00 | 5829 |  |  | 0
2020-08-30 21:00 | 5830 |  |  | 0
2020-08-30 22:00 | 5831 |  |  | 0
2020-08-30 23:00 | 5832 |  |  | 0
2020-08-31 | 5833 |  |  | 0
2020-08-31 01:00 | 5834 |  |  | 0
2020-08-31 02:00 | 5835 |  |  | 0
2020-08-31 03:00 | 5836 |  |  | 0
2020-08-31 04:00 | 5837 |  |  | 0
2020-08-31 05:00 | 5838 |  |  | 0
2020-08-31 06:00 | 5839 |  |  | 0.001654
2020-08-31 07:00 | 5840 |  |  | 0.046312
2020-08-31 08:00 | 5841 |  |  | 0.25802
2020-08-31 09:00 | 5842 |  |  | 0.30764
2020-08-31 10:00 | 5843 |  |  | 0.47139
2020-08-31 11:00 | 5844 |  |  | 0.73437
2020-08-31 12:00 | 5845 |  |  | 0.65994
2020-08-31 13:00 | 5846 |  |  | 0.39034
2020-08-31 14:00 | 5847 |  |  | 0.46146
2020-08-31 15:00 | 5848 |  |  | 0.44492
2020-08-31 16:00 | 5849 |  |  | 0.50281
2020-08-31 17:00 | 5850 |  |  | 0.21171
2020-08-31 18:00 | 5851 |  |  | 0.05789
2020-08-31 19:00 | 5852 |  |  | 0
2020-08-31 20:00 | 5853 |  |  | 0
2020-08-31 21:00 | 5854 |  |  | 0
2020-08-31 22:00 | 5855 |  |  | 0
2020-08-31 23:00 | 5856 |  |  | 0
2020-09-01 | 5857 |  |  | 0
2020-09-01 01:00 | 5858 |  |  | 0
2020-09-01 02:00 | 5859 |  |  | 0
2020-09-01 03:00 | 5860 |  |  | 0
2020-09-01 04:00 | 5861 |  |  | 0
2020-09-01 05:00 | 5862 |  |  | 0
2020-09-01 06:00 | 5863 |  |  | 0
2020-09-01 07:00 | 5864 |  |  | 0.05789
2020-09-01 08:00 | 5865 |  |  | 0.24479
2020-09-01 09:00 | 5866 |  |  | 0.44658
2020-09-01 10:00 | 5867 |  |  | 0.58717
2020-09-01 11:00 | 5868 |  |  | 0.69467
2020-09-01 12:00 | 5869 |  |  | 0.74595
2020-09-01 13:00 | 5870 |  |  | 0.75256
2020-09-01 14:00 | 5871 |  |  | 0.70294
2020-09-01 15:00 | 5872 |  |  | 0.5789
2020-09-01 16:00 | 5873 |  |  | 0.43334
2020-09-01 17:00 | 5874 |  |  | 0.15547
2020-09-01 18:00 | 5875 |  |  | 0.03308
2020-09-01 19:00 | 5876 |  |  | 0
2020-09-01 20:00 | 5877 |  |  | 0
2020-09-01 21:00 | 5878 |  |  | 0
2020-09-01 22:00 | 5879 |  |  | 0
2020-09-01 23:00 | 5880 |  |  | 0
2020-09-02 | 5881 |  |  | 0
2020-09-02 01:00 | 5882 |  |  | 0
2020-09-02 02:00 | 5883 |  |  | 0
2020-09-02 03:00 | 5884 |  |  | 0
2020-09-02 04:00 | 5885 |  |  | 0
2020-09-02 05:00 | 5886 |  |  | 0
2020-09-02 06:00 | 5887 |  |  | 0
2020-09-02 07:00 | 5888 |  |  | 0.014886
2020-09-02 08:00 | 5889 |  |  | 0.026464
2020-09-02 09:00 | 5890 |  |  | 0.092623
2020-09-02 10:00 | 5891 |  |  | 0.31922
2020-09-02 11:00 | 5892 |  |  | 0.71783
2020-09-02 12:00 | 5893 |  |  | 0.5789
2020-09-02 13:00 | 5894 |  |  | 0.73602
2020-09-02 14:00 | 5895 |  |  | 0.45319
2020-09-02 15:00 | 5896 |  |  | 0.26298
2020-09-02 16:00 | 5897 |  |  | 0.074429
2020-09-02 17:00 | 5898 |  |  | 0.001654
2020-09-02 18:00 | 5899 |  |  | 0
2020-09-02 19:00 | 5900 |  |  | 0
2020-09-02 20:00 | 5901 |  |  | 0
2020-09-02 21:00 | 5902 |  |  | 0
2020-09-02 22:00 | 5903 |  |  | 0
2020-09-02 23:00 | 5904 |  |  | 0
2020-09-03 | 5905 |  |  | 0
2020-09-03 01:00 | 5906 |  |  | 0
2020-09-03 02:00 | 5907 |  |  | 0
2020-09-03 03:00 | 5908 |  |  | 0
2020-09-03 04:00 | 5909 |  |  | 0
2020-09-03 05:00 | 5910 |  |  | 0
2020-09-03 06:00 | 5911 |  |  | 0.014886
2020-09-03 07:00 | 5912 |  |  | 0.052928
2020-09-03 08:00 | 5913 |  |  | 0.21336
2020-09-03 09:00 | 5914 |  |  | 0.4168
2020-09-03 10:00 | 5915 |  |  | 0.58386
2020-09-03 11:00 | 5916 |  |  | 0.71121
2020-09-03 12:00 | 5917 |  |  | 0.73933
2020-09-03 13:00 | 5918 |  |  | 0.75422
2020-09-03 14:00 | 5919 |  |  | 0.69302
2020-09-03 15:00 | 5920 |  |  | 0.58882
2020-09-03 16:00 | 5921 |  |  | 0.43004
2020-09-03 17:00 | 5922 |  |  | 0.22825
2020-09-03 18:00 | 5923 |  |  | 0.019848
2020-09-03 19:00 | 5924 |  |  | 0
2020-09-03 20:00 | 5925 |  |  | 0
2020-09-03 21:00 | 5926 |  |  | 0
2020-09-03 22:00 | 5927 |  |  | 0
2020-09-03 23:00 | 5928 |  |  | 0
2020-09-04 | 5929 |  |  | 0
2020-09-04 01:00 | 5930 |  |  | 0
2020-09-04 02:00 | 5931 |  |  | 0
2020-09-04 03:00 | 5932 |  |  | 0
2020-09-04 04:00 | 5933 |  |  | 0
2020-09-04 05:00 | 5934 |  |  | 0
2020-09-04 06:00 | 5935 |  |  | 0
2020-09-04 07:00 | 5936 |  |  | 0.061197
2020-09-04 08:00 | 5937 |  |  | 0.22825
2020-09-04 09:00 | 5938 |  |  | 0.42011
2020-09-04 10:00 | 5939 |  |  | 0.56566
2020-09-04 11:00 | 5940 |  |  | 0.66986
2020-09-04 12:00 | 5941 |  |  | 0.70294
2020-09-04 13:00 | 5942 |  |  | 0.71121
2020-09-04 14:00 | 5943 |  |  | 0.69633
2020-09-04 15:00 | 5944 |  |  | 0.57393
2020-09-04 16:00 | 5945 |  |  | 0.43665
2020-09-04 17:00 | 5946 |  |  | 0.2266
2020-09-04 18:00 | 5947 |  |  | 0.029772
2020-09-04 19:00 | 5948 |  |  | 0
2020-09-04 20:00 | 5949 |  |  | 0
2020-09-04 21:00 | 5950 |  |  | 0
2020-09-04 22:00 | 5951 |  |  | 0
2020-09-04 23:00 | 5952 |  |  | 0
2020-09-05 | 5953 |  |  | 0
2020-09-05 01:00 | 5954 |  |  | 0
2020-09-05 02:00 | 5955 |  |  | 0
2020-09-05 03:00 | 5956 |  |  | 0
2020-09-05 04:00 | 5957 |  |  | 0
2020-09-05 05:00 | 5958 |  |  | 0
2020-09-05 06:00 | 5959 |  |  | 0
2020-09-05 07:00 | 5960 |  |  | 0.071121
2020-09-05 08:00 | 5961 |  |  | 0.22494
2020-09-05 09:00 | 5962 |  |  | 0.4135
2020-09-05 10:00 | 5963 |  |  | 0.56401
2020-09-05 11:00 | 5964 |  |  | 0.66325
2020-09-05 12:00 | 5965 |  |  | 0.71121
2020-09-05 13:00 | 5966 |  |  | 0.71121
2020-09-05 14:00 | 5967 |  |  | 0.67152
2020-09-05 15:00 | 5968 |  |  | 0.56236
2020-09-05 16:00 | 5969 |  |  | 0.40192
2020-09-05 17:00 | 5970 |  |  | 0.19848
2020-09-05 18:00 | 5971 |  |  | 0.01654
2020-09-05 19:00 | 5972 |  |  | 0
2020-09-05 20:00 | 5973 |  |  | 0
2020-09-05 21:00 | 5974 |  |  | 0
2020-09-05 22:00 | 5975 |  |  | 0
2020-09-05 23:00 | 5976 |  |  | 0
2020-09-06 | 5977 |  |  | 0
2020-09-06 01:00 | 5978 |  |  | 0
2020-09-06 02:00 | 5979 |  |  | 0
2020-09-06 03:00 | 5980 |  |  | 0
2020-09-06 04:00 | 5981 |  |  | 0
2020-09-06 05:00 | 5982 |  |  | 0
2020-09-06 06:00 | 5983 |  |  | 0
2020-09-06 07:00 | 5984 |  |  | 0.062851
2020-09-06 08:00 | 5985 |  |  | 0.22163
2020-09-06 09:00 | 5986 |  |  | 0.40523
2020-09-06 10:00 | 5987 |  |  | 0.3953
2020-09-06 11:00 | 5988 |  |  | 0.53755
2020-09-06 12:00 | 5989 |  |  | 0.67648
2020-09-06 13:00 | 5990 |  |  | 0.54251
2020-09-06 14:00 | 5991 |  |  | 0.32253
2020-09-06 15:00 | 5992 |  |  | 0.1654
2020-09-06 16:00 | 5993 |  |  | 0.076083
2020-09-06 17:00 | 5994 |  |  | 0
2020-09-06 18:00 | 5995 |  |  | 0
2020-09-06 19:00 | 5996 |  |  | 0
2020-09-06 20:00 | 5997 |  |  | 0
2020-09-06 21:00 | 5998 |  |  | 0
2020-09-06 22:00 | 5999 |  |  | 0
2020-09-06 23:00 | 6000 |  |  | 0
2020-09-07 | 6001 |  |  | 0
2020-09-07 01:00 | 6002 |  |  | 0
2020-09-07 02:00 | 6003 |  |  | 0
2020-09-07 03:00 | 6004 |  |  | 0
2020-09-07 04:00 | 6005 |  |  | 0
2020-09-07 05:00 | 6006 |  |  | 0
2020-09-07 06:00 | 6007 |  |  | 0
2020-09-07 07:00 | 6008 |  |  | 0.059543
2020-09-07 08:00 | 6009 |  |  | 0.15217
2020-09-07 09:00 | 6010 |  |  | 0.17698
2020-09-07 10:00 | 6011 |  |  | 0.2696
2020-09-07 11:00 | 6012 |  |  | 0.21171
2020-09-07 12:00 | 6013 |  |  | 0.15382
2020-09-07 13:00 | 6014 |  |  | 0.35395
2020-09-07 14:00 | 6015 |  |  | 0.42011
2020-09-07 15:00 | 6016 |  |  | 0.55243
2020-09-07 16:00 | 6017 |  |  | 0.435
2020-09-07 17:00 | 6018 |  |  | 0.23321
2020-09-07 18:00 | 6019 |  |  | 0.019848
2020-09-07 19:00 | 6020 |  |  | 0
2020-09-07 20:00 | 6021 |  |  | 0
2020-09-07 21:00 | 6022 |  |  | 0
2020-09-07 22:00 | 6023 |  |  | 0
2020-09-07 23:00 | 6024 |  |  | 0
2020-09-08 | 6025 |  |  | 0
2020-09-08 01:00 | 6026 |  |  | 0
2020-09-08 02:00 | 6027 |  |  | 0
2020-09-08 03:00 | 6028 |  |  | 0
2020-09-08 04:00 | 6029 |  |  | 0
2020-09-08 05:00 | 6030 |  |  | 0
2020-09-08 06:00 | 6031 |  |  | 0
2020-09-08 07:00 | 6032 |  |  | 0.05789
2020-09-08 08:00 | 6033 |  |  | 0.23156
2020-09-08 09:00 | 6034 |  |  | 0.42011
2020-09-08 10:00 | 6035 |  |  | 0.57228
2020-09-08 11:00 | 6036 |  |  | 0.6831
2020-09-08 12:00 | 6037 |  |  | 0.5789
2020-09-08 13:00 | 6038 |  |  | 0.38538
2020-09-08 14:00 | 6039 |  |  | 0.36718
2020-09-08 15:00 | 6040 |  |  | 0.48627
2020-09-08 16:00 | 6041 |  |  | 0.39696
2020-09-08 17:00 | 6042 |  |  | 0.061197
2020-09-08 18:00 | 6043 |  |  | 0
2020-09-08 19:00 | 6044 |  |  | 0
2020-09-08 20:00 | 6045 |  |  | 0
2020-09-08 21:00 | 6046 |  |  | 0
2020-09-08 22:00 | 6047 |  |  | 0
2020-09-08 23:00 | 6048 |  |  | 0
2020-09-09 | 6049 |  |  | 0
2020-09-09 01:00 | 6050 |  |  | 0
2020-09-09 02:00 | 6051 |  |  | 0
2020-09-09 03:00 | 6052 |  |  | 0
2020-09-09 04:00 | 6053 |  |  | 0
2020-09-09 05:00 | 6054 |  |  | 0
2020-09-09 06:00 | 6055 |  |  | 0.004962
2020-09-09 07:00 | 6056 |  |  | 0.081045
2020-09-09 08:00 | 6057 |  |  | 0.17698
2020-09-09 09:00 | 6058 |  |  | 0.42507
2020-09-09 10:00 | 6059 |  |  | 0.30103
2020-09-09 11:00 | 6060 |  |  | 0.44988
2020-09-09 12:00 | 6061 |  |  | 0.55409
2020-09-09 13:00 | 6062 |  |  | 0.70294
2020-09-09 14:00 | 6063 |  |  | 0.62355
2020-09-09 15:00 | 6064 |  |  | 0.51274
2020-09-09 16:00 | 6065 |  |  | 0.20509
2020-09-09 17:00 | 6066 |  |  | 0.15713
2020-09-09 18:00 | 6067 |  |  | 0.003308
2020-09-09 19:00 | 6068 |  |  | 0
2020-09-09 20:00 | 6069 |  |  | 0
2020-09-09 21:00 | 6070 |  |  | 0
2020-09-09 22:00 | 6071 |  |  | 0
2020-09-09 23:00 | 6072 |  |  | 0
2020-09-10 | 6073 |  |  | 0
2020-09-10 01:00 | 6074 |  |  | 0
2020-09-10 02:00 | 6075 |  |  | 0
2020-09-10 03:00 | 6076 |  |  | 0
2020-09-10 04:00 | 6077 |  |  | 0
2020-09-10 05:00 | 6078 |  |  | 0
2020-09-10 06:00 | 6079 |  |  | 0.001654
2020-09-10 07:00 | 6080 |  |  | 0.079391
2020-09-10 08:00 | 6081 |  |  | 0.16209
2020-09-10 09:00 | 6082 |  |  | 0.35726
2020-09-10 10:00 | 6083 |  |  | 0.54912
2020-09-10 11:00 | 6084 |  |  | 0.52928
2020-09-10 12:00 | 6085 |  |  | 0.67483
2020-09-10 13:00 | 6086 |  |  | 0.48958
2020-09-10 14:00 | 6087 |  |  | 0.25637
2020-09-10 15:00 | 6088 |  |  | 0.22494
2020-09-10 16:00 | 6089 |  |  | 0.2696
2020-09-10 17:00 | 6090 |  |  | 0.079391
2020-09-10 18:00 | 6091 |  |  | 0
2020-09-10 19:00 | 6092 |  |  | 0
2020-09-10 20:00 | 6093 |  |  | 0
2020-09-10 21:00 | 6094 |  |  | 0
2020-09-10 22:00 | 6095 |  |  | 0
2020-09-10 23:00 | 6096 |  |  | 0
2020-09-11 | 6097 |  |  | 0
2020-09-11 01:00 | 6098 |  |  | 0
2020-09-11 02:00 | 6099 |  |  | 0
2020-09-11 03:00 | 6100 |  |  | 0
2020-09-11 04:00 | 6101 |  |  | 0
2020-09-11 05:00 | 6102 |  |  | 0
2020-09-11 06:00 | 6103 |  |  | 0
2020-09-11 07:00 | 6104 |  |  | 0.028118
2020-09-11 08:00 | 6105 |  |  | 0.090969
2020-09-11 09:00 | 6106 |  |  | 0.082699
2020-09-11 10:00 | 6107 |  |  | 0.099239
2020-09-11 11:00 | 6108 |  |  | 0.14886
2020-09-11 12:00 | 6109 |  |  | 0.13066
2020-09-11 13:00 | 6110 |  |  | 0.17863
2020-09-11 14:00 | 6111 |  |  | 0.19352
2020-09-11 15:00 | 6112 |  |  | 0.20509
2020-09-11 16:00 | 6113 |  |  | 0.14059
2020-09-11 17:00 | 6114 |  |  | 0.084353
2020-09-11 18:00 | 6115 |  |  | 0
2020-09-11 19:00 | 6116 |  |  | 0
2020-09-11 20:00 | 6117 |  |  | 0
2020-09-11 21:00 | 6118 |  |  | 0
2020-09-11 22:00 | 6119 |  |  | 0
2020-09-11 23:00 | 6120 |  |  | 0
2020-09-12 | 6121 |  |  | 0
2020-09-12 01:00 | 6122 |  |  | 0
2020-09-12 02:00 | 6123 |  |  | 0
2020-09-12 03:00 | 6124 |  |  | 0
2020-09-12 04:00 | 6125 |  |  | 0
2020-09-12 05:00 | 6126 |  |  | 0
2020-09-12 06:00 | 6127 |  |  | 0
2020-09-12 07:00 | 6128 |  |  | 0.061197
2020-09-12 08:00 | 6129 |  |  | 0.22163
2020-09-12 09:00 | 6130 |  |  | 0.40357
2020-09-12 10:00 | 6131 |  |  | 0.55739
2020-09-12 11:00 | 6132 |  |  | 0.65332
2020-09-12 12:00 | 6133 |  |  | 0.70294
2020-09-12 13:00 | 6134 |  |  | 0.71121
2020-09-12 14:00 | 6135 |  |  | 0.65994
2020-09-12 15:00 | 6136 |  |  | 0.54582
2020-09-12 16:00 | 6137 |  |  | 0.39199
2020-09-12 17:00 | 6138 |  |  | 0.16871
2020-09-12 18:00 | 6139 |  |  | 0.001654
2020-09-12 19:00 | 6140 |  |  | 0
2020-09-12 20:00 | 6141 |  |  | 0
2020-09-12 21:00 | 6142 |  |  | 0
2020-09-12 22:00 | 6143 |  |  | 0
2020-09-12 23:00 | 6144 |  |  | 0
2020-09-13 | 6145 |  |  | 0
2020-09-13 01:00 | 6146 |  |  | 0
2020-09-13 02:00 | 6147 |  |  | 0
2020-09-13 03:00 | 6148 |  |  | 0
2020-09-13 04:00 | 6149 |  |  | 0
2020-09-13 05:00 | 6150 |  |  | 0
2020-09-13 06:00 | 6151 |  |  | 0
2020-09-13 07:00 | 6152 |  |  | 0.062851
2020-09-13 08:00 | 6153 |  |  | 0.2084
2020-09-13 09:00 | 6154 |  |  | 0.38372
2020-09-13 10:00 | 6155 |  |  | 0.54085
2020-09-13 11:00 | 6156 |  |  | 0.61032
2020-09-13 12:00 | 6157 |  |  | 0.69798
2020-09-13 13:00 | 6158 |  |  | 0.68971
2020-09-13 14:00 | 6159 |  |  | 0.62355
2020-09-13 15:00 | 6160 |  |  | 0.36718
2020-09-13 16:00 | 6161 |  |  | 0.11909
2020-09-13 17:00 | 6162 |  |  | 0.079391
2020-09-13 18:00 | 6163 |  |  | 0
2020-09-13 19:00 | 6164 |  |  | 0
2020-09-13 20:00 | 6165 |  |  | 0
2020-09-13 21:00 | 6166 |  |  | 0
2020-09-13 22:00 | 6167 |  |  | 0
2020-09-13 23:00 | 6168 |  |  | 0
2020-09-14 | 6169 |  |  | 0
2020-09-14 01:00 | 6170 |  |  | 0
2020-09-14 02:00 | 6171 |  |  | 0
2020-09-14 03:00 | 6172 |  |  | 0
2020-09-14 04:00 | 6173 |  |  | 0
2020-09-14 05:00 | 6174 |  |  | 0
2020-09-14 06:00 | 6175 |  |  | 0
2020-09-14 07:00 | 6176 |  |  | 0.054582
2020-09-14 08:00 | 6177 |  |  | 0.17036
2020-09-14 09:00 | 6178 |  |  | 0.35561
2020-09-14 10:00 | 6179 |  |  | 0.53093
2020-09-14 11:00 | 6180 |  |  | 0.53093
2020-09-14 12:00 | 6181 |  |  | 0.68475
2020-09-14 13:00 | 6182 |  |  | 0.39199
2020-09-14 14:00 | 6183 |  |  | 0.51935
2020-09-14 15:00 | 6184 |  |  | 0.23156
2020-09-14 16:00 | 6185 |  |  | 0.29937
2020-09-14 17:00 | 6186 |  |  | 0.13563
2020-09-14 18:00 | 6187 |  |  | 0.004962
2020-09-14 19:00 | 6188 |  |  | 0
2020-09-14 20:00 | 6189 |  |  | 0
2020-09-14 21:00 | 6190 |  |  | 0
2020-09-14 22:00 | 6191 |  |  | 0
2020-09-14 23:00 | 6192 |  |  | 0
2020-09-15 | 6193 |  |  | 0
2020-09-15 01:00 | 6194 |  |  | 0
2020-09-15 02:00 | 6195 |  |  | 0
2020-09-15 03:00 | 6196 |  |  | 0
2020-09-15 04:00 | 6197 |  |  | 0
2020-09-15 05:00 | 6198 |  |  | 0
2020-09-15 06:00 | 6199 |  |  | 0.0066159
2020-09-15 07:00 | 6200 |  |  | 0.059543
2020-09-15 08:00 | 6201 |  |  | 0.2084
2020-09-15 09:00 | 6202 |  |  | 0.37215
2020-09-15 10:00 | 6203 |  |  | 0.51935
2020-09-15 11:00 | 6204 |  |  | 0.6037
2020-09-15 12:00 | 6205 |  |  | 0.67648
2020-09-15 13:00 | 6206 |  |  | 0.63182
2020-09-15 14:00 | 6207 |  |  | 0.60867
2020-09-15 15:00 | 6208 |  |  | 0.52266
2020-09-15 16:00 | 6209 |  |  | 0.34238
2020-09-15 17:00 | 6210 |  |  | 0.1257
2020-09-15 18:00 | 6211 |  |  | 0
2020-09-15 19:00 | 6212 |  |  | 0
2020-09-15 20:00 | 6213 |  |  | 0
2020-09-15 21:00 | 6214 |  |  | 0
2020-09-15 22:00 | 6215 |  |  | 0
2020-09-15 23:00 | 6216 |  |  | 0
2020-09-16 | 6217 |  |  | 0
2020-09-16 01:00 | 6218 |  |  | 0
2020-09-16 02:00 | 6219 |  |  | 0
2020-09-16 03:00 | 6220 |  |  | 0
2020-09-16 04:00 | 6221 |  |  | 0
2020-09-16 05:00 | 6222 |  |  | 0
2020-09-16 06:00 | 6223 |  |  | 0
2020-09-16 07:00 | 6224 |  |  | 0.039696
2020-09-16 08:00 | 6225 |  |  | 0.21502
2020-09-16 09:00 | 6226 |  |  | 0.34403
2020-09-16 10:00 | 6227 |  |  | 0.4565
2020-09-16 11:00 | 6228 |  |  | 0.61197
2020-09-16 12:00 | 6229 |  |  | 0.67979
2020-09-16 13:00 | 6230 |  |  | 0.7046
2020-09-16 14:00 | 6231 |  |  | 0.39696
2020-09-16 15:00 | 6232 |  |  | 0.21171
2020-09-16 16:00 | 6233 |  |  | 0.11578
2020-09-16 17:00 | 6234 |  |  | 0.014886
2020-09-16 18:00 | 6235 |  |  | 0
2020-09-16 19:00 | 6236 |  |  | 0
2020-09-16 20:00 | 6237 |  |  | 0
2020-09-16 21:00 | 6238 |  |  | 0
2020-09-16 22:00 | 6239 |  |  | 0
2020-09-16 23:00 | 6240 |  |  | 0
2020-09-17 | 6241 |  |  | 0
2020-09-17 01:00 | 6242 |  |  | 0
2020-09-17 02:00 | 6243 |  |  | 0
2020-09-17 03:00 | 6244 |  |  | 0
2020-09-17 04:00 | 6245 |  |  | 0
2020-09-17 05:00 | 6246 |  |  | 0
2020-09-17 06:00 | 6247 |  |  | 0
2020-09-17 07:00 | 6248 |  |  | 0.052928
2020-09-17 08:00 | 6249 |  |  | 0.21667
2020-09-17 09:00 | 6250 |  |  | 0.40026
2020-09-17 10:00 | 6251 |  |  | 0.55243
2020-09-17 11:00 | 6252 |  |  | 0.64175
2020-09-17 12:00 | 6253 |  |  | 0.6864
2020-09-17 13:00 | 6254 |  |  | 0.66986
2020-09-17 14:00 | 6255 |  |  | 0.59213
2020-09-17 15:00 | 6256 |  |  | 0.51935
2020-09-17 16:00 | 6257 |  |  | 0.34899
2020-09-17 17:00 | 6258 |  |  | 0.10089
2020-09-17 18:00 | 6259 |  |  | 0
2020-09-17 19:00 | 6260 |  |  | 0
2020-09-17 20:00 | 6261 |  |  | 0
2020-09-17 21:00 | 6262 |  |  | 0
2020-09-17 22:00 | 6263 |  |  | 0
2020-09-17 23:00 | 6264 |  |  | 0
2020-09-18 | 6265 |  |  | 0
2020-09-18 01:00 | 6266 |  |  | 0
2020-09-18 02:00 | 6267 |  |  | 0
2020-09-18 03:00 | 6268 |  |  | 0
2020-09-18 04:00 | 6269 |  |  | 0
2020-09-18 05:00 | 6270 |  |  | 0
2020-09-18 06:00 | 6271 |  |  | 0
2020-09-18 07:00 | 6272 |  |  | 0.062851
2020-09-18 08:00 | 6273 |  |  | 0.19848
2020-09-18 09:00 | 6274 |  |  | 0.36222
2020-09-18 10:00 | 6275 |  |  | 0.5177
2020-09-18 11:00 | 6276 |  |  | 0.58386
2020-09-18 12:00 | 6277 |  |  | 0.66821
2020-09-18 13:00 | 6278 |  |  | 0.65498
2020-09-18 14:00 | 6279 |  |  | 0.5789
2020-09-18 15:00 | 6280 |  |  | 0.47635
2020-09-18 16:00 | 6281 |  |  | 0.29441
2020-09-18 17:00 | 6282 |  |  | 0.076083
2020-09-18 18:00 | 6283 |  |  | 0
2020-09-18 19:00 | 6284 |  |  | 0
2020-09-18 20:00 | 6285 |  |  | 0
2020-09-18 21:00 | 6286 |  |  | 0
2020-09-18 22:00 | 6287 |  |  | 0
2020-09-18 23:00 | 6288 |  |  | 0
2020-09-19 | 6289 |  |  | 0
2020-09-19 01:00 | 6290 |  |  | 0
2020-09-19 02:00 | 6291 |  |  | 0
2020-09-19 03:00 | 6292 |  |  | 0
2020-09-19 04:00 | 6293 |  |  | 0
2020-09-19 05:00 | 6294 |  |  | 0
2020-09-19 06:00 | 6295 |  |  | 0
2020-09-19 07:00 | 6296 |  |  | 0
2020-09-19 08:00 | 6297 |  |  | 0.021502
2020-09-19 09:00 | 6298 |  |  | 0.01654
2020-09-19 10:00 | 6299 |  |  | 0.092623
2020-09-19 11:00 | 6300 |  |  | 0.1472
2020-09-19 12:00 | 6301 |  |  | 0.44988
2020-09-19 13:00 | 6302 |  |  | 0.31757
2020-09-19 14:00 | 6303 |  |  | 0.24314
2020-09-19 15:00 | 6304 |  |  | 0.40523
2020-09-19 16:00 | 6305 |  |  | 0.094277
2020-09-19 17:00 | 6306 |  |  | 0.079391
2020-09-19 18:00 | 6307 |  |  | 0
2020-09-19 19:00 | 6308 |  |  | 0
2020-09-19 20:00 | 6309 |  |  | 0
2020-09-19 21:00 | 6310 |  |  | 0
2020-09-19 22:00 | 6311 |  |  | 0
2020-09-19 23:00 | 6312 |  |  | 0
2020-09-20 | 6313 |  |  | 0
2020-09-20 01:00 | 6314 |  |  | 0
2020-09-20 02:00 | 6315 |  |  | 0
2020-09-20 03:00 | 6316 |  |  | 0
2020-09-20 04:00 | 6317 |  |  | 0
2020-09-20 05:00 | 6318 |  |  | 0
2020-09-20 06:00 | 6319 |  |  | 0
2020-09-20 07:00 | 6320 |  |  | 0.011578
2020-09-20 08:00 | 6321 |  |  | 0.18194
2020-09-20 09:00 | 6322 |  |  | 0.18028
2020-09-20 10:00 | 6323 |  |  | 0.15217
2020-09-20 11:00 | 6324 |  |  | 0.14886
2020-09-20 12:00 | 6325 |  |  | 0.40523
2020-09-20 13:00 | 6326 |  |  | 0.478
2020-09-20 14:00 | 6327 |  |  | 0.56897
2020-09-20 15:00 | 6328 |  |  | 0.20013
2020-09-20 16:00 | 6329 |  |  | 0.019848
2020-09-20 17:00 | 6330 |  |  | 0
2020-09-20 18:00 | 6331 |  |  | 0
2020-09-20 19:00 | 6332 |  |  | 0
2020-09-20 20:00 | 6333 |  |  | 0
2020-09-20 21:00 | 6334 |  |  | 0
2020-09-20 22:00 | 6335 |  |  | 0
2020-09-20 23:00 | 6336 |  |  | 0
2020-09-21 | 6337 |  |  | 0
2020-09-21 01:00 | 6338 |  |  | 0
2020-09-21 02:00 | 6339 |  |  | 0
2020-09-21 03:00 | 6340 |  |  | 0
2020-09-21 04:00 | 6341 |  |  | 0
2020-09-21 05:00 | 6342 |  |  | 0
2020-09-21 06:00 | 6343 |  |  | 0
2020-09-21 07:00 | 6344 |  |  | 0.026464
2020-09-21 08:00 | 6345 |  |  | 0.19517
2020-09-21 09:00 | 6346 |  |  | 0.19352
2020-09-21 10:00 | 6347 |  |  | 0.30433
2020-09-21 11:00 | 6348 |  |  | 0.56236
2020-09-21 12:00 | 6349 |  |  | 0.4135
2020-09-21 13:00 | 6350 |  |  | 0.27787
2020-09-21 14:00 | 6351 |  |  | 0.28945
2020-09-21 15:00 | 6352 |  |  | 0.12239
2020-09-21 16:00 | 6353 |  |  | 0.061197
2020-09-21 17:00 | 6354 |  |  | 0.0099239
2020-09-21 18:00 | 6355 |  |  | 0
2020-09-21 19:00 | 6356 |  |  | 0
2020-09-21 20:00 | 6357 |  |  | 0
2020-09-21 21:00 | 6358 |  |  | 0
2020-09-21 22:00 | 6359 |  |  | 0
2020-09-21 23:00 | 6360 |  |  | 0
2020-09-22 | 6361 |  |  | 0
2020-09-22 01:00 | 6362 |  |  | 0
2020-09-22 02:00 | 6363 |  |  | 0
2020-09-22 03:00 | 6364 |  |  | 0
2020-09-22 04:00 | 6365 |  |  | 0
2020-09-22 05:00 | 6366 |  |  | 0
2020-09-22 06:00 | 6367 |  |  | 0
2020-09-22 07:00 | 6368 |  |  | 0.044658
2020-09-22 08:00 | 6369 |  |  | 0.12736
2020-09-22 09:00 | 6370 |  |  | 0.10255
2020-09-22 10:00 | 6371 |  |  | 0.11247
2020-09-22 11:00 | 6372 |  |  | 0.20013
2020-09-22 12:00 | 6373 |  |  | 0.31095
2020-09-22 13:00 | 6374 |  |  | 0.32914
2020-09-22 14:00 | 6375 |  |  | 0.097585
2020-09-22 15:00 | 6376 |  |  | 0.023156
2020-09-22 16:00 | 6377 |  |  | 0
2020-09-22 17:00 | 6378 |  |  | 0
2020-09-22 18:00 | 6379 |  |  | 0
2020-09-22 19:00 | 6380 |  |  | 0
2020-09-22 20:00 | 6381 |  |  | 0
2020-09-22 21:00 | 6382 |  |  | 0
2020-09-22 22:00 | 6383 |  |  | 0
2020-09-22 23:00 | 6384 |  |  | 0
2020-09-23 | 6385 |  |  | 0
2020-09-23 01:00 | 6386 |  |  | 0
2020-09-23 02:00 | 6387 |  |  | 0
2020-09-23 03:00 | 6388 |  |  | 0
2020-09-23 04:00 | 6389 |  |  | 0
2020-09-23 05:00 | 6390 |  |  | 0
2020-09-23 06:00 | 6391 |  |  | 0
2020-09-23 07:00 | 6392 |  |  | 0.03308
2020-09-23 08:00 | 6393 |  |  | 0.18855
2020-09-23 09:00 | 6394 |  |  | 0.33411
2020-09-23 10:00 | 6395 |  |  | 0.25471
2020-09-23 11:00 | 6396 |  |  | 0.13232
2020-09-23 12:00 | 6397 |  |  | 0.24148
2020-09-23 13:00 | 6398 |  |  | 0.54912
2020-09-23 14:00 | 6399 |  |  | 0.54416
2020-09-23 15:00 | 6400 |  |  | 0.23652
2020-09-23 16:00 | 6401 |  |  | 0.11909
2020-09-23 17:00 | 6402 |  |  | 0.077737
2020-09-23 18:00 | 6403 |  |  | 0
2020-09-23 19:00 | 6404 |  |  | 0
2020-09-23 20:00 | 6405 |  |  | 0
2020-09-23 21:00 | 6406 |  |  | 0
2020-09-23 22:00 | 6407 |  |  | 0
2020-09-23 23:00 | 6408 |  |  | 0
2020-09-24 | 6409 |  |  | 0
2020-09-24 01:00 | 6410 |  |  | 0
2020-09-24 02:00 | 6411 |  |  | 0
2020-09-24 03:00 | 6412 |  |  | 0
2020-09-24 04:00 | 6413 |  |  | 0
2020-09-24 05:00 | 6414 |  |  | 0
2020-09-24 06:00 | 6415 |  |  | 0
2020-09-24 07:00 | 6416 |  |  | 0.013232
2020-09-24 08:00 | 6417 |  |  | 0.086007
2020-09-24 09:00 | 6418 |  |  | 0.23652
2020-09-24 10:00 | 6419 |  |  | 0.26133
2020-09-24 11:00 | 6420 |  |  | 0.19352
2020-09-24 12:00 | 6421 |  |  | 0.56236
2020-09-24 13:00 | 6422 |  |  | 0.3093
2020-09-24 14:00 | 6423 |  |  | 0.28614
2020-09-24 15:00 | 6424 |  |  | 0.15382
2020-09-24 16:00 | 6425 |  |  | 0.082699
2020-09-24 17:00 | 6426 |  |  | 0
2020-09-24 18:00 | 6427 |  |  | 0
2020-09-24 19:00 | 6428 |  |  | 0
2020-09-24 20:00 | 6429 |  |  | 0
2020-09-24 21:00 | 6430 |  |  | 0
2020-09-24 22:00 | 6431 |  |  | 0
2020-09-24 23:00 | 6432 |  |  | 0
2020-09-25 | 6433 |  |  | 0
2020-09-25 01:00 | 6434 |  |  | 0
2020-09-25 02:00 | 6435 |  |  | 0
2020-09-25 03:00 | 6436 |  |  | 0
2020-09-25 04:00 | 6437 |  |  | 0
2020-09-25 05:00 | 6438 |  |  | 0
2020-09-25 06:00 | 6439 |  |  | 0.0066159
2020-09-25 07:00 | 6440 |  |  | 0.018194
2020-09-25 08:00 | 6441 |  |  | 0.039696
2020-09-25 09:00 | 6442 |  |  | 0.15878
2020-09-25 10:00 | 6443 |  |  | 0.59709
2020-09-25 11:00 | 6444 |  |  | 0.3738
2020-09-25 12:00 | 6445 |  |  | 0.61197
2020-09-25 13:00 | 6446 |  |  | 0.61363
2020-09-25 14:00 | 6447 |  |  | 0.15878
2020-09-25 15:00 | 6448 |  |  | 0.1472
2020-09-25 16:00 | 6449 |  |  | 0.10586
2020-09-25 17:00 | 6450 |  |  | 0.069467
2020-09-25 18:00 | 6451 |  |  | 0
2020-09-25 19:00 | 6452 |  |  | 0
2020-09-25 20:00 | 6453 |  |  | 0
2020-09-25 21:00 | 6454 |  |  | 0
2020-09-25 22:00 | 6455 |  |  | 0
2020-09-25 23:00 | 6456 |  |  | 0
2020-09-26 | 6457 |  |  | 0
2020-09-26 01:00 | 6458 |  |  | 0
2020-09-26 02:00 | 6459 |  |  | 0
2020-09-26 03:00 | 6460 |  |  | 0
2020-09-26 04:00 | 6461 |  |  | 0
2020-09-26 05:00 | 6462 |  |  | 0
2020-09-26 06:00 | 6463 |  |  | 0
2020-09-26 07:00 | 6464 |  |  | 0.034734
2020-09-26 08:00 | 6465 |  |  | 0.23652
2020-09-26 09:00 | 6466 |  |  | 0.46808
2020-09-26 10:00 | 6467 |  |  | 0.63017
2020-09-26 11:00 | 6468 |  |  | 0.7261
2020-09-26 12:00 | 6469 |  |  | 0.81045
2020-09-26 13:00 | 6470 |  |  | 0.80384
2020-09-26 14:00 | 6471 |  |  | 0.71948
2020-09-26 15:00 | 6472 |  |  | 0.59709
2020-09-26 16:00 | 6473 |  |  | 0.36718
2020-09-26 17:00 | 6474 |  |  | 0.11082
2020-09-26 18:00 | 6475 |  |  | 0
2020-09-26 19:00 | 6476 |  |  | 0
2020-09-26 20:00 | 6477 |  |  | 0
2020-09-26 21:00 | 6478 |  |  | 0
2020-09-26 22:00 | 6479 |  |  | 0
2020-09-26 23:00 | 6480 |  |  | 0
2020-09-27 | 6481 |  |  | 0
2020-09-27 01:00 | 6482 |  |  | 0
2020-09-27 02:00 | 6483 |  |  | 0
2020-09-27 03:00 | 6484 |  |  | 0
2020-09-27 04:00 | 6485 |  |  | 0
2020-09-27 05:00 | 6486 |  |  | 0
2020-09-27 06:00 | 6487 |  |  | 0
2020-09-27 07:00 | 6488 |  |  | 0.067813
2020-09-27 08:00 | 6489 |  |  | 0.24148
2020-09-27 09:00 | 6490 |  |  | 0.41184
2020-09-27 10:00 | 6491 |  |  | 0.59709
2020-09-27 11:00 | 6492 |  |  | 0.69633
2020-09-27 12:00 | 6493 |  |  | 0.75256
2020-09-27 13:00 | 6494 |  |  | 0.74595
2020-09-27 14:00 | 6495 |  |  | 0.70129
2020-09-27 15:00 | 6496 |  |  | 0.48627
2020-09-27 16:00 | 6497 |  |  | 0.2696
2020-09-27 17:00 | 6498 |  |  | 0.013232
2020-09-27 18:00 | 6499 |  |  | 0
2020-09-27 19:00 | 6500 |  |  | 0
2020-09-27 20:00 | 6501 |  |  | 0
2020-09-27 21:00 | 6502 |  |  | 0
2020-09-27 22:00 | 6503 |  |  | 0
2020-09-27 23:00 | 6504 |  |  | 0
2020-09-28 | 6505 |  |  | 0
2020-09-28 01:00 | 6506 |  |  | 0
2020-09-28 02:00 | 6507 |  |  | 0
2020-09-28 03:00 | 6508 |  |  | 0
2020-09-28 04:00 | 6509 |  |  | 0
2020-09-28 05:00 | 6510 |  |  | 0
2020-09-28 06:00 | 6511 |  |  | 0
2020-09-28 07:00 | 6512 |  |  | 0.038042
2020-09-28 08:00 | 6513 |  |  | 0.22494
2020-09-28 09:00 | 6514 |  |  | 0.435
2020-09-28 10:00 | 6515 |  |  | 0.58055
2020-09-28 11:00 | 6516 |  |  | 0.69798
2020-09-28 12:00 | 6517 |  |  | 0.71121
2020-09-28 13:00 | 6518 |  |  | 0.70294
2020-09-28 14:00 | 6519 |  |  | 0.67317
2020-09-28 15:00 | 6520 |  |  | 0.53755
2020-09-28 16:00 | 6521 |  |  | 0.31426
2020-09-28 17:00 | 6522 |  |  | 0.077737
2020-09-28 18:00 | 6523 |  |  | 0
2020-09-28 19:00 | 6524 |  |  | 0
2020-09-28 20:00 | 6525 |  |  | 0
2020-09-28 21:00 | 6526 |  |  | 0
2020-09-28 22:00 | 6527 |  |  | 0
2020-09-28 23:00 | 6528 |  |  | 0
2020-09-29 | 6529 |  |  | 0
2020-09-29 01:00 | 6530 |  |  | 0
2020-09-29 02:00 | 6531 |  |  | 0
2020-09-29 03:00 | 6532 |  |  | 0
2020-09-29 04:00 | 6533 |  |  | 0
2020-09-29 05:00 | 6534 |  |  | 0
2020-09-29 06:00 | 6535 |  |  | 0
2020-09-29 07:00 | 6536 |  |  | 0.034734
2020-09-29 08:00 | 6537 |  |  | 0.21667
2020-09-29 09:00 | 6538 |  |  | 0.39696
2020-09-29 10:00 | 6539 |  |  | 0.55574
2020-09-29 11:00 | 6540 |  |  | 0.63678
2020-09-29 12:00 | 6541 |  |  | 0.61363
2020-09-29 13:00 | 6542 |  |  | 0.48131
2020-09-29 14:00 | 6543 |  |  | 0.42838
2020-09-29 15:00 | 6544 |  |  | 0.44658
2020-09-29 16:00 | 6545 |  |  | 0.19517
2020-09-29 17:00 | 6546 |  |  | 0.0066159
2020-09-29 18:00 | 6547 |  |  | 0
2020-09-29 19:00 | 6548 |  |  | 0
2020-09-29 20:00 | 6549 |  |  | 0
2020-09-29 21:00 | 6550 |  |  | 0
2020-09-29 22:00 | 6551 |  |  | 0
2020-09-29 23:00 | 6552 |  |  | 0
2020-09-30 | 6553 |  |  | 0
2020-09-30 01:00 | 6554 |  |  | 0
2020-09-30 02:00 | 6555 |  |  | 0
2020-09-30 03:00 | 6556 |  |  | 0
2020-09-30 04:00 | 6557 |  |  | 0
2020-09-30 05:00 | 6558 |  |  | 0
2020-09-30 06:00 | 6559 |  |  | 0
2020-09-30 07:00 | 6560 |  |  | 0.021502
2020-09-30 08:00 | 6561 |  |  | 0.19517
2020-09-30 09:00 | 6562 |  |  | 0.38042
2020-09-30 10:00 | 6563 |  |  | 0.54251
2020-09-30 11:00 | 6564 |  |  | 0.61859
2020-09-30 12:00 | 6565 |  |  | 0.6649
2020-09-30 13:00 | 6566 |  |  | 0.68475
2020-09-30 14:00 | 6567 |  |  | 0.60701
2020-09-30 15:00 | 6568 |  |  | 0.46808
2020-09-30 16:00 | 6569 |  |  | 0.23983
2020-09-30 17:00 | 6570 |  |  | 0.062851
2020-09-30 18:00 | 6571 |  |  | 0
2020-09-30 19:00 | 6572 |  |  | 0
2020-09-30 20:00 | 6573 |  |  | 0
2020-09-30 21:00 | 6574 |  |  | 0
2020-09-30 22:00 | 6575 |  |  | 0
2020-09-30 23:00 | 6576 |  |  | 0
2020-10-01 | 6577 |  |  | 0
2020-10-01 01:00 | 6578 |  |  | 0
2020-10-01 02:00 | 6579 |  |  | 0
2020-10-01 03:00 | 6580 |  |  | 0
2020-10-01 04:00 | 6581 |  |  | 0
2020-10-01 05:00 | 6582 |  |  | 0
2020-10-01 06:00 | 6583 |  |  | 0
2020-10-01 07:00 | 6584 |  |  | 0.062851
2020-10-01 08:00 | 6585 |  |  | 0.095931
2020-10-01 09:00 | 6586 |  |  | 0.24314
2020-10-01 10:00 | 6587 |  |  | 0.47635
2020-10-01 11:00 | 6588 |  |  | 0.58386
2020-10-01 12:00 | 6589 |  |  | 0.29937
2020-10-01 13:00 | 6590 |  |  | 0.28118
2020-10-01 14:00 | 6591 |  |  | 0.24479
2020-10-01 15:00 | 6592 |  |  | 0.1257
2020-10-01 16:00 | 6593 |  |  | 0.084353
2020-10-01 17:00 | 6594 |  |  | 0.004962
2020-10-01 18:00 | 6595 |  |  | 0
2020-10-01 19:00 | 6596 |  |  | 0
2020-10-01 20:00 | 6597 |  |  | 0
2020-10-01 21:00 | 6598 |  |  | 0
2020-10-01 22:00 | 6599 |  |  | 0
2020-10-01 23:00 | 6600 |  |  | 0
2020-10-02 | 6601 |  |  | 0
2020-10-02 01:00 | 6602 |  |  | 0
2020-10-02 02:00 | 6603 |  |  | 0
2020-10-02 03:00 | 6604 |  |  | 0
2020-10-02 04:00 | 6605 |  |  | 0
2020-10-02 05:00 | 6606 |  |  | 0
2020-10-02 06:00 | 6607 |  |  | 0
2020-10-02 07:00 | 6608 |  |  | 0
2020-10-02 08:00 | 6609 |  |  | 0
2020-10-02 09:00 | 6610 |  |  | 0.0066159
2020-10-02 10:00 | 6611 |  |  | 0.018194
2020-10-02 11:00 | 6612 |  |  | 0.029772
2020-10-02 12:00 | 6613 |  |  | 0.021502
2020-10-02 13:00 | 6614 |  |  | 0.003308
2020-10-02 14:00 | 6615 |  |  | 0
2020-10-02 15:00 | 6616 |  |  | 0
2020-10-02 16:00 | 6617 |  |  | 0
2020-10-02 17:00 | 6618 |  |  | 0
2020-10-02 18:00 | 6619 |  |  | 0
2020-10-02 19:00 | 6620 |  |  | 0
2020-10-02 20:00 | 6621 |  |  | 0
2020-10-02 21:00 | 6622 |  |  | 0
2020-10-02 22:00 | 6623 |  |  | 0
2020-10-02 23:00 | 6624 |  |  | 0
2020-10-03 | 6625 |  |  | 0
2020-10-03 01:00 | 6626 |  |  | 0
2020-10-03 02:00 | 6627 |  |  | 0
2020-10-03 03:00 | 6628 |  |  | 0
2020-10-03 04:00 | 6629 |  |  | 0
2020-10-03 05:00 | 6630 |  |  | 0
2020-10-03 06:00 | 6631 |  |  | 0
2020-10-03 07:00 | 6632 |  |  | 0.0066159
2020-10-03 08:00 | 6633 |  |  | 0.1869
2020-10-03 09:00 | 6634 |  |  | 0.42673
2020-10-03 10:00 | 6635 |  |  | 0.55078
2020-10-03 11:00 | 6636 |  |  | 0.70129
2020-10-03 12:00 | 6637 |  |  | 0.71287
2020-10-03 13:00 | 6638 |  |  | 0.70294
2020-10-03 14:00 | 6639 |  |  | 0.6219
2020-10-03 15:00 | 6640 |  |  | 0.17698
2020-10-03 16:00 | 6641 |  |  | 0.092623
2020-10-03 17:00 | 6642 |  |  | 0.0066159
2020-10-03 18:00 | 6643 |  |  | 0
2020-10-03 19:00 | 6644 |  |  | 0
2020-10-03 20:00 | 6645 |  |  | 0
2020-10-03 21:00 | 6646 |  |  | 0
2020-10-03 22:00 | 6647 |  |  | 0
2020-10-03 23:00 | 6648 |  |  | 0
2020-10-04 | 6649 |  |  | 0
2020-10-04 01:00 | 6650 |  |  | 0
2020-10-04 02:00 | 6651 |  |  | 0
2020-10-04 03:00 | 6652 |  |  | 0
2020-10-04 04:00 | 6653 |  |  | 0
2020-10-04 05:00 | 6654 |  |  | 0
2020-10-04 06:00 | 6655 |  |  | 0
2020-10-04 07:00 | 6656 |  |  | 0.034734
2020-10-04 08:00 | 6657 |  |  | 0.21667
2020-10-04 09:00 | 6658 |  |  | 0.42838
2020-10-04 10:00 | 6659 |  |  | 0.32087
2020-10-04 11:00 | 6660 |  |  | 0.49454
2020-10-04 12:00 | 6661 |  |  | 0.55078
2020-10-04 13:00 | 6662 |  |  | 0.55078
2020-10-04 14:00 | 6663 |  |  | 0.1257
2020-10-04 15:00 | 6664 |  |  | 0.059543
2020-10-04 16:00 | 6665 |  |  | 0.001654
2020-10-04 17:00 | 6666 |  |  | 0
2020-10-04 18:00 | 6667 |  |  | 0
2020-10-04 19:00 | 6668 |  |  | 0
2020-10-04 20:00 | 6669 |  |  | 0
2020-10-04 21:00 | 6670 |  |  | 0
2020-10-04 22:00 | 6671 |  |  | 0
2020-10-04 23:00 | 6672 |  |  | 0
2020-10-05 | 6673 |  |  | 0
2020-10-05 01:00 | 6674 |  |  | 0
2020-10-05 02:00 | 6675 |  |  | 0
2020-10-05 03:00 | 6676 |  |  | 0
2020-10-05 04:00 | 6677 |  |  | 0
2020-10-05 05:00 | 6678 |  |  | 0
2020-10-05 06:00 | 6679 |  |  | 0
2020-10-05 07:00 | 6680 |  |  | 0.014886
2020-10-05 08:00 | 6681 |  |  | 0.014886
2020-10-05 09:00 | 6682 |  |  | 0.039696
2020-10-05 10:00 | 6683 |  |  | 0.11247
2020-10-05 11:00 | 6684 |  |  | 0.13066
2020-10-05 12:00 | 6685 |  |  | 0.13728
2020-10-05 13:00 | 6686 |  |  | 0.17036
2020-10-05 14:00 | 6687 |  |  | 0.41515
2020-10-05 15:00 | 6688 |  |  | 0.14224
2020-10-05 16:00 | 6689 |  |  | 0.12901
2020-10-05 17:00 | 6690 |  |  | 0.028118
2020-10-05 18:00 | 6691 |  |  | 0
2020-10-05 19:00 | 6692 |  |  | 0
2020-10-05 20:00 | 6693 |  |  | 0
2020-10-05 21:00 | 6694 |  |  | 0
2020-10-05 22:00 | 6695 |  |  | 0
2020-10-05 23:00 | 6696 |  |  | 0
2020-10-06 | 6697 |  |  | 0
2020-10-06 01:00 | 6698 |  |  | 0
2020-10-06 02:00 | 6699 |  |  | 0
2020-10-06 03:00 | 6700 |  |  | 0
2020-10-06 04:00 | 6701 |  |  | 0
2020-10-06 05:00 | 6702 |  |  | 0
2020-10-06 06:00 | 6703 |  |  | 0
2020-10-06 07:00 | 6704 |  |  | 0.039696
2020-10-06 08:00 | 6705 |  |  | 0.17532
2020-10-06 09:00 | 6706 |  |  | 0.27125
2020-10-06 10:00 | 6707 |  |  | 0.17201
2020-10-06 11:00 | 6708 |  |  | 0.21336
2020-10-06 12:00 | 6709 |  |  | 0.51439
2020-10-06 13:00 | 6710 |  |  | 0.59709
2020-10-06 14:00 | 6711 |  |  | 0.31922
2020-10-06 15:00 | 6712 |  |  | 0.27622
2020-10-06 16:00 | 6713 |  |  | 0.094277
2020-10-06 17:00 | 6714 |  |  | 0.004962
2020-10-06 18:00 | 6715 |  |  | 0
2020-10-06 19:00 | 6716 |  |  | 0
2020-10-06 20:00 | 6717 |  |  | 0
2020-10-06 21:00 | 6718 |  |  | 0
2020-10-06 22:00 | 6719 |  |  | 0
2020-10-06 23:00 | 6720 |  |  | 0
2020-10-07 | 6721 |  |  | 0
2020-10-07 01:00 | 6722 |  |  | 0
2020-10-07 02:00 | 6723 |  |  | 0
2020-10-07 03:00 | 6724 |  |  | 0
2020-10-07 04:00 | 6725 |  |  | 0
2020-10-07 05:00 | 6726 |  |  | 0
2020-10-07 06:00 | 6727 |  |  | 0
2020-10-07 07:00 | 6728 |  |  | 0.026464
2020-10-07 08:00 | 6729 |  |  | 0.17367
2020-10-07 09:00 | 6730 |  |  | 0.33907
2020-10-07 10:00 | 6731 |  |  | 0.38372
2020-10-07 11:00 | 6732 |  |  | 0.65994
2020-10-07 12:00 | 6733 |  |  | 0.7046
2020-10-07 13:00 | 6734 |  |  | 0.59874
2020-10-07 14:00 | 6735 |  |  | 0.56236
2020-10-07 15:00 | 6736 |  |  | 0.38538
2020-10-07 16:00 | 6737 |  |  | 0.20013
2020-10-07 17:00 | 6738 |  |  | 0.036388
2020-10-07 18:00 | 6739 |  |  | 0
2020-10-07 19:00 | 6740 |  |  | 0
2020-10-07 20:00 | 6741 |  |  | 0
2020-10-07 21:00 | 6742 |  |  | 0
2020-10-07 22:00 | 6743 |  |  | 0
2020-10-07 23:00 | 6744 |  |  | 0
2020-10-08 | 6745 |  |  | 0
2020-10-08 01:00 | 6746 |  |  | 0
2020-10-08 02:00 | 6747 |  |  | 0
2020-10-08 03:00 | 6748 |  |  | 0
2020-10-08 04:00 | 6749 |  |  | 0
2020-10-08 05:00 | 6750 |  |  | 0
2020-10-08 06:00 | 6751 |  |  | 0
2020-10-08 07:00 | 6752 |  |  | 0.028118
2020-10-08 08:00 | 6753 |  |  | 0.20675
2020-10-08 09:00 | 6754 |  |  | 0.39696
2020-10-08 10:00 | 6755 |  |  | 0.56401
2020-10-08 11:00 | 6756 |  |  | 0.65167
2020-10-08 12:00 | 6757 |  |  | 0.69137
2020-10-08 13:00 | 6758 |  |  | 0.70129
2020-10-08 14:00 | 6759 |  |  | 0.60701
2020-10-08 15:00 | 6760 |  |  | 0.42838
2020-10-08 16:00 | 6761 |  |  | 0.21006
2020-10-08 17:00 | 6762 |  |  | 0.013232
2020-10-08 18:00 | 6763 |  |  | 0
2020-10-08 19:00 | 6764 |  |  | 0
2020-10-08 20:00 | 6765 |  |  | 0
2020-10-08 21:00 | 6766 |  |  | 0
2020-10-08 22:00 | 6767 |  |  | 0
2020-10-08 23:00 | 6768 |  |  | 0
2020-10-09 | 6769 |  |  | 0
2020-10-09 01:00 | 6770 |  |  | 0
2020-10-09 02:00 | 6771 |  |  | 0
2020-10-09 03:00 | 6772 |  |  | 0
2020-10-09 04:00 | 6773 |  |  | 0
2020-10-09 05:00 | 6774 |  |  | 0
2020-10-09 06:00 | 6775 |  |  | 0
2020-10-09 07:00 | 6776 |  |  | 0.04135
2020-10-09 08:00 | 6777 |  |  | 0.13563
2020-10-09 09:00 | 6778 |  |  | 0.19352
2020-10-09 10:00 | 6779 |  |  | 0.26464
2020-10-09 11:00 | 6780 |  |  | 0.39696
2020-10-09 12:00 | 6781 |  |  | 0.31757
2020-10-09 13:00 | 6782 |  |  | 0.26795
2020-10-09 14:00 | 6783 |  |  | 0.23652
2020-10-09 15:00 | 6784 |  |  | 0.15382
2020-10-09 16:00 | 6785 |  |  | 0.061197
2020-10-09 17:00 | 6786 |  |  | 0
2020-10-09 18:00 | 6787 |  |  | 0
2020-10-09 19:00 | 6788 |  |  | 0
2020-10-09 20:00 | 6789 |  |  | 0
2020-10-09 21:00 | 6790 |  |  | 0
2020-10-09 22:00 | 6791 |  |  | 0
2020-10-09 23:00 | 6792 |  |  | 0
2020-10-10 | 6793 |  |  | 0
2020-10-10 01:00 | 6794 |  |  | 0
2020-10-10 02:00 | 6795 |  |  | 0
2020-10-10 03:00 | 6796 |  |  | 0
2020-10-10 04:00 | 6797 |  |  | 0
2020-10-10 05:00 | 6798 |  |  | 0
2020-10-10 06:00 | 6799 |  |  | 0
2020-10-10 07:00 | 6800 |  |  | 0.034734
2020-10-10 08:00 | 6801 |  |  | 0.15713
2020-10-10 09:00 | 6802 |  |  | 0.34899
2020-10-10 10:00 | 6803 |  |  | 0.36884
2020-10-10 11:00 | 6804 |  |  | 0.52762
2020-10-10 12:00 | 6805 |  |  | 0.56566
2020-10-10 13:00 | 6806 |  |  | 0.66821
2020-10-10 14:00 | 6807 |  |  | 0.43169
2020-10-10 15:00 | 6808 |  |  | 0.10916
2020-10-10 16:00 | 6809 |  |  | 0.036388
2020-10-10 17:00 | 6810 |  |  | 0
2020-10-10 18:00 | 6811 |  |  | 0
2020-10-10 19:00 | 6812 |  |  | 0
2020-10-10 20:00 | 6813 |  |  | 0
2020-10-10 21:00 | 6814 |  |  | 0
2020-10-10 22:00 | 6815 |  |  | 0
2020-10-10 23:00 | 6816 |  |  | 0
2020-10-11 | 6817 |  |  | 0
2020-10-11 01:00 | 6818 |  |  | 0
2020-10-11 02:00 | 6819 |  |  | 0
2020-10-11 03:00 | 6820 |  |  | 0
2020-10-11 04:00 | 6821 |  |  | 0
2020-10-11 05:00 | 6822 |  |  | 0
2020-10-11 06:00 | 6823 |  |  | 0
2020-10-11 07:00 | 6824 |  |  | 0.031426
2020-10-11 08:00 | 6825 |  |  | 0.089315
2020-10-11 09:00 | 6826 |  |  | 0.28945
2020-10-11 10:00 | 6827 |  |  | 0.48627
2020-10-11 11:00 | 6828 |  |  | 0.59543
2020-10-11 12:00 | 6829 |  |  | 0.62521
2020-10-11 13:00 | 6830 |  |  | 0.40688
2020-10-11 14:00 | 6831 |  |  | 0.14224
2020-10-11 15:00 | 6832 |  |  | 0.036388
2020-10-11 16:00 | 6833 |  |  | 0
2020-10-11 17:00 | 6834 |  |  | 0
2020-10-11 18:00 | 6835 |  |  | 0
2020-10-11 19:00 | 6836 |  |  | 0
2020-10-11 20:00 | 6837 |  |  | 0
2020-10-11 21:00 | 6838 |  |  | 0
2020-10-11 22:00 | 6839 |  |  | 0
2020-10-11 23:00 | 6840 |  |  | 0
2020-10-12 | 6841 |  |  | 0
2020-10-12 01:00 | 6842 |  |  | 0
2020-10-12 02:00 | 6843 |  |  | 0
2020-10-12 03:00 | 6844 |  |  | 0
2020-10-12 04:00 | 6845 |  |  | 0
2020-10-12 05:00 | 6846 |  |  | 0
2020-10-12 06:00 | 6847 |  |  | 0
2020-10-12 07:00 | 6848 |  |  | 0.02481
2020-10-12 08:00 | 6849 |  |  | 0.20675
2020-10-12 09:00 | 6850 |  |  | 0.41515
2020-10-12 10:00 | 6851 |  |  | 0.57559
2020-10-12 11:00 | 6852 |  |  | 0.69137
2020-10-12 12:00 | 6853 |  |  | 0.70294
2020-10-12 13:00 | 6854 |  |  | 0.69302
2020-10-12 14:00 | 6855 |  |  | 0.63017
2020-10-12 15:00 | 6856 |  |  | 0.43334
2020-10-12 16:00 | 6857 |  |  | 0.17367
2020-10-12 17:00 | 6858 |  |  | 0.019848
2020-10-12 18:00 | 6859 |  |  | 0
2020-10-12 19:00 | 6860 |  |  | 0
2020-10-12 20:00 | 6861 |  |  | 0
2020-10-12 21:00 | 6862 |  |  | 0
2020-10-12 22:00 | 6863 |  |  | 0
2020-10-12 23:00 | 6864 |  |  | 0
2020-10-13 | 6865 |  |  | 0
2020-10-13 01:00 | 6866 |  |  | 0
2020-10-13 02:00 | 6867 |  |  | 0
2020-10-13 03:00 | 6868 |  |  | 0
2020-10-13 04:00 | 6869 |  |  | 0
2020-10-13 05:00 | 6870 |  |  | 0
2020-10-13 06:00 | 6871 |  |  | 0
2020-10-13 07:00 | 6872 |  |  | 0.019848
2020-10-13 08:00 | 6873 |  |  | 0.19682
2020-10-13 09:00 | 6874 |  |  | 0.38869
2020-10-13 10:00 | 6875 |  |  | 0.56566
2020-10-13 11:00 | 6876 |  |  | 0.67648
2020-10-13 12:00 | 6877 |  |  | 0.70294
2020-10-13 13:00 | 6878 |  |  | 0.63348
2020-10-13 14:00 | 6879 |  |  | 0.6037
2020-10-13 15:00 | 6880 |  |  | 0.35891
2020-10-13 16:00 | 6881 |  |  | 0.064505
2020-10-13 17:00 | 6882 |  |  | 0.014886
2020-10-13 18:00 | 6883 |  |  | 0
2020-10-13 19:00 | 6884 |  |  | 0
2020-10-13 20:00 | 6885 |  |  | 0
2020-10-13 21:00 | 6886 |  |  | 0
2020-10-13 22:00 | 6887 |  |  | 0
2020-10-13 23:00 | 6888 |  |  | 0
2020-10-14 | 6889 |  |  | 0
2020-10-14 01:00 | 6890 |  |  | 0
2020-10-14 02:00 | 6891 |  |  | 0
2020-10-14 03:00 | 6892 |  |  | 0
2020-10-14 04:00 | 6893 |  |  | 0
2020-10-14 05:00 | 6894 |  |  | 0
2020-10-14 06:00 | 6895 |  |  | 0
2020-10-14 07:00 | 6896 |  |  | 0.01654
2020-10-14 08:00 | 6897 |  |  | 0.12736
2020-10-14 09:00 | 6898 |  |  | 0.29772
2020-10-14 10:00 | 6899 |  |  | 0.19021
2020-10-14 11:00 | 6900 |  |  | 0.3738
2020-10-14 12:00 | 6901 |  |  | 0.44492
2020-10-14 13:00 | 6902 |  |  | 0.5177
2020-10-14 14:00 | 6903 |  |  | 0.45815
2020-10-14 15:00 | 6904 |  |  | 0.33907
2020-10-14 16:00 | 6905 |  |  | 0.061197
2020-10-14 17:00 | 6906 |  |  | 0
2020-10-14 18:00 | 6907 |  |  | 0
2020-10-14 19:00 | 6908 |  |  | 0
2020-10-14 20:00 | 6909 |  |  | 0
2020-10-14 21:00 | 6910 |  |  | 0
2020-10-14 22:00 | 6911 |  |  | 0
2020-10-14 23:00 | 6912 |  |  | 0
2020-10-15 | 6913 |  |  | 0
2020-10-15 01:00 | 6914 |  |  | 0
2020-10-15 02:00 | 6915 |  |  | 0
2020-10-15 03:00 | 6916 |  |  | 0
2020-10-15 04:00 | 6917 |  |  | 0
2020-10-15 05:00 | 6918 |  |  | 0
2020-10-15 06:00 | 6919 |  |  | 0
2020-10-15 07:00 | 6920 |  |  | 0.0099239
2020-10-15 08:00 | 6921 |  |  | 0.021502
2020-10-15 09:00 | 6922 |  |  | 0.023156
2020-10-15 10:00 | 6923 |  |  | 0.031426
2020-10-15 11:00 | 6924 |  |  | 0.043004
2020-10-15 12:00 | 6925 |  |  | 0.071121
2020-10-15 13:00 | 6926 |  |  | 0.14059
2020-10-15 14:00 | 6927 |  |  | 0.076083
2020-10-15 15:00 | 6928 |  |  | 0.039696
2020-10-15 16:00 | 6929 |  |  | 0
2020-10-15 17:00 | 6930 |  |  | 0
2020-10-15 18:00 | 6931 |  |  | 0
2020-10-15 19:00 | 6932 |  |  | 0
2020-10-15 20:00 | 6933 |  |  | 0
2020-10-15 21:00 | 6934 |  |  | 0
2020-10-15 22:00 | 6935 |  |  | 0
2020-10-15 23:00 | 6936 |  |  | 0
2020-10-16 | 6937 |  |  | 0
2020-10-16 01:00 | 6938 |  |  | 0
2020-10-16 02:00 | 6939 |  |  | 0
2020-10-16 03:00 | 6940 |  |  | 0
2020-10-16 04:00 | 6941 |  |  | 0
2020-10-16 05:00 | 6942 |  |  | 0
2020-10-16 06:00 | 6943 |  |  | 0
2020-10-16 07:00 | 6944 |  |  | 0.018194
2020-10-16 08:00 | 6945 |  |  | 0.087661
2020-10-16 09:00 | 6946 |  |  | 0.14059
2020-10-16 10:00 | 6947 |  |  | 0.16044
2020-10-16 11:00 | 6948 |  |  | 0.28118
2020-10-16 12:00 | 6949 |  |  | 0.61197
2020-10-16 13:00 | 6950 |  |  | 0.56897
2020-10-16 14:00 | 6951 |  |  | 0.56401
2020-10-16 15:00 | 6952 |  |  | 0.3738
2020-10-16 16:00 | 6953 |  |  | 0.17036
2020-10-16 17:00 | 6954 |  |  | 0
2020-10-16 18:00 | 6955 |  |  | 0
2020-10-16 19:00 | 6956 |  |  | 0
2020-10-16 20:00 | 6957 |  |  | 0
2020-10-16 21:00 | 6958 |  |  | 0
2020-10-16 22:00 | 6959 |  |  | 0
2020-10-16 23:00 | 6960 |  |  | 0
2020-10-17 | 6961 |  |  | 0
2020-10-17 01:00 | 6962 |  |  | 0
2020-10-17 02:00 | 6963 |  |  | 0
2020-10-17 03:00 | 6964 |  |  | 0
2020-10-17 04:00 | 6965 |  |  | 0
2020-10-17 05:00 | 6966 |  |  | 0
2020-10-17 06:00 | 6967 |  |  | 0
2020-10-17 07:00 | 6968 |  |  | 0.0082699
2020-10-17 08:00 | 6969 |  |  | 0.17201
2020-10-17 09:00 | 6970 |  |  | 0.37049
2020-10-17 10:00 | 6971 |  |  | 0.52928
2020-10-17 11:00 | 6972 |  |  | 0.59378
2020-10-17 12:00 | 6973 |  |  | 0.66821
2020-10-17 13:00 | 6974 |  |  | 0.63844
2020-10-17 14:00 | 6975 |  |  | 0.55078
2020-10-17 15:00 | 6976 |  |  | 0.38207
2020-10-17 16:00 | 6977 |  |  | 0.15547
2020-10-17 17:00 | 6978 |  |  | 0.001654
2020-10-17 18:00 | 6979 |  |  | 0
2020-10-17 19:00 | 6980 |  |  | 0
2020-10-17 20:00 | 6981 |  |  | 0
2020-10-17 21:00 | 6982 |  |  | 0
2020-10-17 22:00 | 6983 |  |  | 0
2020-10-17 23:00 | 6984 |  |  | 0
2020-10-18 | 6985 |  |  | 0
2020-10-18 01:00 | 6986 |  |  | 0
2020-10-18 02:00 | 6987 |  |  | 0
2020-10-18 03:00 | 6988 |  |  | 0
2020-10-18 04:00 | 6989 |  |  | 0
2020-10-18 05:00 | 6990 |  |  | 0
2020-10-18 06:00 | 6991 |  |  | 0
2020-10-18 07:00 | 6992 |  |  | 0
2020-10-18 08:00 | 6993 |  |  | 0.044658
2020-10-18 09:00 | 6994 |  |  | 0.26298
2020-10-18 10:00 | 6995 |  |  | 0.40523
2020-10-18 11:00 | 6996 |  |  | 0.5177
2020-10-18 12:00 | 6997 |  |  | 0.47304
2020-10-18 13:00 | 6998 |  |  | 0.57393
2020-10-18 14:00 | 6999 |  |  | 0.19682
2020-10-18 15:00 | 7000 |  |  | 0.22163
2020-10-18 16:00 | 7001 |  |  | 0.077737
2020-10-18 17:00 | 7002 |  |  | 0
2020-10-18 18:00 | 7003 |  |  | 0
2020-10-18 19:00 | 7004 |  |  | 0
2020-10-18 20:00 | 7005 |  |  | 0
2020-10-18 21:00 | 7006 |  |  | 0
2020-10-18 22:00 | 7007 |  |  | 0
2020-10-18 23:00 | 7008 |  |  | 0
2020-10-19 | 7009 |  |  | 0
2020-10-19 01:00 | 7010 |  |  | 0
2020-10-19 02:00 | 7011 |  |  | 0
2020-10-19 03:00 | 7012 |  |  | 0
2020-10-19 04:00 | 7013 |  |  | 0
2020-10-19 05:00 | 7014 |  |  | 0
2020-10-19 06:00 | 7015 |  |  | 0
2020-10-19 07:00 | 7016 |  |  | 0
2020-10-19 08:00 | 7017 |  |  | 0.0082699
2020-10-19 09:00 | 7018 |  |  | 0.14059
2020-10-19 10:00 | 7019 |  |  | 0.21667
2020-10-19 11:00 | 7020 |  |  | 0.34899
2020-10-19 12:00 | 7021 |  |  | 0.47304
2020-10-19 13:00 | 7022 |  |  | 0.48131
2020-10-19 14:00 | 7023 |  |  | 0.059543
2020-10-19 15:00 | 7024 |  |  | 0
2020-10-19 16:00 | 7025 |  |  | 0
2020-10-19 17:00 | 7026 |  |  | 0
2020-10-19 18:00 | 7027 |  |  | 0
2020-10-19 19:00 | 7028 |  |  | 0
2020-10-19 20:00 | 7029 |  |  | 0
2020-10-19 21:00 | 7030 |  |  | 0
2020-10-19 22:00 | 7031 |  |  | 0
2020-10-19 23:00 | 7032 |  |  | 0
2020-10-20 | 7033 |  |  | 0
2020-10-20 01:00 | 7034 |  |  | 0
2020-10-20 02:00 | 7035 |  |  | 0
2020-10-20 03:00 | 7036 |  |  | 0
2020-10-20 04:00 | 7037 |  |  | 0
2020-10-20 05:00 | 7038 |  |  | 0
2020-10-20 06:00 | 7039 |  |  | 0
2020-10-20 07:00 | 7040 |  |  | 0
2020-10-20 08:00 | 7041 |  |  | 0.0099239
2020-10-20 09:00 | 7042 |  |  | 0.036388
2020-10-20 10:00 | 7043 |  |  | 0.061197
2020-10-20 11:00 | 7044 |  |  | 0.1257
2020-10-20 12:00 | 7045 |  |  | 0.12736
2020-10-20 13:00 | 7046 |  |  | 0.13728
2020-10-20 14:00 | 7047 |  |  | 0.13728
2020-10-20 15:00 | 7048 |  |  | 0.081045
2020-10-20 16:00 | 7049 |  |  | 0.0066159
2020-10-20 17:00 | 7050 |  |  | 0
2020-10-20 18:00 | 7051 |  |  | 0
2020-10-20 19:00 | 7052 |  |  | 0
2020-10-20 20:00 | 7053 |  |  | 0
2020-10-20 21:00 | 7054 |  |  | 0
2020-10-20 22:00 | 7055 |  |  | 0
2020-10-20 23:00 | 7056 |  |  | 0
2020-10-21 | 7057 |  |  | 0
2020-10-21 01:00 | 7058 |  |  | 0
2020-10-21 02:00 | 7059 |  |  | 0
2020-10-21 03:00 | 7060 |  |  | 0
2020-10-21 04:00 | 7061 |  |  | 0
2020-10-21 05:00 | 7062 |  |  | 0
2020-10-21 06:00 | 7063 |  |  | 0
2020-10-21 07:00 | 7064 |  |  | 0
2020-10-21 08:00 | 7065 |  |  | 0.014886
2020-10-21 09:00 | 7066 |  |  | 0.046312
2020-10-21 10:00 | 7067 |  |  | 0.092623
2020-10-21 11:00 | 7068 |  |  | 0.077737
2020-10-21 12:00 | 7069 |  |  | 0.069467
2020-10-21 13:00 | 7070 |  |  | 0.097585
2020-10-21 14:00 | 7071 |  |  | 0.046312
2020-10-21 15:00 | 7072 |  |  | 0.02481
2020-10-21 16:00 | 7073 |  |  | 0
2020-10-21 17:00 | 7074 |  |  | 0
2020-10-21 18:00 | 7075 |  |  | 0
2020-10-21 19:00 | 7076 |  |  | 0
2020-10-21 20:00 | 7077 |  |  | 0
2020-10-21 21:00 | 7078 |  |  | 0
2020-10-21 22:00 | 7079 |  |  | 0
2020-10-21 23:00 | 7080 |  |  | 0
2020-10-22 | 7081 |  |  | 0
2020-10-22 01:00 | 7082 |  |  | 0
2020-10-22 02:00 | 7083 |  |  | 0
2020-10-22 03:00 | 7084 |  |  | 0
2020-10-22 04:00 | 7085 |  |  | 0
2020-10-22 05:00 | 7086 |  |  | 0
2020-10-22 06:00 | 7087 |  |  | 0
2020-10-22 07:00 | 7088 |  |  | 0
2020-10-22 08:00 | 7089 |  |  | 0
2020-10-22 09:00 | 7090 |  |  | 0.028118
2020-10-22 10:00 | 7091 |  |  | 0.052928
2020-10-22 11:00 | 7092 |  |  | 0.11909
2020-10-22 12:00 | 7093 |  |  | 0.11082
2020-10-22 13:00 | 7094 |  |  | 0.043004
2020-10-22 14:00 | 7095 |  |  | 0.023156
2020-10-22 15:00 | 7096 |  |  | 0.023156
2020-10-22 16:00 | 7097 |  |  | 0
2020-10-22 17:00 | 7098 |  |  | 0
2020-10-22 18:00 | 7099 |  |  | 0
2020-10-22 19:00 | 7100 |  |  | 0
2020-10-22 20:00 | 7101 |  |  | 0
2020-10-22 21:00 | 7102 |  |  | 0
2020-10-22 22:00 | 7103 |  |  | 0
2020-10-22 23:00 | 7104 |  |  | 0
2020-10-23 | 7105 |  |  | 0
2020-10-23 01:00 | 7106 |  |  | 0
2020-10-23 02:00 | 7107 |  |  | 0
2020-10-23 03:00 | 7108 |  |  | 0
2020-10-23 04:00 | 7109 |  |  | 0
2020-10-23 05:00 | 7110 |  |  | 0
2020-10-23 06:00 | 7111 |  |  | 0
2020-10-23 07:00 | 7112 |  |  | 0
2020-10-23 08:00 | 7113 |  |  | 0
2020-10-23 09:00 | 7114 |  |  | 0.001654
2020-10-23 10:00 | 7115 |  |  | 0
2020-10-23 11:00 | 7116 |  |  | 0.0099239
2020-10-23 12:00 | 7117 |  |  | 0.043004
2020-10-23 13:00 | 7118 |  |  | 0.011578
2020-10-23 14:00 | 7119 |  |  | 0.031426
2020-10-23 15:00 | 7120 |  |  | 0.001654
2020-10-23 16:00 | 7121 |  |  | 0
2020-10-23 17:00 | 7122 |  |  | 0
2020-10-23 18:00 | 7123 |  |  | 0
2020-10-23 19:00 | 7124 |  |  | 0
2020-10-23 20:00 | 7125 |  |  | 0
2020-10-23 21:00 | 7126 |  |  | 0
2020-10-23 22:00 | 7127 |  |  | 0
2020-10-23 23:00 | 7128 |  |  | 0
2020-10-24 | 7129 |  |  | 0
2020-10-24 01:00 | 7130 |  |  | 0
2020-10-24 02:00 | 7131 |  |  | 0
2020-10-24 03:00 | 7132 |  |  | 0
2020-10-24 04:00 | 7133 |  |  | 0
2020-10-24 05:00 | 7134 |  |  | 0
2020-10-24 06:00 | 7135 |  |  | 0
2020-10-24 07:00 | 7136 |  |  | 0
2020-10-24 08:00 | 7137 |  |  | 0.043004
2020-10-24 09:00 | 7138 |  |  | 0.28118
2020-10-24 10:00 | 7139 |  |  | 0.3953
2020-10-24 11:00 | 7140 |  |  | 0.57063
2020-10-24 12:00 | 7141 |  |  | 0.59874
2020-10-24 13:00 | 7142 |  |  | 0.58882
2020-10-24 14:00 | 7143 |  |  | 0.46973
2020-10-24 15:00 | 7144 |  |  | 0.28779
2020-10-24 16:00 | 7145 |  |  | 0.089315
2020-10-24 17:00 | 7146 |  |  | 0
2020-10-24 18:00 | 7147 |  |  | 0
2020-10-24 19:00 | 7148 |  |  | 0
2020-10-24 20:00 | 7149 |  |  | 0
2020-10-24 21:00 | 7150 |  |  | 0
2020-10-24 22:00 | 7151 |  |  | 0
2020-10-24 23:00 | 7152 |  |  | 0
2020-10-25 | 7153 |  |  | 0
2020-10-25 01:00 | 7154 |  |  | 0
2020-10-25 02:00 | 7155 |  |  | 0
2020-10-25 03:00 | 7156 |  |  | 0
2020-10-25 04:00 | 7157 |  |  | 0
2020-10-25 05:00 | 7158 |  |  | 0
2020-10-25 06:00 | 7159 |  |  | 0
2020-10-25 07:00 | 7160 |  |  | 0.014886
2020-10-25 08:00 | 7161 |  |  | 0.043004
2020-10-25 09:00 | 7162 |  |  | 0.071121
2020-10-25 10:00 | 7163 |  |  | 0.16705
2020-10-25 11:00 | 7164 |  |  | 0.066159
2020-10-25 12:00 | 7165 |  |  | 0.056236
2020-10-25 13:00 | 7166 |  |  | 0.026464
2020-10-25 14:00 | 7167 |  |  | 0.029772
2020-10-25 15:00 | 7168 |  |  | 0.003308
2020-10-25 16:00 | 7169 |  |  | 0
2020-10-25 17:00 | 7170 |  |  | 0
2020-10-25 18:00 | 7171 |  |  | 0
2020-10-25 19:00 | 7172 |  |  | 0
2020-10-25 20:00 | 7173 |  |  | 0
2020-10-25 21:00 | 7174 |  |  | 0
2020-10-25 22:00 | 7175 |  |  | 0
2020-10-25 23:00 | 7176 |  |  | 0
2020-10-26 | 7177 |  |  | 0
2020-10-26 01:00 | 7178 |  |  | 0
2020-10-26 02:00 | 7179 |  |  | 0
2020-10-26 03:00 | 7180 |  |  | 0
2020-10-26 04:00 | 7181 |  |  | 0
2020-10-26 05:00 | 7182 |  |  | 0
2020-10-26 06:00 | 7183 |  |  | 0
2020-10-26 07:00 | 7184 |  |  | 0
2020-10-26 08:00 | 7185 |  |  | 0.004962
2020-10-26 09:00 | 7186 |  |  | 0.072775
2020-10-26 10:00 | 7187 |  |  | 0.15382
2020-10-26 11:00 | 7188 |  |  | 0.099239
2020-10-26 12:00 | 7189 |  |  | 0.072775
2020-10-26 13:00 | 7190 |  |  | 0.021502
2020-10-26 14:00 | 7191 |  |  | 0.014886
2020-10-26 15:00 | 7192 |  |  | 0
2020-10-26 16:00 | 7193 |  |  | 0
2020-10-26 17:00 | 7194 |  |  | 0
2020-10-26 18:00 | 7195 |  |  | 0
2020-10-26 19:00 | 7196 |  |  | 0
2020-10-26 20:00 | 7197 |  |  | 0
2020-10-26 21:00 | 7198 |  |  | 0
2020-10-26 22:00 | 7199 |  |  | 0
2020-10-26 23:00 | 7200 |  |  | 0
2020-10-27 | 7201 |  |  | 0
2020-10-27 01:00 | 7202 |  |  | 0
2020-10-27 02:00 | 7203 |  |  | 0
2020-10-27 03:00 | 7204 |  |  | 0
2020-10-27 04:00 | 7205 |  |  | 0
2020-10-27 05:00 | 7206 |  |  | 0
2020-10-27 06:00 | 7207 |  |  | 0
2020-10-27 07:00 | 7208 |  |  | 0.074429
2020-10-27 08:00 | 7209 |  |  | 0.3738
2020-10-27 09:00 | 7210 |  |  | 0.52928
2020-10-27 10:00 | 7211 |  |  | 0.61363
2020-10-27 11:00 | 7212 |  |  | 0.6649
2020-10-27 12:00 | 7213 |  |  | 0.62355
2020-10-27 13:00 | 7214 |  |  | 0.49289
2020-10-27 14:00 | 7215 |  |  | 0.31095
2020-10-27 15:00 | 7216 |  |  | 0.10255
2020-10-27 16:00 | 7217 |  |  | 0
2020-10-27 17:00 | 7218 |  |  | 0
2020-10-27 18:00 | 7219 |  |  | 0
2020-10-27 19:00 | 7220 |  |  | 0
2020-10-27 20:00 | 7221 |  |  | 0
2020-10-27 21:00 | 7222 |  |  | 0
2020-10-27 22:00 | 7223 |  |  | 0
2020-10-27 23:00 | 7224 |  |  | 0
2020-10-28 | 7225 |  |  | 0
2020-10-28 01:00 | 7226 |  |  | 0
2020-10-28 02:00 | 7227 |  |  | 0
2020-10-28 03:00 | 7228 |  |  | 0
2020-10-28 04:00 | 7229 |  |  | 0
2020-10-28 05:00 | 7230 |  |  | 0
2020-10-28 06:00 | 7231 |  |  | 0.014886
2020-10-28 07:00 | 7232 |  |  | 0.16374
2020-10-28 08:00 | 7233 |  |  | 0.34734
2020-10-28 09:00 | 7234 |  |  | 0.51108
2020-10-28 10:00 | 7235 |  |  | 0.58551
2020-10-28 11:00 | 7236 |  |  | 0.6037
2020-10-28 12:00 | 7237 |  |  | 0.59543
2020-10-28 13:00 | 7238 |  |  | 0.42838
2020-10-28 14:00 | 7239 |  |  | 0.30268
2020-10-28 15:00 | 7240 |  |  | 0.087661
2020-10-28 16:00 | 7241 |  |  | 0
2020-10-28 17:00 | 7242 |  |  | 0
2020-10-28 18:00 | 7243 |  |  | 0
2020-10-28 19:00 | 7244 |  |  | 0
2020-10-28 20:00 | 7245 |  |  | 0
2020-10-28 21:00 | 7246 |  |  | 0
2020-10-28 22:00 | 7247 |  |  | 0
2020-10-28 23:00 | 7248 |  |  | 0
2020-10-29 | 7249 |  |  | 0
2020-10-29 01:00 | 7250 |  |  | 0
2020-10-29 02:00 | 7251 |  |  | 0
2020-10-29 03:00 | 7252 |  |  | 0
2020-10-29 04:00 | 7253 |  |  | 0
2020-10-29 05:00 | 7254 |  |  | 0
2020-10-29 06:00 | 7255 |  |  | 0.0066159
2020-10-29 07:00 | 7256 |  |  | 0.074429
2020-10-29 08:00 | 7257 |  |  | 0.24148
2020-10-29 09:00 | 7258 |  |  | 0.32418
2020-10-29 10:00 | 7259 |  |  | 0.37049
2020-10-29 11:00 | 7260 |  |  | 0.39696
2020-10-29 12:00 | 7261 |  |  | 0.42342
2020-10-29 13:00 | 7262 |  |  | 0.32584
2020-10-29 14:00 | 7263 |  |  | 0.18855
2020-10-29 15:00 | 7264 |  |  | 0.076083
2020-10-29 16:00 | 7265 |  |  | 0
2020-10-29 17:00 | 7266 |  |  | 0
2020-10-29 18:00 | 7267 |  |  | 0
2020-10-29 19:00 | 7268 |  |  | 0
2020-10-29 20:00 | 7269 |  |  | 0
2020-10-29 21:00 | 7270 |  |  | 0
2020-10-29 22:00 | 7271 |  |  | 0
2020-10-29 23:00 | 7272 |  |  | 0
2020-10-30 | 7273 |  |  | 0
2020-10-30 01:00 | 7274 |  |  | 0
2020-10-30 02:00 | 7275 |  |  | 0
2020-10-30 03:00 | 7276 |  |  | 0
2020-10-30 04:00 | 7277 |  |  | 0
2020-10-30 05:00 | 7278 |  |  | 0
2020-10-30 06:00 | 7279 |  |  | 0.0066159
2020-10-30 07:00 | 7280 |  |  | 0.12074
2020-10-30 08:00 | 7281 |  |  | 0.27291
2020-10-30 09:00 | 7282 |  |  | 0.40026
2020-10-30 10:00 | 7283 |  |  | 0.4995
2020-10-30 11:00 | 7284 |  |  | 0.58055
2020-10-30 12:00 | 7285 |  |  | 0.42177
2020-10-30 13:00 | 7286 |  |  | 0.40688
2020-10-30 14:00 | 7287 |  |  | 0.23983
2020-10-30 15:00 | 7288 |  |  | 0.077737
2020-10-30 16:00 | 7289 |  |  | 0
2020-10-30 17:00 | 7290 |  |  | 0
2020-10-30 18:00 | 7291 |  |  | 0
2020-10-30 19:00 | 7292 |  |  | 0
2020-10-30 20:00 | 7293 |  |  | 0
2020-10-30 21:00 | 7294 |  |  | 0
2020-10-30 22:00 | 7295 |  |  | 0
2020-10-30 23:00 | 7296 |  |  | 0
2020-10-31 | 7297 |  |  | 0
2020-10-31 01:00 | 7298 |  |  | 0
2020-10-31 02:00 | 7299 |  |  | 0
2020-10-31 03:00 | 7300 |  |  | 0
2020-10-31 04:00 | 7301 |  |  | 0
2020-10-31 05:00 | 7302 |  |  | 0
2020-10-31 06:00 | 7303 |  |  | 0
2020-10-31 07:00 | 7304 |  |  | 0.10089
2020-10-31 08:00 | 7305 |  |  | 0.29276
2020-10-31 09:00 | 7306 |  |  | 0.44161
2020-10-31 10:00 | 7307 |  |  | 0.44161
2020-10-31 11:00 | 7308 |  |  | 0.50447
2020-10-31 12:00 | 7309 |  |  | 0.53258
2020-10-31 13:00 | 7310 |  |  | 0.39034
2020-10-31 14:00 | 7311 |  |  | 0.22163
2020-10-31 15:00 | 7312 |  |  | 0.047966
2020-10-31 16:00 | 7313 |  |  | 0
2020-10-31 17:00 | 7314 |  |  | 0
2020-10-31 18:00 | 7315 |  |  | 0
2020-10-31 19:00 | 7316 |  |  | 0
2020-10-31 20:00 | 7317 |  |  | 0
2020-10-31 21:00 | 7318 |  |  | 0
2020-10-31 22:00 | 7319 |  |  | 0
2020-10-31 23:00 | 7320 |  |  | 0
2020-11-01 | 7321 |  |  | 0
2020-11-01 01:00 | 7322 |  |  | 0
2020-11-01 02:00 | 7323 |  |  | 0
2020-11-01 03:00 | 7324 |  |  | 0
2020-11-01 04:00 | 7325 |  |  | 0
2020-11-01 05:00 | 7326 |  |  | 0
2020-11-01 06:00 | 7327 |  |  | 0.018194
2020-11-01 07:00 | 7328 |  |  | 0.082699
2020-11-01 08:00 | 7329 |  |  | 0.13728
2020-11-01 09:00 | 7330 |  |  | 0.27125
2020-11-01 10:00 | 7331 |  |  | 0.24148
2020-11-01 11:00 | 7332 |  |  | 0.27622
2020-11-01 12:00 | 7333 |  |  | 0.18194
2020-11-01 13:00 | 7334 |  |  | 0.36057
2020-11-01 14:00 | 7335 |  |  | 0.21998
2020-11-01 15:00 | 7336 |  |  | 0.026464
2020-11-01 16:00 | 7337 |  |  | 0
2020-11-01 17:00 | 7338 |  |  | 0
2020-11-01 18:00 | 7339 |  |  | 0
2020-11-01 19:00 | 7340 |  |  | 0
2020-11-01 20:00 | 7341 |  |  | 0
2020-11-01 21:00 | 7342 |  |  | 0
2020-11-01 22:00 | 7343 |  |  | 0
2020-11-01 23:00 | 7344 |  |  | 0
2020-11-02 | 7345 |  |  | 0
2020-11-02 01:00 | 7346 |  |  | 0
2020-11-02 02:00 | 7347 |  |  | 0
2020-11-02 03:00 | 7348 |  |  | 0
2020-11-02 04:00 | 7349 |  |  | 0
2020-11-02 05:00 | 7350 |  |  | 0
2020-11-02 06:00 | 7351 |  |  | 0
2020-11-02 07:00 | 7352 |  |  | 0.0099239
2020-11-02 08:00 | 7353 |  |  | 0.056236
2020-11-02 09:00 | 7354 |  |  | 0.11743
2020-11-02 10:00 | 7355 |  |  | 0.34899
2020-11-02 11:00 | 7356 |  |  | 0.53424
2020-11-02 12:00 | 7357 |  |  | 0.49123
2020-11-02 13:00 | 7358 |  |  | 0.37545
2020-11-02 14:00 | 7359 |  |  | 0.21006
2020-11-02 15:00 | 7360 |  |  | 0.052928
2020-11-02 16:00 | 7361 |  |  | 0
2020-11-02 17:00 | 7362 |  |  | 0
2020-11-02 18:00 | 7363 |  |  | 0
2020-11-02 19:00 | 7364 |  |  | 0
2020-11-02 20:00 | 7365 |  |  | 0
2020-11-02 21:00 | 7366 |  |  | 0
2020-11-02 22:00 | 7367 |  |  | 0
2020-11-02 23:00 | 7368 |  |  | 0
2020-11-03 | 7369 |  |  | 0
2020-11-03 01:00 | 7370 |  |  | 0
2020-11-03 02:00 | 7371 |  |  | 0
2020-11-03 03:00 | 7372 |  |  | 0
2020-11-03 04:00 | 7373 |  |  | 0
2020-11-03 05:00 | 7374 |  |  | 0
2020-11-03 06:00 | 7375 |  |  | 0
2020-11-03 07:00 | 7376 |  |  | 0.019848
2020-11-03 08:00 | 7377 |  |  | 0.067813
2020-11-03 09:00 | 7378 |  |  | 0.13066
2020-11-03 10:00 | 7379 |  |  | 0.14059
2020-11-03 11:00 | 7380 |  |  | 0.14224
2020-11-03 12:00 | 7381 |  |  | 0.11909
2020-11-03 13:00 | 7382 |  |  | 0.062851
2020-11-03 14:00 | 7383 |  |  | 0.011578
2020-11-03 15:00 | 7384 |  |  | 0
2020-11-03 16:00 | 7385 |  |  | 0
2020-11-03 17:00 | 7386 |  |  | 0
2020-11-03 18:00 | 7387 |  |  | 0
2020-11-03 19:00 | 7388 |  |  | 0
2020-11-03 20:00 | 7389 |  |  | 0
2020-11-03 21:00 | 7390 |  |  | 0
2020-11-03 22:00 | 7391 |  |  | 0
2020-11-03 23:00 | 7392 |  |  | 0
2020-11-04 | 7393 |  |  | 0
2020-11-04 01:00 | 7394 |  |  | 0
2020-11-04 02:00 | 7395 |  |  | 0
2020-11-04 03:00 | 7396 |  |  | 0
2020-11-04 04:00 | 7397 |  |  | 0
2020-11-04 05:00 | 7398 |  |  | 0
2020-11-04 06:00 | 7399 |  |  | 0
2020-11-04 07:00 | 7400 |  |  | 0.0066159
2020-11-04 08:00 | 7401 |  |  | 0.0066159
2020-11-04 09:00 | 7402 |  |  | 0.05789
2020-11-04 10:00 | 7403 |  |  | 0.13728
2020-11-04 11:00 | 7404 |  |  | 0.12901
2020-11-04 12:00 | 7405 |  |  | 0.14224
2020-11-04 13:00 | 7406 |  |  | 0.12736
2020-11-04 14:00 | 7407 |  |  | 0.066159
2020-11-04 15:00 | 7408 |  |  | 0.0066159
2020-11-04 16:00 | 7409 |  |  | 0
2020-11-04 17:00 | 7410 |  |  | 0
2020-11-04 18:00 | 7411 |  |  | 0
2020-11-04 19:00 | 7412 |  |  | 0
2020-11-04 20:00 | 7413 |  |  | 0
2020-11-04 21:00 | 7414 |  |  | 0
2020-11-04 22:00 | 7415 |  |  | 0
2020-11-04 23:00 | 7416 |  |  | 0
2020-11-05 | 7417 |  |  | 0
2020-11-05 01:00 | 7418 |  |  | 0
2020-11-05 02:00 | 7419 |  |  | 0
2020-11-05 03:00 | 7420 |  |  | 0
2020-11-05 04:00 | 7421 |  |  | 0
2020-11-05 05:00 | 7422 |  |  | 0
2020-11-05 06:00 | 7423 |  |  | 0
2020-11-05 07:00 | 7424 |  |  | 0.071121
2020-11-05 08:00 | 7425 |  |  | 0.2696
2020-11-05 09:00 | 7426 |  |  | 0.42177
2020-11-05 10:00 | 7427 |  |  | 0.5177
2020-11-05 11:00 | 7428 |  |  | 0.52762
2020-11-05 12:00 | 7429 |  |  | 0.478
2020-11-05 13:00 | 7430 |  |  | 0.37711
2020-11-05 14:00 | 7431 |  |  | 0.16871
2020-11-05 15:00 | 7432 |  |  | 0.021502
2020-11-05 16:00 | 7433 |  |  | 0
2020-11-05 17:00 | 7434 |  |  | 0
2020-11-05 18:00 | 7435 |  |  | 0
2020-11-05 19:00 | 7436 |  |  | 0
2020-11-05 20:00 | 7437 |  |  | 0
2020-11-05 21:00 | 7438 |  |  | 0
2020-11-05 22:00 | 7439 |  |  | 0
2020-11-05 23:00 | 7440 |  |  | 0
2020-11-06 | 7441 |  |  | 0
2020-11-06 01:00 | 7442 |  |  | 0
2020-11-06 02:00 | 7443 |  |  | 0
2020-11-06 03:00 | 7444 |  |  | 0
2020-11-06 04:00 | 7445 |  |  | 0
2020-11-06 05:00 | 7446 |  |  | 0
2020-11-06 06:00 | 7447 |  |  | 0
2020-11-06 07:00 | 7448 |  |  | 0.0082699
2020-11-06 08:00 | 7449 |  |  | 0.086007
2020-11-06 09:00 | 7450 |  |  | 0.1257
2020-11-06 10:00 | 7451 |  |  | 0.14555
2020-11-06 11:00 | 7452 |  |  | 0.2266
2020-11-06 12:00 | 7453 |  |  | 0.30764
2020-11-06 13:00 | 7454 |  |  | 0.29276
2020-11-06 14:00 | 7455 |  |  | 0.16705
2020-11-06 15:00 | 7456 |  |  | 0.028118
2020-11-06 16:00 | 7457 |  |  | 0
2020-11-06 17:00 | 7458 |  |  | 0
2020-11-06 18:00 | 7459 |  |  | 0
2020-11-06 19:00 | 7460 |  |  | 0
2020-11-06 20:00 | 7461 |  |  | 0
2020-11-06 21:00 | 7462 |  |  | 0
2020-11-06 22:00 | 7463 |  |  | 0
2020-11-06 23:00 | 7464 |  |  | 0
2020-11-07 | 7465 |  |  | 0
2020-11-07 01:00 | 7466 |  |  | 0
2020-11-07 02:00 | 7467 |  |  | 0
2020-11-07 03:00 | 7468 |  |  | 0
2020-11-07 04:00 | 7469 |  |  | 0
2020-11-07 05:00 | 7470 |  |  | 0
2020-11-07 06:00 | 7471 |  |  | 0
2020-11-07 07:00 | 7472 |  |  | 0.097585
2020-11-07 08:00 | 7473 |  |  | 0.25968
2020-11-07 09:00 | 7474 |  |  | 0.3953
2020-11-07 10:00 | 7475 |  |  | 0.47966
2020-11-07 11:00 | 7476 |  |  | 0.51604
2020-11-07 12:00 | 7477 |  |  | 0.26298
2020-11-07 13:00 | 7478 |  |  | 0.16705
2020-11-07 14:00 | 7479 |  |  | 0.13728
2020-11-07 15:00 | 7480 |  |  | 0.01654
2020-11-07 16:00 | 7481 |  |  | 0
2020-11-07 17:00 | 7482 |  |  | 0
2020-11-07 18:00 | 7483 |  |  | 0
2020-11-07 19:00 | 7484 |  |  | 0
2020-11-07 20:00 | 7485 |  |  | 0
2020-11-07 21:00 | 7486 |  |  | 0
2020-11-07 22:00 | 7487 |  |  | 0
2020-11-07 23:00 | 7488 |  |  | 0
2020-11-08 | 7489 |  |  | 0
2020-11-08 01:00 | 7490 |  |  | 0
2020-11-08 02:00 | 7491 |  |  | 0
2020-11-08 03:00 | 7492 |  |  | 0
2020-11-08 04:00 | 7493 |  |  | 0
2020-11-08 05:00 | 7494 |  |  | 0
2020-11-08 06:00 | 7495 |  |  | 0
2020-11-08 07:00 | 7496 |  |  | 0.095931
2020-11-08 08:00 | 7497 |  |  | 0.27787
2020-11-08 09:00 | 7498 |  |  | 0.35561
2020-11-08 10:00 | 7499 |  |  | 0.23817
2020-11-08 11:00 | 7500 |  |  | 0.3738
2020-11-08 12:00 | 7501 |  |  | 0.33245
2020-11-08 13:00 | 7502 |  |  | 0.36222
2020-11-08 14:00 | 7503 |  |  | 0.21171
2020-11-08 15:00 | 7504 |  |  | 0.039696
2020-11-08 16:00 | 7505 |  |  | 0
2020-11-08 17:00 | 7506 |  |  | 0
2020-11-08 18:00 | 7507 |  |  | 0
2020-11-08 19:00 | 7508 |  |  | 0
2020-11-08 20:00 | 7509 |  |  | 0
2020-11-08 21:00 | 7510 |  |  | 0
2020-11-08 22:00 | 7511 |  |  | 0
2020-11-08 23:00 | 7512 |  |  | 0
2020-11-09 | 7513 |  |  | 0
2020-11-09 01:00 | 7514 |  |  | 0
2020-11-09 02:00 | 7515 |  |  | 0
2020-11-09 03:00 | 7516 |  |  | 0
2020-11-09 04:00 | 7517 |  |  | 0
2020-11-09 05:00 | 7518 |  |  | 0
2020-11-09 06:00 | 7519 |  |  | 0
2020-11-09 07:00 | 7520 |  |  | 0.10916
2020-11-09 08:00 | 7521 |  |  | 0.28118
2020-11-09 09:00 | 7522 |  |  | 0.4135
2020-11-09 10:00 | 7523 |  |  | 0.52266
2020-11-09 11:00 | 7524 |  |  | 0.56897
2020-11-09 12:00 | 7525 |  |  | 0.45815
2020-11-09 13:00 | 7526 |  |  | 0.36222
2020-11-09 14:00 | 7527 |  |  | 0.18525
2020-11-09 15:00 | 7528 |  |  | 0.02481
2020-11-09 16:00 | 7529 |  |  | 0
2020-11-09 17:00 | 7530 |  |  | 0
2020-11-09 18:00 | 7531 |  |  | 0
2020-11-09 19:00 | 7532 |  |  | 0
2020-11-09 20:00 | 7533 |  |  | 0
2020-11-09 21:00 | 7534 |  |  | 0
2020-11-09 22:00 | 7535 |  |  | 0
2020-11-09 23:00 | 7536 |  |  | 0
2020-11-10 | 7537 |  |  | 0
2020-11-10 01:00 | 7538 |  |  | 0
2020-11-10 02:00 | 7539 |  |  | 0
2020-11-10 03:00 | 7540 |  |  | 0
2020-11-10 04:00 | 7541 |  |  | 0
2020-11-10 05:00 | 7542 |  |  | 0
2020-11-10 06:00 | 7543 |  |  | 0
2020-11-10 07:00 | 7544 |  |  | 0.090969
2020-11-10 08:00 | 7545 |  |  | 0.19186
2020-11-10 09:00 | 7546 |  |  | 0.31591
2020-11-10 10:00 | 7547 |  |  | 0.45154
2020-11-10 11:00 | 7548 |  |  | 0.36718
2020-11-10 12:00 | 7549 |  |  | 0.41184
2020-11-10 13:00 | 7550 |  |  | 0.32914
2020-11-10 14:00 | 7551 |  |  | 0.18525
2020-11-10 15:00 | 7552 |  |  | 0.026464
2020-11-10 16:00 | 7553 |  |  | 0
2020-11-10 17:00 | 7554 |  |  | 0
2020-11-10 18:00 | 7555 |  |  | 0
2020-11-10 19:00 | 7556 |  |  | 0
2020-11-10 20:00 | 7557 |  |  | 0
2020-11-10 21:00 | 7558 |  |  | 0
2020-11-10 22:00 | 7559 |  |  | 0
2020-11-10 23:00 | 7560 |  |  | 0
2020-11-11 | 7561 |  |  | 0
2020-11-11 01:00 | 7562 |  |  | 0
2020-11-11 02:00 | 7563 |  |  | 0
2020-11-11 03:00 | 7564 |  |  | 0
2020-11-11 04:00 | 7565 |  |  | 0
2020-11-11 05:00 | 7566 |  |  | 0
2020-11-11 06:00 | 7567 |  |  | 0
2020-11-11 07:00 | 7568 |  |  | 0.072775
2020-11-11 08:00 | 7569 |  |  | 0.22825
2020-11-11 09:00 | 7570 |  |  | 0.38042
2020-11-11 10:00 | 7571 |  |  | 0.43996
2020-11-11 11:00 | 7572 |  |  | 0.46477
2020-11-11 12:00 | 7573 |  |  | 0.42177
2020-11-11 13:00 | 7574 |  |  | 0.23817
2020-11-11 14:00 | 7575 |  |  | 0.074429
2020-11-11 15:00 | 7576 |  |  | 0.004962
2020-11-11 16:00 | 7577 |  |  | 0
2020-11-11 17:00 | 7578 |  |  | 0
2020-11-11 18:00 | 7579 |  |  | 0
2020-11-11 19:00 | 7580 |  |  | 0
2020-11-11 20:00 | 7581 |  |  | 0
2020-11-11 21:00 | 7582 |  |  | 0
2020-11-11 22:00 | 7583 |  |  | 0
2020-11-11 23:00 | 7584 |  |  | 0
2020-11-12 | 7585 |  |  | 0
2020-11-12 01:00 | 7586 |  |  | 0
2020-11-12 02:00 | 7587 |  |  | 0
2020-11-12 03:00 | 7588 |  |  | 0
2020-11-12 04:00 | 7589 |  |  | 0
2020-11-12 05:00 | 7590 |  |  | 0
2020-11-12 06:00 | 7591 |  |  | 0
2020-11-12 07:00 | 7592 |  |  | 0
2020-11-12 08:00 | 7593 |  |  | 0.019848
2020-11-12 09:00 | 7594 |  |  | 0.05789
2020-11-12 10:00 | 7595 |  |  | 0.10255
2020-11-12 11:00 | 7596 |  |  | 0.064505
2020-11-12 12:00 | 7597 |  |  | 0.043004
2020-11-12 13:00 | 7598 |  |  | 0.029772
2020-11-12 14:00 | 7599 |  |  | 0
2020-11-12 15:00 | 7600 |  |  | 0
2020-11-12 16:00 | 7601 |  |  | 0
2020-11-12 17:00 | 7602 |  |  | 0
2020-11-12 18:00 | 7603 |  |  | 0
2020-11-12 19:00 | 7604 |  |  | 0
2020-11-12 20:00 | 7605 |  |  | 0
2020-11-12 21:00 | 7606 |  |  | 0
2020-11-12 22:00 | 7607 |  |  | 0
2020-11-12 23:00 | 7608 |  |  | 0
2020-11-13 | 7609 |  |  | 0
2020-11-13 01:00 | 7610 |  |  | 0
2020-11-13 02:00 | 7611 |  |  | 0
2020-11-13 03:00 | 7612 |  |  | 0
2020-11-13 04:00 | 7613 |  |  | 0
2020-11-13 05:00 | 7614 |  |  | 0
2020-11-13 06:00 | 7615 |  |  | 0
2020-11-13 07:00 | 7616 |  |  | 0
2020-11-13 08:00 | 7617 |  |  | 0
2020-11-13 09:00 | 7618 |  |  | 0
2020-11-13 10:00 | 7619 |  |  | 0.019848
2020-11-13 11:00 | 7620 |  |  | 0.026464
2020-11-13 12:00 | 7621 |  |  | 0.052928
2020-11-13 13:00 | 7622 |  |  | 0.05789
2020-11-13 14:00 | 7623 |  |  | 0.034734
2020-11-13 15:00 | 7624 |  |  | 0
2020-11-13 16:00 | 7625 |  |  | 0
2020-11-13 17:00 | 7626 |  |  | 0
2020-11-13 18:00 | 7627 |  |  | 0
2020-11-13 19:00 | 7628 |  |  | 0
2020-11-13 20:00 | 7629 |  |  | 0
2020-11-13 21:00 | 7630 |  |  | 0
2020-11-13 22:00 | 7631 |  |  | 0
2020-11-13 23:00 | 7632 |  |  | 0
2020-11-14 | 7633 |  |  | 0
2020-11-14 01:00 | 7634 |  |  | 0
2020-11-14 02:00 | 7635 |  |  | 0
2020-11-14 03:00 | 7636 |  |  | 0
2020-11-14 04:00 | 7637 |  |  | 0
2020-11-14 05:00 | 7638 |  |  | 0
2020-11-14 06:00 | 7639 |  |  | 0
2020-11-14 07:00 | 7640 |  |  | 0.051274
2020-11-14 08:00 | 7641 |  |  | 0.21336
2020-11-14 09:00 | 7642 |  |  | 0.35561
2020-11-14 10:00 | 7643 |  |  | 0.43831
2020-11-14 11:00 | 7644 |  |  | 0.45154
2020-11-14 12:00 | 7645 |  |  | 0.42507
2020-11-14 13:00 | 7646 |  |  | 0.31591
2020-11-14 14:00 | 7647 |  |  | 0.14886
2020-11-14 15:00 | 7648 |  |  | 0.013232
2020-11-14 16:00 | 7649 |  |  | 0
2020-11-14 17:00 | 7650 |  |  | 0
2020-11-14 18:00 | 7651 |  |  | 0
2020-11-14 19:00 | 7652 |  |  | 0
2020-11-14 20:00 | 7653 |  |  | 0
2020-11-14 21:00 | 7654 |  |  | 0
2020-11-14 22:00 | 7655 |  |  | 0
2020-11-14 23:00 | 7656 |  |  | 0
2020-11-15 | 7657 |  |  | 0
2020-11-15 01:00 | 7658 |  |  | 0
2020-11-15 02:00 | 7659 |  |  | 0
2020-11-15 03:00 | 7660 |  |  | 0
2020-11-15 04:00 | 7661 |  |  | 0
2020-11-15 05:00 | 7662 |  |  | 0
2020-11-15 06:00 | 7663 |  |  | 0
2020-11-15 07:00 | 7664 |  |  | 0.018194
2020-11-15 08:00 | 7665 |  |  | 0.052928
2020-11-15 09:00 | 7666 |  |  | 0.064505
2020-11-15 10:00 | 7667 |  |  | 0.13728
2020-11-15 11:00 | 7668 |  |  | 0.14059
2020-11-15 12:00 | 7669 |  |  | 0.15217
2020-11-15 13:00 | 7670 |  |  | 0.11082
2020-11-15 14:00 | 7671 |  |  | 0.076083
2020-11-15 15:00 | 7672 |  |  | 0.003308
2020-11-15 16:00 | 7673 |  |  | 0
2020-11-15 17:00 | 7674 |  |  | 0
2020-11-15 18:00 | 7675 |  |  | 0
2020-11-15 19:00 | 7676 |  |  | 0
2020-11-15 20:00 | 7677 |  |  | 0
2020-11-15 21:00 | 7678 |  |  | 0
2020-11-15 22:00 | 7679 |  |  | 0
2020-11-15 23:00 | 7680 |  |  | 0
2020-11-16 | 7681 |  |  | 0
2020-11-16 01:00 | 7682 |  |  | 0
2020-11-16 02:00 | 7683 |  |  | 0
2020-11-16 03:00 | 7684 |  |  | 0
2020-11-16 04:00 | 7685 |  |  | 0
2020-11-16 05:00 | 7686 |  |  | 0
2020-11-16 06:00 | 7687 |  |  | 0
2020-11-16 07:00 | 7688 |  |  | 0.0099239
2020-11-16 08:00 | 7689 |  |  | 0.16374
2020-11-16 09:00 | 7690 |  |  | 0.32749
2020-11-16 10:00 | 7691 |  |  | 0.42507
2020-11-16 11:00 | 7692 |  |  | 0.45485
2020-11-16 12:00 | 7693 |  |  | 0.42838
2020-11-16 13:00 | 7694 |  |  | 0.31922
2020-11-16 14:00 | 7695 |  |  | 0.12074
2020-11-16 15:00 | 7696 |  |  | 0.013232
2020-11-16 16:00 | 7697 |  |  | 0
2020-11-16 17:00 | 7698 |  |  | 0
2020-11-16 18:00 | 7699 |  |  | 0
2020-11-16 19:00 | 7700 |  |  | 0
2020-11-16 20:00 | 7701 |  |  | 0
2020-11-16 21:00 | 7702 |  |  | 0
2020-11-16 22:00 | 7703 |  |  | 0
2020-11-16 23:00 | 7704 |  |  | 0
2020-11-17 | 7705 |  |  | 0
2020-11-17 01:00 | 7706 |  |  | 0
2020-11-17 02:00 | 7707 |  |  | 0
2020-11-17 03:00 | 7708 |  |  | 0
2020-11-17 04:00 | 7709 |  |  | 0
2020-11-17 05:00 | 7710 |  |  | 0
2020-11-17 06:00 | 7711 |  |  | 0
2020-11-17 07:00 | 7712 |  |  | 0.087661
2020-11-17 08:00 | 7713 |  |  | 0.23487
2020-11-17 09:00 | 7714 |  |  | 0.38372
2020-11-17 10:00 | 7715 |  |  | 0.47304
2020-11-17 11:00 | 7716 |  |  | 0.45815
2020-11-17 12:00 | 7717 |  |  | 0.41019
2020-11-17 13:00 | 7718 |  |  | 0.28945
2020-11-17 14:00 | 7719 |  |  | 0.13728
2020-11-17 15:00 | 7720 |  |  | 0.014886
2020-11-17 16:00 | 7721 |  |  | 0
2020-11-17 17:00 | 7722 |  |  | 0
2020-11-17 18:00 | 7723 |  |  | 0
2020-11-17 19:00 | 7724 |  |  | 0
2020-11-17 20:00 | 7725 |  |  | 0
2020-11-17 21:00 | 7726 |  |  | 0
2020-11-17 22:00 | 7727 |  |  | 0
2020-11-17 23:00 | 7728 |  |  | 0
2020-11-18 | 7729 |  |  | 0
2020-11-18 01:00 | 7730 |  |  | 0
2020-11-18 02:00 | 7731 |  |  | 0
2020-11-18 03:00 | 7732 |  |  | 0
2020-11-18 04:00 | 7733 |  |  | 0
2020-11-18 05:00 | 7734 |  |  | 0
2020-11-18 06:00 | 7735 |  |  | 0
2020-11-18 07:00 | 7736 |  |  | 0.076083
2020-11-18 08:00 | 7737 |  |  | 0.22825
2020-11-18 09:00 | 7738 |  |  | 0.37711
2020-11-18 10:00 | 7739 |  |  | 0.46146
2020-11-18 11:00 | 7740 |  |  | 0.48131
2020-11-18 12:00 | 7741 |  |  | 0.42177
2020-11-18 13:00 | 7742 |  |  | 0.32253
2020-11-18 14:00 | 7743 |  |  | 0.16209
2020-11-18 15:00 | 7744 |  |  | 0.011578
2020-11-18 16:00 | 7745 |  |  | 0
2020-11-18 17:00 | 7746 |  |  | 0
2020-11-18 18:00 | 7747 |  |  | 0
2020-11-18 19:00 | 7748 |  |  | 0
2020-11-18 20:00 | 7749 |  |  | 0
2020-11-18 21:00 | 7750 |  |  | 0
2020-11-18 22:00 | 7751 |  |  | 0
2020-11-18 23:00 | 7752 |  |  | 0
2020-11-19 | 7753 |  |  | 0
2020-11-19 01:00 | 7754 |  |  | 0
2020-11-19 02:00 | 7755 |  |  | 0
2020-11-19 03:00 | 7756 |  |  | 0
2020-11-19 04:00 | 7757 |  |  | 0
2020-11-19 05:00 | 7758 |  |  | 0
2020-11-19 06:00 | 7759 |  |  | 0
2020-11-19 07:00 | 7760 |  |  | 0.074429
2020-11-19 08:00 | 7761 |  |  | 0.23487
2020-11-19 09:00 | 7762 |  |  | 0.37711
2020-11-19 10:00 | 7763 |  |  | 0.45485
2020-11-19 11:00 | 7764 |  |  | 0.46808
2020-11-19 12:00 | 7765 |  |  | 0.42342
2020-11-19 13:00 | 7766 |  |  | 0.29276
2020-11-19 14:00 | 7767 |  |  | 0.10089
2020-11-19 15:00 | 7768 |  |  | 0.013232
2020-11-19 16:00 | 7769 |  |  | 0
2020-11-19 17:00 | 7770 |  |  | 0
2020-11-19 18:00 | 7771 |  |  | 0
2020-11-19 19:00 | 7772 |  |  | 0
2020-11-19 20:00 | 7773 |  |  | 0
2020-11-19 21:00 | 7774 |  |  | 0
2020-11-19 22:00 | 7775 |  |  | 0
2020-11-19 23:00 | 7776 |  |  | 0
2020-11-20 | 7777 |  |  | 0
2020-11-20 01:00 | 7778 |  |  | 0
2020-11-20 02:00 | 7779 |  |  | 0
2020-11-20 03:00 | 7780 |  |  | 0
2020-11-20 04:00 | 7781 |  |  | 0
2020-11-20 05:00 | 7782 |  |  | 0
2020-11-20 06:00 | 7783 |  |  | 0
2020-11-20 07:00 | 7784 |  |  | 0.079391
2020-11-20 08:00 | 7785 |  |  | 0.25802
2020-11-20 09:00 | 7786 |  |  | 0.41019
2020-11-20 10:00 | 7787 |  |  | 0.51604
2020-11-20 11:00 | 7788 |  |  | 0.48296
2020-11-20 12:00 | 7789 |  |  | 0.45154
2020-11-20 13:00 | 7790 |  |  | 0.32253
2020-11-20 14:00 | 7791 |  |  | 0.16871
2020-11-20 15:00 | 7792 |  |  | 0.013232
2020-11-20 16:00 | 7793 |  |  | 0
2020-11-20 17:00 | 7794 |  |  | 0
2020-11-20 18:00 | 7795 |  |  | 0
2020-11-20 19:00 | 7796 |  |  | 0
2020-11-20 20:00 | 7797 |  |  | 0
2020-11-20 21:00 | 7798 |  |  | 0
2020-11-20 22:00 | 7799 |  |  | 0
2020-11-20 23:00 | 7800 |  |  | 0
2020-11-21 | 7801 |  |  | 0
2020-11-21 01:00 | 7802 |  |  | 0
2020-11-21 02:00 | 7803 |  |  | 0
2020-11-21 03:00 | 7804 |  |  | 0
2020-11-21 04:00 | 7805 |  |  | 0
2020-11-21 05:00 | 7806 |  |  | 0
2020-11-21 06:00 | 7807 |  |  | 0
2020-11-21 07:00 | 7808 |  |  | 0.01654
2020-11-21 08:00 | 7809 |  |  | 0.043004
2020-11-21 09:00 | 7810 |  |  | 0.10916
2020-11-21 10:00 | 7811 |  |  | 0.13232
2020-11-21 11:00 | 7812 |  |  | 0.3308
2020-11-21 12:00 | 7813 |  |  | 0.3953
2020-11-21 13:00 | 7814 |  |  | 0.3093
2020-11-21 14:00 | 7815 |  |  | 0.13397
2020-11-21 15:00 | 7816 |  |  | 0
2020-11-21 16:00 | 7817 |  |  | 0
2020-11-21 17:00 | 7818 |  |  | 0
2020-11-21 18:00 | 7819 |  |  | 0
2020-11-21 19:00 | 7820 |  |  | 0
2020-11-21 20:00 | 7821 |  |  | 0
2020-11-21 21:00 | 7822 |  |  | 0
2020-11-21 22:00 | 7823 |  |  | 0
2020-11-21 23:00 | 7824 |  |  | 0
2020-11-22 | 7825 |  |  | 0
2020-11-22 01:00 | 7826 |  |  | 0
2020-11-22 02:00 | 7827 |  |  | 0
2020-11-22 03:00 | 7828 |  |  | 0
2020-11-22 04:00 | 7829 |  |  | 0
2020-11-22 05:00 | 7830 |  |  | 0
2020-11-22 06:00 | 7831 |  |  | 0
2020-11-22 07:00 | 7832 |  |  | 0.077737
2020-11-22 08:00 | 7833 |  |  | 0.24148
2020-11-22 09:00 | 7834 |  |  | 0.39199
2020-11-22 10:00 | 7835 |  |  | 0.48462
2020-11-22 11:00 | 7836 |  |  | 0.48462
2020-11-22 12:00 | 7837 |  |  | 0.43169
2020-11-22 13:00 | 7838 |  |  | 0.3126
2020-11-22 14:00 | 7839 |  |  | 0.15382
2020-11-22 15:00 | 7840 |  |  | 0.0099239
2020-11-22 16:00 | 7841 |  |  | 0
2020-11-22 17:00 | 7842 |  |  | 0
2020-11-22 18:00 | 7843 |  |  | 0
2020-11-22 19:00 | 7844 |  |  | 0
2020-11-22 20:00 | 7845 |  |  | 0
2020-11-22 21:00 | 7846 |  |  | 0
2020-11-22 22:00 | 7847 |  |  | 0
2020-11-22 23:00 | 7848 |  |  | 0
2020-11-23 | 7849 |  |  | 0
2020-11-23 01:00 | 7850 |  |  | 0
2020-11-23 02:00 | 7851 |  |  | 0
2020-11-23 03:00 | 7852 |  |  | 0
2020-11-23 04:00 | 7853 |  |  | 0
2020-11-23 05:00 | 7854 |  |  | 0
2020-11-23 06:00 | 7855 |  |  | 0
2020-11-23 07:00 | 7856 |  |  | 0.077737
2020-11-23 08:00 | 7857 |  |  | 0.23652
2020-11-23 09:00 | 7858 |  |  | 0.3738
2020-11-23 10:00 | 7859 |  |  | 0.44988
2020-11-23 11:00 | 7860 |  |  | 0.42673
2020-11-23 12:00 | 7861 |  |  | 0.4135
2020-11-23 13:00 | 7862 |  |  | 0.28283
2020-11-23 14:00 | 7863 |  |  | 0.13893
2020-11-23 15:00 | 7864 |  |  | 0.018194
2020-11-23 16:00 | 7865 |  |  | 0
2020-11-23 17:00 | 7866 |  |  | 0
2020-11-23 18:00 | 7867 |  |  | 0
2020-11-23 19:00 | 7868 |  |  | 0
2020-11-23 20:00 | 7869 |  |  | 0
2020-11-23 21:00 | 7870 |  |  | 0
2020-11-23 22:00 | 7871 |  |  | 0
2020-11-23 23:00 | 7872 |  |  | 0
2020-11-24 | 7873 |  |  | 0
2020-11-24 01:00 | 7874 |  |  | 0
2020-11-24 02:00 | 7875 |  |  | 0
2020-11-24 03:00 | 7876 |  |  | 0
2020-11-24 04:00 | 7877 |  |  | 0
2020-11-24 05:00 | 7878 |  |  | 0
2020-11-24 06:00 | 7879 |  |  | 0
2020-11-24 07:00 | 7880 |  |  | 0.043004
2020-11-24 08:00 | 7881 |  |  | 0.22494
2020-11-24 09:00 | 7882 |  |  | 0.3738
2020-11-24 10:00 | 7883 |  |  | 0.43665
2020-11-24 11:00 | 7884 |  |  | 0.42507
2020-11-24 12:00 | 7885 |  |  | 0.42011
2020-11-24 13:00 | 7886 |  |  | 0.28614
2020-11-24 14:00 | 7887 |  |  | 0.1257
2020-11-24 15:00 | 7888 |  |  | 0.0082699
2020-11-24 16:00 | 7889 |  |  | 0
2020-11-24 17:00 | 7890 |  |  | 0
2020-11-24 18:00 | 7891 |  |  | 0
2020-11-24 19:00 | 7892 |  |  | 0
2020-11-24 20:00 | 7893 |  |  | 0
2020-11-24 21:00 | 7894 |  |  | 0
2020-11-24 22:00 | 7895 |  |  | 0
2020-11-24 23:00 | 7896 |  |  | 0
2020-11-25 | 7897 |  |  | 0
2020-11-25 01:00 | 7898 |  |  | 0
2020-11-25 02:00 | 7899 |  |  | 0
2020-11-25 03:00 | 7900 |  |  | 0
2020-11-25 04:00 | 7901 |  |  | 0
2020-11-25 05:00 | 7902 |  |  | 0
2020-11-25 06:00 | 7903 |  |  | 0
2020-11-25 07:00 | 7904 |  |  | 0.044658
2020-11-25 08:00 | 7905 |  |  | 0.18855
2020-11-25 09:00 | 7906 |  |  | 0.35065
2020-11-25 10:00 | 7907 |  |  | 0.42177
2020-11-25 11:00 | 7908 |  |  | 0.4168
2020-11-25 12:00 | 7909 |  |  | 0.38703
2020-11-25 13:00 | 7910 |  |  | 0.27291
2020-11-25 14:00 | 7911 |  |  | 0.12736
2020-11-25 15:00 | 7912 |  |  | 0.0082699
2020-11-25 16:00 | 7913 |  |  | 0
2020-11-25 17:00 | 7914 |  |  | 0
2020-11-25 18:00 | 7915 |  |  | 0
2020-11-25 19:00 | 7916 |  |  | 0
2020-11-25 20:00 | 7917 |  |  | 0
2020-11-25 21:00 | 7918 |  |  | 0
2020-11-25 22:00 | 7919 |  |  | 0
2020-11-25 23:00 | 7920 |  |  | 0
2020-11-26 | 7921 |  |  | 0
2020-11-26 01:00 | 7922 |  |  | 0
2020-11-26 02:00 | 7923 |  |  | 0
2020-11-26 03:00 | 7924 |  |  | 0
2020-11-26 04:00 | 7925 |  |  | 0
2020-11-26 05:00 | 7926 |  |  | 0
2020-11-26 06:00 | 7927 |  |  | 0
2020-11-26 07:00 | 7928 |  |  | 0.054582
2020-11-26 08:00 | 7929 |  |  | 0.2084
2020-11-26 09:00 | 7930 |  |  | 0.34568
2020-11-26 10:00 | 7931 |  |  | 0.42673
2020-11-26 11:00 | 7932 |  |  | 0.42673
2020-11-26 12:00 | 7933 |  |  | 0.37545
2020-11-26 13:00 | 7934 |  |  | 0.26795
2020-11-26 14:00 | 7935 |  |  | 0.11413
2020-11-26 15:00 | 7936 |  |  | 0.0066159
2020-11-26 16:00 | 7937 |  |  | 0
2020-11-26 17:00 | 7938 |  |  | 0
2020-11-26 18:00 | 7939 |  |  | 0
2020-11-26 19:00 | 7940 |  |  | 0
2020-11-26 20:00 | 7941 |  |  | 0
2020-11-26 21:00 | 7942 |  |  | 0
2020-11-26 22:00 | 7943 |  |  | 0
2020-11-26 23:00 | 7944 |  |  | 0
2020-11-27 | 7945 |  |  | 0
2020-11-27 01:00 | 7946 |  |  | 0
2020-11-27 02:00 | 7947 |  |  | 0
2020-11-27 03:00 | 7948 |  |  | 0
2020-11-27 04:00 | 7949 |  |  | 0
2020-11-27 05:00 | 7950 |  |  | 0
2020-11-27 06:00 | 7951 |  |  | 0
2020-11-27 07:00 | 7952 |  |  | 0.034734
2020-11-27 08:00 | 7953 |  |  | 0.18194
2020-11-27 09:00 | 7954 |  |  | 0.31426
2020-11-27 10:00 | 7955 |  |  | 0.37215
2020-11-27 11:00 | 7956 |  |  | 0.35891
2020-11-27 12:00 | 7957 |  |  | 0.3093
2020-11-27 13:00 | 7958 |  |  | 0.23487
2020-11-27 14:00 | 7959 |  |  | 0.11578
2020-11-27 15:00 | 7960 |  |  | 0.0066159
2020-11-27 16:00 | 7961 |  |  | 0
2020-11-27 17:00 | 7962 |  |  | 0
2020-11-27 18:00 | 7963 |  |  | 0
2020-11-27 19:00 | 7964 |  |  | 0
2020-11-27 20:00 | 7965 |  |  | 0
2020-11-27 21:00 | 7966 |  |  | 0
2020-11-27 22:00 | 7967 |  |  | 0
2020-11-27 23:00 | 7968 |  |  | 0
2020-11-28 | 7969 |  |  | 0
2020-11-28 01:00 | 7970 |  |  | 0
2020-11-28 02:00 | 7971 |  |  | 0
2020-11-28 03:00 | 7972 |  |  | 0
2020-11-28 04:00 | 7973 |  |  | 0
2020-11-28 05:00 | 7974 |  |  | 0
2020-11-28 06:00 | 7975 |  |  | 0
2020-11-28 07:00 | 7976 |  |  | 0
2020-11-28 08:00 | 7977 |  |  | 0.011578
2020-11-28 09:00 | 7978 |  |  | 0.043004
2020-11-28 10:00 | 7979 |  |  | 0.10916
2020-11-28 11:00 | 7980 |  |  | 0.074429
2020-11-28 12:00 | 7981 |  |  | 0.12901
2020-11-28 13:00 | 7982 |  |  | 0.071121
2020-11-28 14:00 | 7983 |  |  | 0
2020-11-28 15:00 | 7984 |  |  | 0
2020-11-28 16:00 | 7985 |  |  | 0
2020-11-28 17:00 | 7986 |  |  | 0
2020-11-28 18:00 | 7987 |  |  | 0
2020-11-28 19:00 | 7988 |  |  | 0
2020-11-28 20:00 | 7989 |  |  | 0
2020-11-28 21:00 | 7990 |  |  | 0
2020-11-28 22:00 | 7991 |  |  | 0
2020-11-28 23:00 | 7992 |  |  | 0
2020-11-29 | 7993 |  |  | 0
2020-11-29 01:00 | 7994 |  |  | 0
2020-11-29 02:00 | 7995 |  |  | 0
2020-11-29 03:00 | 7996 |  |  | 0
2020-11-29 04:00 | 7997 |  |  | 0
2020-11-29 05:00 | 7998 |  |  | 0
2020-11-29 06:00 | 7999 |  |  | 0
2020-11-29 07:00 | 8000 |  |  | 0
2020-11-29 08:00 | 8001 |  |  | 0.04135
2020-11-29 09:00 | 8002 |  |  | 0.087661
2020-11-29 10:00 | 8003 |  |  | 0.14224
2020-11-29 11:00 | 8004 |  |  | 0.35561
2020-11-29 12:00 | 8005 |  |  | 0.34734
2020-11-29 13:00 | 8006 |  |  | 0.21336
2020-11-29 14:00 | 8007 |  |  | 0.1042
2020-11-29 15:00 | 8008 |  |  | 0.0082699
2020-11-29 16:00 | 8009 |  |  | 0
2020-11-29 17:00 | 8010 |  |  | 0
2020-11-29 18:00 | 8011 |  |  | 0
2020-11-29 19:00 | 8012 |  |  | 0
2020-11-29 20:00 | 8013 |  |  | 0
2020-11-29 21:00 | 8014 |  |  | 0
2020-11-29 22:00 | 8015 |  |  | 0
2020-11-29 23:00 | 8016 |  |  | 0
2020-11-30 | 8017 |  |  | 0
2020-11-30 01:00 | 8018 |  |  | 0
2020-11-30 02:00 | 8019 |  |  | 0
2020-11-30 03:00 | 8020 |  |  | 0
2020-11-30 04:00 | 8021 |  |  | 0
2020-11-30 05:00 | 8022 |  |  | 0
2020-11-30 06:00 | 8023 |  |  | 0
2020-11-30 07:00 | 8024 |  |  | 0
2020-11-30 08:00 | 8025 |  |  | 0.018194
2020-11-30 09:00 | 8026 |  |  | 0.04135
2020-11-30 10:00 | 8027 |  |  | 0.081045
2020-11-30 11:00 | 8028 |  |  | 0.099239
2020-11-30 12:00 | 8029 |  |  | 0.05789
2020-11-30 13:00 | 8030 |  |  | 0.03308
2020-11-30 14:00 | 8031 |  |  | 0
2020-11-30 15:00 | 8032 |  |  | 0
2020-11-30 16:00 | 8033 |  |  | 0
2020-11-30 17:00 | 8034 |  |  | 0
2020-11-30 18:00 | 8035 |  |  | 0
2020-11-30 19:00 | 8036 |  |  | 0
2020-11-30 20:00 | 8037 |  |  | 0
2020-11-30 21:00 | 8038 |  |  | 0
2020-11-30 22:00 | 8039 |  |  | 0
2020-11-30 23:00 | 8040 |  |  | 0
2020-12-01 | 8041 |  |  | 0
2020-12-01 01:00 | 8042 |  |  | 0
2020-12-01 02:00 | 8043 |  |  | 0
2020-12-01 03:00 | 8044 |  |  | 0
2020-12-01 04:00 | 8045 |  |  | 0
2020-12-01 05:00 | 8046 |  |  | 0
2020-12-01 06:00 | 8047 |  |  | 0
2020-12-01 07:00 | 8048 |  |  | 0
2020-12-01 08:00 | 8049 |  |  | 0.0099239
2020-12-01 09:00 | 8050 |  |  | 0.043004
2020-12-01 10:00 | 8051 |  |  | 0.043004
2020-12-01 11:00 | 8052 |  |  | 0.064505
2020-12-01 12:00 | 8053 |  |  | 0.014886
2020-12-01 13:00 | 8054 |  |  | 0
2020-12-01 14:00 | 8055 |  |  | 0
2020-12-01 15:00 | 8056 |  |  | 0
2020-12-01 16:00 | 8057 |  |  | 0
2020-12-01 17:00 | 8058 |  |  | 0
2020-12-01 18:00 | 8059 |  |  | 0
2020-12-01 19:00 | 8060 |  |  | 0
2020-12-01 20:00 | 8061 |  |  | 0
2020-12-01 21:00 | 8062 |  |  | 0
2020-12-01 22:00 | 8063 |  |  | 0
2020-12-01 23:00 | 8064 |  |  | 0
2020-12-02 | 8065 |  |  | 0
2020-12-02 01:00 | 8066 |  |  | 0
2020-12-02 02:00 | 8067 |  |  | 0
2020-12-02 03:00 | 8068 |  |  | 0
2020-12-02 04:00 | 8069 |  |  | 0
2020-12-02 05:00 | 8070 |  |  | 0
2020-12-02 06:00 | 8071 |  |  | 0
2020-12-02 07:00 | 8072 |  |  | 0
2020-12-02 08:00 | 8073 |  |  | 0.03308
2020-12-02 09:00 | 8074 |  |  | 0.089315
2020-12-02 10:00 | 8075 |  |  | 0.044658
2020-12-02 11:00 | 8076 |  |  | 0.10916
2020-12-02 12:00 | 8077 |  |  | 0.089315
2020-12-02 13:00 | 8078 |  |  | 0.029772
2020-12-02 14:00 | 8079 |  |  | 0
2020-12-02 15:00 | 8080 |  |  | 0
2020-12-02 16:00 | 8081 |  |  | 0
2020-12-02 17:00 | 8082 |  |  | 0
2020-12-02 18:00 | 8083 |  |  | 0
2020-12-02 19:00 | 8084 |  |  | 0
2020-12-02 20:00 | 8085 |  |  | 0
2020-12-02 21:00 | 8086 |  |  | 0
2020-12-02 22:00 | 8087 |  |  | 0
2020-12-02 23:00 | 8088 |  |  | 0
2020-12-03 | 8089 |  |  | 0
2020-12-03 01:00 | 8090 |  |  | 0
2020-12-03 02:00 | 8091 |  |  | 0
2020-12-03 03:00 | 8092 |  |  | 0
2020-12-03 04:00 | 8093 |  |  | 0
2020-12-03 05:00 | 8094 |  |  | 0
2020-12-03 06:00 | 8095 |  |  | 0
2020-12-03 07:00 | 8096 |  |  | 0
2020-12-03 08:00 | 8097 |  |  | 0.064505
2020-12-03 09:00 | 8098 |  |  | 0.2481
2020-12-03 10:00 | 8099 |  |  | 0.14059
2020-12-03 11:00 | 8100 |  |  | 0.16044
2020-12-03 12:00 | 8101 |  |  | 0.090969
2020-12-03 13:00 | 8102 |  |  | 0.028118
2020-12-03 14:00 | 8103 |  |  | 0
2020-12-03 15:00 | 8104 |  |  | 0
2020-12-03 16:00 | 8105 |  |  | 0
2020-12-03 17:00 | 8106 |  |  | 0
2020-12-03 18:00 | 8107 |  |  | 0
2020-12-03 19:00 | 8108 |  |  | 0
2020-12-03 20:00 | 8109 |  |  | 0
2020-12-03 21:00 | 8110 |  |  | 0
2020-12-03 22:00 | 8111 |  |  | 0
2020-12-03 23:00 | 8112 |  |  | 0
2020-12-04 | 8113 |  |  | 0
2020-12-04 01:00 | 8114 |  |  | 0
2020-12-04 02:00 | 8115 |  |  | 0
2020-12-04 03:00 | 8116 |  |  | 0
2020-12-04 04:00 | 8117 |  |  | 0
2020-12-04 05:00 | 8118 |  |  | 0
2020-12-04 06:00 | 8119 |  |  | 0
2020-12-04 07:00 | 8120 |  |  | 0
2020-12-04 08:00 | 8121 |  |  | 0
2020-12-04 09:00 | 8122 |  |  | 0
2020-12-04 10:00 | 8123 |  |  | 0
2020-12-04 11:00 | 8124 |  |  | 0
2020-12-04 12:00 | 8125 |  |  | 0
2020-12-04 13:00 | 8126 |  |  | 0
2020-12-04 14:00 | 8127 |  |  | 0
2020-12-04 15:00 | 8128 |  |  | 0
2020-12-04 16:00 | 8129 |  |  | 0
2020-12-04 17:00 | 8130 |  |  | 0
2020-12-04 18:00 | 8131 |  |  | 0
2020-12-04 19:00 | 8132 |  |  | 0
2020-12-04 20:00 | 8133 |  |  | 0
2020-12-04 21:00 | 8134 |  |  | 0
2020-12-04 22:00 | 8135 |  |  | 0
2020-12-04 23:00 | 8136 |  |  | 0
2020-12-05 | 8137 |  |  | 0
2020-12-05 01:00 | 8138 |  |  | 0
2020-12-05 02:00 | 8139 |  |  | 0
2020-12-05 03:00 | 8140 |  |  | 0
2020-12-05 04:00 | 8141 |  |  | 0
2020-12-05 05:00 | 8142 |  |  | 0
2020-12-05 06:00 | 8143 |  |  | 0
2020-12-05 07:00 | 8144 |  |  | 0
2020-12-05 08:00 | 8145 |  |  | 0
2020-12-05 09:00 | 8146 |  |  | 0
2020-12-05 10:00 | 8147 |  |  | 0.029772
2020-12-05 11:00 | 8148 |  |  | 0.04135
2020-12-05 12:00 | 8149 |  |  | 0.018194
2020-12-05 13:00 | 8150 |  |  | 0.0066159
2020-12-05 14:00 | 8151 |  |  | 0
2020-12-05 15:00 | 8152 |  |  | 0
2020-12-05 16:00 | 8153 |  |  | 0
2020-12-05 17:00 | 8154 |  |  | 0
2020-12-05 18:00 | 8155 |  |  | 0
2020-12-05 19:00 | 8156 |  |  | 0
2020-12-05 20:00 | 8157 |  |  | 0
2020-12-05 21:00 | 8158 |  |  | 0
2020-12-05 22:00 | 8159 |  |  | 0
2020-12-05 23:00 | 8160 |  |  | 0
2020-12-06 | 8161 |  |  | 0
2020-12-06 01:00 | 8162 |  |  | 0
2020-12-06 02:00 | 8163 |  |  | 0
2020-12-06 03:00 | 8164 |  |  | 0
2020-12-06 04:00 | 8165 |  |  | 0
2020-12-06 05:00 | 8166 |  |  | 0
2020-12-06 06:00 | 8167 |  |  | 0
2020-12-06 07:00 | 8168 |  |  | 0.011578
2020-12-06 08:00 | 8169 |  |  | 0.066159
2020-12-06 09:00 | 8170 |  |  | 0.052928
2020-12-06 10:00 | 8171 |  |  | 0.38538
2020-12-06 11:00 | 8172 |  |  | 0.40688
2020-12-06 12:00 | 8173 |  |  | 0.27125
2020-12-06 13:00 | 8174 |  |  | 0.1869
2020-12-06 14:00 | 8175 |  |  | 0.023156
2020-12-06 15:00 | 8176 |  |  | 0
2020-12-06 16:00 | 8177 |  |  | 0
2020-12-06 17:00 | 8178 |  |  | 0
2020-12-06 18:00 | 8179 |  |  | 0
2020-12-06 19:00 | 8180 |  |  | 0
2020-12-06 20:00 | 8181 |  |  | 0
2020-12-06 21:00 | 8182 |  |  | 0
2020-12-06 22:00 | 8183 |  |  | 0
2020-12-06 23:00 | 8184 |  |  | 0
2020-12-07 | 8185 |  |  | 0
2020-12-07 01:00 | 8186 |  |  | 0
2020-12-07 02:00 | 8187 |  |  | 0
2020-12-07 03:00 | 8188 |  |  | 0
2020-12-07 04:00 | 8189 |  |  | 0
2020-12-07 05:00 | 8190 |  |  | 0
2020-12-07 06:00 | 8191 |  |  | 0
2020-12-07 07:00 | 8192 |  |  | 0.0082699
2020-12-07 08:00 | 8193 |  |  | 0.038042
2020-12-07 09:00 | 8194 |  |  | 0.066159
2020-12-07 10:00 | 8195 |  |  | 0.077737
2020-12-07 11:00 | 8196 |  |  | 0.081045
2020-12-07 12:00 | 8197 |  |  | 0.076083
2020-12-07 13:00 | 8198 |  |  | 0.001654
2020-12-07 14:00 | 8199 |  |  | 0.011578
2020-12-07 15:00 | 8200 |  |  | 0
2020-12-07 16:00 | 8201 |  |  | 0
2020-12-07 17:00 | 8202 |  |  | 0
2020-12-07 18:00 | 8203 |  |  | 0
2020-12-07 19:00 | 8204 |  |  | 0
2020-12-07 20:00 | 8205 |  |  | 0
2020-12-07 21:00 | 8206 |  |  | 0
2020-12-07 22:00 | 8207 |  |  | 0
2020-12-07 23:00 | 8208 |  |  | 0
2020-12-08 | 8209 |  |  | 0
2020-12-08 01:00 | 8210 |  |  | 0
2020-12-08 02:00 | 8211 |  |  | 0
2020-12-08 03:00 | 8212 |  |  | 0
2020-12-08 04:00 | 8213 |  |  | 0
2020-12-08 05:00 | 8214 |  |  | 0
2020-12-08 06:00 | 8215 |  |  | 0
2020-12-08 07:00 | 8216 |  |  | 0
2020-12-08 08:00 | 8217 |  |  | 0.036388
2020-12-08 09:00 | 8218 |  |  | 0.066159
2020-12-08 10:00 | 8219 |  |  | 0.056236
2020-12-08 11:00 | 8220 |  |  | 0.1042
2020-12-08 12:00 | 8221 |  |  | 0.052928
2020-12-08 13:00 | 8222 |  |  | 0.04135
2020-12-08 14:00 | 8223 |  |  | 0.01654
2020-12-08 15:00 | 8224 |  |  | 0
2020-12-08 16:00 | 8225 |  |  | 0
2020-12-08 17:00 | 8226 |  |  | 0
2020-12-08 18:00 | 8227 |  |  | 0
2020-12-08 19:00 | 8228 |  |  | 0
2020-12-08 20:00 | 8229 |  |  | 0
2020-12-08 21:00 | 8230 |  |  | 0
2020-12-08 22:00 | 8231 |  |  | 0
2020-12-08 23:00 | 8232 |  |  | 0
2020-12-09 | 8233 |  |  | 0
2020-12-09 01:00 | 8234 |  |  | 0
2020-12-09 02:00 | 8235 |  |  | 0
2020-12-09 03:00 | 8236 |  |  | 0
2020-12-09 04:00 | 8237 |  |  | 0
2020-12-09 05:00 | 8238 |  |  | 0
2020-12-09 06:00 | 8239 |  |  | 0
2020-12-09 07:00 | 8240 |  |  | 0
2020-12-09 08:00 | 8241 |  |  | 0.029772
2020-12-09 09:00 | 8242 |  |  | 0.1042
2020-12-09 10:00 | 8243 |  |  | 0.13563
2020-12-09 11:00 | 8244 |  |  | 0.12901
2020-12-09 12:00 | 8245 |  |  | 0.092623
2020-12-09 13:00 | 8246 |  |  | 0.043004
2020-12-09 14:00 | 8247 |  |  | 0.0082699
2020-12-09 15:00 | 8248 |  |  | 0
2020-12-09 16:00 | 8249 |  |  | 0
2020-12-09 17:00 | 8250 |  |  | 0
2020-12-09 18:00 | 8251 |  |  | 0
2020-12-09 19:00 | 8252 |  |  | 0
2020-12-09 20:00 | 8253 |  |  | 0
2020-12-09 21:00 | 8254 |  |  | 0
2020-12-09 22:00 | 8255 |  |  | 0
2020-12-09 23:00 | 8256 |  |  | 0
2020-12-10 | 8257 |  |  | 0
2020-12-10 01:00 | 8258 |  |  | 0
2020-12-10 02:00 | 8259 |  |  | 0
2020-12-10 03:00 | 8260 |  |  | 0
2020-12-10 04:00 | 8261 |  |  | 0
2020-12-10 05:00 | 8262 |  |  | 0
2020-12-10 06:00 | 8263 |  |  | 0
2020-12-10 07:00 | 8264 |  |  | 0
2020-12-10 08:00 | 8265 |  |  | 0.029772
2020-12-10 09:00 | 8266 |  |  | 0.12239
2020-12-10 10:00 | 8267 |  |  | 0.14224
2020-12-10 11:00 | 8268 |  |  | 0.17036
2020-12-10 12:00 | 8269 |  |  | 0.13563
2020-12-10 13:00 | 8270 |  |  | 0.071121
2020-12-10 14:00 | 8271 |  |  | 0.036388
2020-12-10 15:00 | 8272 |  |  | 0
2020-12-10 16:00 | 8273 |  |  | 0
2020-12-10 17:00 | 8274 |  |  | 0
2020-12-10 18:00 | 8275 |  |  | 0
2020-12-10 19:00 | 8276 |  |  | 0
2020-12-10 20:00 | 8277 |  |  | 0
2020-12-10 21:00 | 8278 |  |  | 0
2020-12-10 22:00 | 8279 |  |  | 0
2020-12-10 23:00 | 8280 |  |  | 0
2020-12-11 | 8281 |  |  | 0
2020-12-11 01:00 | 8282 |  |  | 0
2020-12-11 02:00 | 8283 |  |  | 0
2020-12-11 03:00 | 8284 |  |  | 0
2020-12-11 04:00 | 8285 |  |  | 0
2020-12-11 05:00 | 8286 |  |  | 0
2020-12-11 06:00 | 8287 |  |  | 0
2020-12-11 07:00 | 8288 |  |  | 0
2020-12-11 08:00 | 8289 |  |  | 0.036388
2020-12-11 09:00 | 8290 |  |  | 0.044658
2020-12-11 10:00 | 8291 |  |  | 0.069467
2020-12-11 11:00 | 8292 |  |  | 0.039696
2020-12-11 12:00 | 8293 |  |  | 0.051274
2020-12-11 13:00 | 8294 |  |  | 0.028118
2020-12-11 14:00 | 8295 |  |  | 0.0082699
2020-12-11 15:00 | 8296 |  |  | 0
2020-12-11 16:00 | 8297 |  |  | 0
2020-12-11 17:00 | 8298 |  |  | 0
2020-12-11 18:00 | 8299 |  |  | 0
2020-12-11 19:00 | 8300 |  |  | 0
2020-12-11 20:00 | 8301 |  |  | 0
2020-12-11 21:00 | 8302 |  |  | 0
2020-12-11 22:00 | 8303 |  |  | 0
2020-12-11 23:00 | 8304 |  |  | 0
2020-12-12 | 8305 |  |  | 0
2020-12-12 01:00 | 8306 |  |  | 0
2020-12-12 02:00 | 8307 |  |  | 0
2020-12-12 03:00 | 8308 |  |  | 0
2020-12-12 04:00 | 8309 |  |  | 0
2020-12-12 05:00 | 8310 |  |  | 0
2020-12-12 06:00 | 8311 |  |  | 0
2020-12-12 07:00 | 8312 |  |  | 0.031426
2020-12-12 08:00 | 8313 |  |  | 0.1439
2020-12-12 09:00 | 8314 |  |  | 0.16209
2020-12-12 10:00 | 8315 |  |  | 0.30764
2020-12-12 11:00 | 8316 |  |  | 0.31426
2020-12-12 12:00 | 8317 |  |  | 0.37049
2020-12-12 13:00 | 8318 |  |  | 0.16871
2020-12-12 14:00 | 8319 |  |  | 0.12901
2020-12-12 15:00 | 8320 |  |  | 0.0099239
2020-12-12 16:00 | 8321 |  |  | 0
2020-12-12 17:00 | 8322 |  |  | 0
2020-12-12 18:00 | 8323 |  |  | 0
2020-12-12 19:00 | 8324 |  |  | 0
2020-12-12 20:00 | 8325 |  |  | 0
2020-12-12 21:00 | 8326 |  |  | 0
2020-12-12 22:00 | 8327 |  |  | 0
2020-12-12 23:00 | 8328 |  |  | 0
2020-12-13 | 8329 |  |  | 0
2020-12-13 01:00 | 8330 |  |  | 0
2020-12-13 02:00 | 8331 |  |  | 0
2020-12-13 03:00 | 8332 |  |  | 0
2020-12-13 04:00 | 8333 |  |  | 0
2020-12-13 05:00 | 8334 |  |  | 0
2020-12-13 06:00 | 8335 |  |  | 0
2020-12-13 07:00 | 8336 |  |  | 0.029772
2020-12-13 08:00 | 8337 |  |  | 0.20013
2020-12-13 09:00 | 8338 |  |  | 0.33576
2020-12-13 10:00 | 8339 |  |  | 0.42673
2020-12-13 11:00 | 8340 |  |  | 0.42673
2020-12-13 12:00 | 8341 |  |  | 0.39696
2020-12-13 13:00 | 8342 |  |  | 0.27952
2020-12-13 14:00 | 8343 |  |  | 0.11082
2020-12-13 15:00 | 8344 |  |  | 0.001654
2020-12-13 16:00 | 8345 |  |  | 0
2020-12-13 17:00 | 8346 |  |  | 0
2020-12-13 18:00 | 8347 |  |  | 0
2020-12-13 19:00 | 8348 |  |  | 0
2020-12-13 20:00 | 8349 |  |  | 0
2020-12-13 21:00 | 8350 |  |  | 0
2020-12-13 22:00 | 8351 |  |  | 0
2020-12-13 23:00 | 8352 |  |  | 0
2020-12-14 | 8353 |  |  | 0
2020-12-14 01:00 | 8354 |  |  | 0
2020-12-14 02:00 | 8355 |  |  | 0
2020-12-14 03:00 | 8356 |  |  | 0
2020-12-14 04:00 | 8357 |  |  | 0
2020-12-14 05:00 | 8358 |  |  | 0
2020-12-14 06:00 | 8359 |  |  | 0
2020-12-14 07:00 | 8360 |  |  | 0.038042
2020-12-14 08:00 | 8361 |  |  | 0.18028
2020-12-14 09:00 | 8362 |  |  | 0.28283
2020-12-14 10:00 | 8363 |  |  | 0.31095
2020-12-14 11:00 | 8364 |  |  | 0.38042
2020-12-14 12:00 | 8365 |  |  | 0.36718
2020-12-14 13:00 | 8366 |  |  | 0.25306
2020-12-14 14:00 | 8367 |  |  | 0.10089
2020-12-14 15:00 | 8368 |  |  | 0.004962
2020-12-14 16:00 | 8369 |  |  | 0
2020-12-14 17:00 | 8370 |  |  | 0
2020-12-14 18:00 | 8371 |  |  | 0
2020-12-14 19:00 | 8372 |  |  | 0
2020-12-14 20:00 | 8373 |  |  | 0
2020-12-14 21:00 | 8374 |  |  | 0
2020-12-14 22:00 | 8375 |  |  | 0
2020-12-14 23:00 | 8376 |  |  | 0
2020-12-15 | 8377 |  |  | 0
2020-12-15 01:00 | 8378 |  |  | 0
2020-12-15 02:00 | 8379 |  |  | 0
2020-12-15 03:00 | 8380 |  |  | 0
2020-12-15 04:00 | 8381 |  |  | 0
2020-12-15 05:00 | 8382 |  |  | 0
2020-12-15 06:00 | 8383 |  |  | 0
2020-12-15 07:00 | 8384 |  |  | 0
2020-12-15 08:00 | 8385 |  |  | 0.062851
2020-12-15 09:00 | 8386 |  |  | 0.1257
2020-12-15 10:00 | 8387 |  |  | 0.15878
2020-12-15 11:00 | 8388 |  |  | 0.15878
2020-12-15 12:00 | 8389 |  |  | 0.15713
2020-12-15 13:00 | 8390 |  |  | 0.14555
2020-12-15 14:00 | 8391 |  |  | 0.047966
2020-12-15 15:00 | 8392 |  |  | 0.0082699
2020-12-15 16:00 | 8393 |  |  | 0
2020-12-15 17:00 | 8394 |  |  | 0
2020-12-15 18:00 | 8395 |  |  | 0
2020-12-15 19:00 | 8396 |  |  | 0
2020-12-15 20:00 | 8397 |  |  | 0
2020-12-15 21:00 | 8398 |  |  | 0
2020-12-15 22:00 | 8399 |  |  | 0
2020-12-15 23:00 | 8400 |  |  | 0
2020-12-16 | 8401 |  |  | 0
2020-12-16 01:00 | 8402 |  |  | 0
2020-12-16 02:00 | 8403 |  |  | 0
2020-12-16 03:00 | 8404 |  |  | 0
2020-12-16 04:00 | 8405 |  |  | 0
2020-12-16 05:00 | 8406 |  |  | 0
2020-12-16 06:00 | 8407 |  |  | 0
2020-12-16 07:00 | 8408 |  |  | 0
2020-12-16 08:00 | 8409 |  |  | 0.039696
2020-12-16 09:00 | 8410 |  |  | 0.13728
2020-12-16 10:00 | 8411 |  |  | 0.32253
2020-12-16 11:00 | 8412 |  |  | 0.20344
2020-12-16 12:00 | 8413 |  |  | 0.25968
2020-12-16 13:00 | 8414 |  |  | 0.22825
2020-12-16 14:00 | 8415 |  |  | 0.086007
2020-12-16 15:00 | 8416 |  |  | 0
2020-12-16 16:00 | 8417 |  |  | 0
2020-12-16 17:00 | 8418 |  |  | 0
2020-12-16 18:00 | 8419 |  |  | 0
2020-12-16 19:00 | 8420 |  |  | 0
2020-12-16 20:00 | 8421 |  |  | 0
2020-12-16 21:00 | 8422 |  |  | 0
2020-12-16 22:00 | 8423 |  |  | 0
2020-12-16 23:00 | 8424 |  |  | 0
2020-12-17 | 8425 |  |  | 0
2020-12-17 01:00 | 8426 |  |  | 0
2020-12-17 02:00 | 8427 |  |  | 0
2020-12-17 03:00 | 8428 |  |  | 0
2020-12-17 04:00 | 8429 |  |  | 0
2020-12-17 05:00 | 8430 |  |  | 0
2020-12-17 06:00 | 8431 |  |  | 0
2020-12-17 07:00 | 8432 |  |  | 0.018194
2020-12-17 08:00 | 8433 |  |  | 0.18028
2020-12-17 09:00 | 8434 |  |  | 0.29772
2020-12-17 10:00 | 8435 |  |  | 0.36057
2020-12-17 11:00 | 8436 |  |  | 0.41846
2020-12-17 12:00 | 8437 |  |  | 0.38538
2020-12-17 13:00 | 8438 |  |  | 0.27952
2020-12-17 14:00 | 8439 |  |  | 0.11082
2020-12-17 15:00 | 8440 |  |  | 0.004962
2020-12-17 16:00 | 8441 |  |  | 0
2020-12-17 17:00 | 8442 |  |  | 0
2020-12-17 18:00 | 8443 |  |  | 0
2020-12-17 19:00 | 8444 |  |  | 0
2020-12-17 20:00 | 8445 |  |  | 0
2020-12-17 21:00 | 8446 |  |  | 0
2020-12-17 22:00 | 8447 |  |  | 0
2020-12-17 23:00 | 8448 |  |  | 0
2020-12-18 | 8449 |  |  | 0
2020-12-18 01:00 | 8450 |  |  | 0
2020-12-18 02:00 | 8451 |  |  | 0
2020-12-18 03:00 | 8452 |  |  | 0
2020-12-18 04:00 | 8453 |  |  | 0
2020-12-18 05:00 | 8454 |  |  | 0
2020-12-18 06:00 | 8455 |  |  | 0
2020-12-18 07:00 | 8456 |  |  | 0.011578
2020-12-18 08:00 | 8457 |  |  | 0.15217
2020-12-18 09:00 | 8458 |  |  | 0.29276
2020-12-18 10:00 | 8459 |  |  | 0.39365
2020-12-18 11:00 | 8460 |  |  | 0.42673
2020-12-18 12:00 | 8461 |  |  | 0.36884
2020-12-18 13:00 | 8462 |  |  | 0.26298
2020-12-18 14:00 | 8463 |  |  | 0.10586
2020-12-18 15:00 | 8464 |  |  | 0.004962
2020-12-18 16:00 | 8465 |  |  | 0
2020-12-18 17:00 | 8466 |  |  | 0
2020-12-18 18:00 | 8467 |  |  | 0
2020-12-18 19:00 | 8468 |  |  | 0
2020-12-18 20:00 | 8469 |  |  | 0
2020-12-18 21:00 | 8470 |  |  | 0
2020-12-18 22:00 | 8471 |  |  | 0
2020-12-18 23:00 | 8472 |  |  | 0
2020-12-19 | 8473 |  |  | 0
2020-12-19 01:00 | 8474 |  |  | 0
2020-12-19 02:00 | 8475 |  |  | 0
2020-12-19 03:00 | 8476 |  |  | 0
2020-12-19 04:00 | 8477 |  |  | 0
2020-12-19 05:00 | 8478 |  |  | 0
2020-12-19 06:00 | 8479 |  |  | 0
2020-12-19 07:00 | 8480 |  |  | 0.023156
2020-12-19 08:00 | 8481 |  |  | 0.092623
2020-12-19 09:00 | 8482 |  |  | 0.25306
2020-12-19 10:00 | 8483 |  |  | 0.24479
2020-12-19 11:00 | 8484 |  |  | 0.16044
2020-12-19 12:00 | 8485 |  |  | 0.10586
2020-12-19 13:00 | 8486 |  |  | 0.066159
2020-12-19 14:00 | 8487 |  |  | 0
2020-12-19 15:00 | 8488 |  |  | 0
2020-12-19 16:00 | 8489 |  |  | 0
2020-12-19 17:00 | 8490 |  |  | 0
2020-12-19 18:00 | 8491 |  |  | 0
2020-12-19 19:00 | 8492 |  |  | 0
2020-12-19 20:00 | 8493 |  |  | 0
2020-12-19 21:00 | 8494 |  |  | 0
2020-12-19 22:00 | 8495 |  |  | 0
2020-12-19 23:00 | 8496 |  |  | 0
2020-12-20 | 8497 |  |  | 0
2020-12-20 01:00 | 8498 |  |  | 0
2020-12-20 02:00 | 8499 |  |  | 0
2020-12-20 03:00 | 8500 |  |  | 0
2020-12-20 04:00 | 8501 |  |  | 0
2020-12-20 05:00 | 8502 |  |  | 0
2020-12-20 06:00 | 8503 |  |  | 0
2020-12-20 07:00 | 8504 |  |  | 0
2020-12-20 08:00 | 8505 |  |  | 0
2020-12-20 09:00 | 8506 |  |  | 0.011578
2020-12-20 10:00 | 8507 |  |  | 0
2020-12-20 11:00 | 8508 |  |  | 0
2020-12-20 12:00 | 8509 |  |  | 0
2020-12-20 13:00 | 8510 |  |  | 0
2020-12-20 14:00 | 8511 |  |  | 0
2020-12-20 15:00 | 8512 |  |  | 0
2020-12-20 16:00 | 8513 |  |  | 0
2020-12-20 17:00 | 8514 |  |  | 0
2020-12-20 18:00 | 8515 |  |  | 0
2020-12-20 19:00 | 8516 |  |  | 0
2020-12-20 20:00 | 8517 |  |  | 0
2020-12-20 21:00 | 8518 |  |  | 0
2020-12-20 22:00 | 8519 |  |  | 0
2020-12-20 23:00 | 8520 |  |  | 0
2020-12-21 | 8521 |  |  | 0
2020-12-21 01:00 | 8522 |  |  | 0
2020-12-21 02:00 | 8523 |  |  | 0
2020-12-21 03:00 | 8524 |  |  | 0
2020-12-21 04:00 | 8525 |  |  | 0
2020-12-21 05:00 | 8526 |  |  | 0
2020-12-21 06:00 | 8527 |  |  | 0
2020-12-21 07:00 | 8528 |  |  | 0.004962
2020-12-21 08:00 | 8529 |  |  | 0.051274
2020-12-21 09:00 | 8530 |  |  | 0.21667
2020-12-21 10:00 | 8531 |  |  | 0.15547
2020-12-21 11:00 | 8532 |  |  | 0.28779
2020-12-21 12:00 | 8533 |  |  | 0.13893
2020-12-21 13:00 | 8534 |  |  | 0.13728
2020-12-21 14:00 | 8535 |  |  | 0.056236
2020-12-21 15:00 | 8536 |  |  | 0
2020-12-21 16:00 | 8537 |  |  | 0
2020-12-21 17:00 | 8538 |  |  | 0
2020-12-21 18:00 | 8539 |  |  | 0
2020-12-21 19:00 | 8540 |  |  | 0
2020-12-21 20:00 | 8541 |  |  | 0
2020-12-21 21:00 | 8542 |  |  | 0
2020-12-21 22:00 | 8543 |  |  | 0
2020-12-21 23:00 | 8544 |  |  | 0
2020-12-22 | 8545 |  |  | 0
2020-12-22 01:00 | 8546 |  |  | 0
2020-12-22 02:00 | 8547 |  |  | 0
2020-12-22 03:00 | 8548 |  |  | 0
2020-12-22 04:00 | 8549 |  |  | 0
2020-12-22 05:00 | 8550 |  |  | 0
2020-12-22 06:00 | 8551 |  |  | 0
2020-12-22 07:00 | 8552 |  |  | 0
2020-12-22 08:00 | 8553 |  |  | 0.034734
2020-12-22 09:00 | 8554 |  |  | 0.092623
2020-12-22 10:00 | 8555 |  |  | 0.2266
2020-12-22 11:00 | 8556 |  |  | 0.19848
2020-12-22 12:00 | 8557 |  |  | 0.1654
2020-12-22 13:00 | 8558 |  |  | 0.15382
2020-12-22 14:00 | 8559 |  |  | 0.056236
2020-12-22 15:00 | 8560 |  |  | 0.003308
2020-12-22 16:00 | 8561 |  |  | 0
2020-12-22 17:00 | 8562 |  |  | 0
2020-12-22 18:00 | 8563 |  |  | 0
2020-12-22 19:00 | 8564 |  |  | 0
2020-12-22 20:00 | 8565 |  |  | 0
2020-12-22 21:00 | 8566 |  |  | 0
2020-12-22 22:00 | 8567 |  |  | 0
2020-12-22 23:00 | 8568 |  |  | 0
2020-12-23 | 8569 |  |  | 0
2020-12-23 01:00 | 8570 |  |  | 0
2020-12-23 02:00 | 8571 |  |  | 0
2020-12-23 03:00 | 8572 |  |  | 0
2020-12-23 04:00 | 8573 |  |  | 0
2020-12-23 05:00 | 8574 |  |  | 0
2020-12-23 06:00 | 8575 |  |  | 0
2020-12-23 07:00 | 8576 |  |  | 0
2020-12-23 08:00 | 8577 |  |  | 0.013232
2020-12-23 09:00 | 8578 |  |  | 0.04135
2020-12-23 10:00 | 8579 |  |  | 0.081045
2020-12-23 11:00 | 8580 |  |  | 0.043004
2020-12-23 12:00 | 8581 |  |  | 0.034734
2020-12-23 13:00 | 8582 |  |  | 0.013232
2020-12-23 14:00 | 8583 |  |  | 0
2020-12-23 15:00 | 8584 |  |  | 0
2020-12-23 16:00 | 8585 |  |  | 0
2020-12-23 17:00 | 8586 |  |  | 0
2020-12-23 18:00 | 8587 |  |  | 0
2020-12-23 19:00 | 8588 |  |  | 0
2020-12-23 20:00 | 8589 |  |  | 0
2020-12-23 21:00 | 8590 |  |  | 0
2020-12-23 22:00 | 8591 |  |  | 0
2020-12-23 23:00 | 8592 |  |  | 0
2020-12-24 | 8593 |  |  | 0
2020-12-24 01:00 | 8594 |  |  | 0
2020-12-24 02:00 | 8595 |  |  | 0
2020-12-24 03:00 | 8596 |  |  | 0
2020-12-24 04:00 | 8597 |  |  | 0
2020-12-24 05:00 | 8598 |  |  | 0
2020-12-24 06:00 | 8599 |  |  | 0
2020-12-24 07:00 | 8600 |  |  | 0
2020-12-24 08:00 | 8601 |  |  | 0
2020-12-24 09:00 | 8602 |  |  | 0.011578
2020-12-24 10:00 | 8603 |  |  | 0.14555
2020-12-24 11:00 | 8604 |  |  | 0.24479
2020-12-24 12:00 | 8605 |  |  | 0.18525
2020-12-24 13:00 | 8606 |  |  | 0.034734
2020-12-24 14:00 | 8607 |  |  | 0.011578
2020-12-24 15:00 | 8608 |  |  | 0
2020-12-24 16:00 | 8609 |  |  | 0
2020-12-24 17:00 | 8610 |  |  | 0
2020-12-24 18:00 | 8611 |  |  | 0
2020-12-24 19:00 | 8612 |  |  | 0
2020-12-24 20:00 | 8613 |  |  | 0
2020-12-24 21:00 | 8614 |  |  | 0
2020-12-24 22:00 | 8615 |  |  | 0
2020-12-24 23:00 | 8616 |  |  | 0
2020-12-25 | 8617 |  |  | 0
2020-12-25 01:00 | 8618 |  |  | 0
2020-12-25 02:00 | 8619 |  |  | 0
2020-12-25 03:00 | 8620 |  |  | 0
2020-12-25 04:00 | 8621 |  |  | 0
2020-12-25 05:00 | 8622 |  |  | 0
2020-12-25 06:00 | 8623 |  |  | 0
2020-12-25 07:00 | 8624 |  |  | 0
2020-12-25 08:00 | 8625 |  |  | 0
2020-12-25 09:00 | 8626 |  |  | 0.019848
2020-12-25 10:00 | 8627 |  |  | 0.05789
2020-12-25 11:00 | 8628 |  |  | 0.24479
2020-12-25 12:00 | 8629 |  |  | 0.27456
2020-12-25 13:00 | 8630 |  |  | 0.15547
2020-12-25 14:00 | 8631 |  |  | 0.003308
2020-12-25 15:00 | 8632 |  |  | 0
2020-12-25 16:00 | 8633 |  |  | 0
2020-12-25 17:00 | 8634 |  |  | 0
2020-12-25 18:00 | 8635 |  |  | 0
2020-12-25 19:00 | 8636 |  |  | 0
2020-12-25 20:00 | 8637 |  |  | 0
2020-12-25 21:00 | 8638 |  |  | 0
2020-12-25 22:00 | 8639 |  |  | 0
2020-12-25 23:00 | 8640 |  |  | 0
2020-12-26 | 8641 |  |  | 0
2020-12-26 01:00 | 8642 |  |  | 0
2020-12-26 02:00 | 8643 |  |  | 0
2020-12-26 03:00 | 8644 |  |  | 0
2020-12-26 04:00 | 8645 |  |  | 0
2020-12-26 05:00 | 8646 |  |  | 0
2020-12-26 06:00 | 8647 |  |  | 0
2020-12-26 07:00 | 8648 |  |  | 0.023156
2020-12-26 08:00 | 8649 |  |  | 0.19021
2020-12-26 09:00 | 8650 |  |  | 0.33411
2020-12-26 10:00 | 8651 |  |  | 0.42673
2020-12-26 11:00 | 8652 |  |  | 0.44658
2020-12-26 12:00 | 8653 |  |  | 0.41515
2020-12-26 13:00 | 8654 |  |  | 0.29441
2020-12-26 14:00 | 8655 |  |  | 0.11413
2020-12-26 15:00 | 8656 |  |  | 0.001654
2020-12-26 16:00 | 8657 |  |  | 0
2020-12-26 17:00 | 8658 |  |  | 0
2020-12-26 18:00 | 8659 |  |  | 0
2020-12-26 19:00 | 8660 |  |  | 0
2020-12-26 20:00 | 8661 |  |  | 0
2020-12-26 21:00 | 8662 |  |  | 0
2020-12-26 22:00 | 8663 |  |  | 0
2020-12-26 23:00 | 8664 |  |  | 0
2020-12-27 | 8665 |  |  | 0
2020-12-27 01:00 | 8666 |  |  | 0
2020-12-27 02:00 | 8667 |  |  | 0
2020-12-27 03:00 | 8668 |  |  | 0
2020-12-27 04:00 | 8669 |  |  | 0
2020-12-27 05:00 | 8670 |  |  | 0
2020-12-27 06:00 | 8671 |  |  | 0
2020-12-27 07:00 | 8672 |  |  | 0.026464
2020-12-27 08:00 | 8673 |  |  | 0.11743
2020-12-27 09:00 | 8674 |  |  | 0.12736
2020-12-27 10:00 | 8675 |  |  | 0.11247
2020-12-27 11:00 | 8676 |  |  | 0.17367
2020-12-27 12:00 | 8677 |  |  | 0.1439
2020-12-27 13:00 | 8678 |  |  | 0.14059
2020-12-27 14:00 | 8679 |  |  | 0.044658
2020-12-27 15:00 | 8680 |  |  | 0
2020-12-27 16:00 | 8681 |  |  | 0
2020-12-27 17:00 | 8682 |  |  | 0
2020-12-27 18:00 | 8683 |  |  | 0
2020-12-27 19:00 | 8684 |  |  | 0
2020-12-27 20:00 | 8685 |  |  | 0
2020-12-27 21:00 | 8686 |  |  | 0
2020-12-27 22:00 | 8687 |  |  | 0
2020-12-27 23:00 | 8688 |  |  | 0
2020-12-28 | 8689 |  |  | 0
2020-12-28 01:00 | 8690 |  |  | 0
2020-12-28 02:00 | 8691 |  |  | 0
2020-12-28 03:00 | 8692 |  |  | 0
2020-12-28 04:00 | 8693 |  |  | 0
2020-12-28 05:00 | 8694 |  |  | 0
2020-12-28 06:00 | 8695 |  |  | 0
2020-12-28 07:00 | 8696 |  |  | 0
2020-12-28 08:00 | 8697 |  |  | 0
2020-12-28 09:00 | 8698 |  |  | 0
2020-12-28 10:00 | 8699 |  |  | 0
2020-12-28 11:00 | 8700 |  |  | 0.011578
2020-12-28 12:00 | 8701 |  |  | 0.072775
2020-12-28 13:00 | 8702 |  |  | 0.2266
2020-12-28 14:00 | 8703 |  |  | 0.12901
2020-12-28 15:00 | 8704 |  |  | 0.0099239
2020-12-28 16:00 | 8705 |  |  | 0
2020-12-28 17:00 | 8706 |  |  | 0
2020-12-28 18:00 | 8707 |  |  | 0
2020-12-28 19:00 | 8708 |  |  | 0
2020-12-28 20:00 | 8709 |  |  | 0
2020-12-28 21:00 | 8710 |  |  | 0
2020-12-28 22:00 | 8711 |  |  | 0
2020-12-28 23:00 | 8712 |  |  | 0
2020-12-29 | 8713 |  |  | 0
2020-12-29 01:00 | 8714 |  |  | 0
2020-12-29 02:00 | 8715 |  |  | 0
2020-12-29 03:00 | 8716 |  |  | 0
2020-12-29 04:00 | 8717 |  |  | 0
2020-12-29 05:00 | 8718 |  |  | 0
2020-12-29 06:00 | 8719 |  |  | 0
2020-12-29 07:00 | 8720 |  |  | 0
2020-12-29 08:00 | 8721 |  |  | 0.054582
2020-12-29 09:00 | 8722 |  |  | 0.23487
2020-12-29 10:00 | 8723 |  |  | 0.18028
2020-12-29 11:00 | 8724 |  |  | 0.16209
2020-12-29 12:00 | 8725 |  |  | 0.17367
2020-12-29 13:00 | 8726 |  |  | 0.24314
2020-12-29 14:00 | 8727 |  |  | 0.11743
2020-12-29 15:00 | 8728 |  |  | 0.0099239
2020-12-29 16:00 | 8729 |  |  | 0
2020-12-29 17:00 | 8730 |  |  | 0
2020-12-29 18:00 | 8731 |  |  | 0
2020-12-29 19:00 | 8732 |  |  | 0
2020-12-29 20:00 | 8733 |  |  | 0
2020-12-29 21:00 | 8734 |  |  | 0
2020-12-29 22:00 | 8735 |  |  | 0
2020-12-29 23:00 | 8736 |  |  | 0
2020-12-30 | 8737 |  |  | 0
2020-12-30 01:00 | 8738 |  |  | 0
2020-12-30 02:00 | 8739 |  |  | 0
2020-12-30 03:00 | 8740 |  |  | 0
2020-12-30 04:00 | 8741 |  |  | 0
2020-12-30 05:00 | 8742 |  |  | 0
2020-12-30 06:00 | 8743 |  |  | 0
2020-12-30 07:00 | 8744 |  |  | 0
2020-12-30 08:00 | 8745 |  |  | 0.003308
2020-12-30 09:00 | 8746 |  |  | 0.2266
2020-12-30 10:00 | 8747 |  |  | 0.31426
2020-12-30 11:00 | 8748 |  |  | 0.42177
2020-12-30 12:00 | 8749 |  |  | 0.41515
2020-12-30 13:00 | 8750 |  |  | 0.29606
2020-12-30 14:00 | 8751 |  |  | 0.1472
2020-12-30 15:00 | 8752 |  |  | 0.011578
2020-12-30 16:00 | 8753 |  |  | 0
2020-12-30 17:00 | 8754 |  |  | 0
2020-12-30 18:00 | 8755 |  |  | 0
2020-12-30 19:00 | 8756 |  |  | 0
2020-12-30 20:00 | 8757 |  |  | 0
2020-12-30 21:00 | 8758 |  |  | 0
2020-12-30 22:00 | 8759 |  |  | 0
2020-12-30 23:00 | 8760 |  |  | 0
2020-12-31
2020-12-31 01:00
2020-12-31 02:00
2020-12-31 03:00
2020-12-31 04:00
2020-12-31 05:00
2020-12-31 06:00
2020-12-31 07:00
2020-12-31 08:00
2020-12-31 09:00
2020-12-31 10:00
2020-12-31 11:00
2020-12-31 12:00
2020-12-31 13:00
2020-12-31 14:00
2020-12-31 15:00
2020-12-31 16:00
2020-12-31 17:00
2020-12-31 18:00
2020-12-31 19:00
2020-12-31 20:00
2020-12-31 21:00
2020-12-31 22:00
2020-12-31 23:00

## Turin2019
Time | Hour of the year | Raw PV power measurements (facultative) | Normalized PV power [0-1] (faculative) | Normalized PV power corrected
2019-01-01 | 1 |  |  | 0
2019-01-01 01:00 | 2 |  |  | 0
2019-01-01 02:00 | 3 |  |  | 0
2019-01-01 03:00 | 4 |  |  | 0
2019-01-01 04:00 | 5 |  |  | 0
2019-01-01 05:00 | 6 |  |  | 0
2019-01-01 06:00 | 7 |  |  | 0
2019-01-01 07:00 | 8 |  |  | 0
2019-01-01 08:00 | 9 |  |  | 0.0075013
2019-01-01 09:00 | 10 |  |  | 0.056093
2019-01-01 10:00 | 11 |  |  | 0.13736
2019-01-01 11:00 | 12 |  |  | 0.27063
2019-01-01 12:00 | 13 |  |  | 0.40098
2019-01-01 13:00 | 14 |  |  | 0.36481
2019-01-01 14:00 | 15 |  |  | 0.27946
2019-01-01 15:00 | 16 |  |  | 0.13694
2019-01-01 16:00 | 17 |  |  | 0.026338
2019-01-01 17:00 | 18 |  |  | 0
2019-01-01 18:00 | 19 |  |  | 0
2019-01-01 19:00 | 20 |  |  | 0
2019-01-01 20:00 | 21 |  |  | 0
2019-01-01 21:00 | 22 |  |  | 0
2019-01-01 22:00 | 23 |  |  | 0
2019-01-01 23:00 | 24 |  |  | 0
2019-01-02 | 25 |  |  | 0
2019-01-02 01:00 | 26 |  |  | 0
2019-01-02 02:00 | 27 |  |  | 0
2019-01-02 03:00 | 28 |  |  | 0
2019-01-02 04:00 | 29 |  |  | 0
2019-01-02 05:00 | 30 |  |  | 0
2019-01-02 06:00 | 31 |  |  | 0
2019-01-02 07:00 | 32 |  |  | 0
2019-01-02 08:00 | 33 |  |  | 0.017336
2019-01-02 09:00 | 34 |  |  | 0.092765
2019-01-02 10:00 | 35 |  |  | 0.32705
2019-01-02 11:00 | 36 |  |  | 0.44841
2019-01-02 12:00 | 37 |  |  | 0.4735
2019-01-02 13:00 | 38 |  |  | 0.44107
2019-01-02 14:00 | 39 |  |  | 0.3168
2019-01-02 15:00 | 40 |  |  | 0.15994
2019-01-02 16:00 | 41 |  |  | 0.030422
2019-01-02 17:00 | 42 |  |  | 0
2019-01-02 18:00 | 43 |  |  | 0
2019-01-02 19:00 | 44 |  |  | 0
2019-01-02 20:00 | 45 |  |  | 0
2019-01-02 21:00 | 46 |  |  | 0
2019-01-02 22:00 | 47 |  |  | 0
2019-01-02 23:00 | 48 |  |  | 0
2019-01-03 | 49 |  |  | 0
2019-01-03 01:00 | 50 |  |  | 0
2019-01-03 02:00 | 51 |  |  | 0
2019-01-03 03:00 | 52 |  |  | 0
2019-01-03 04:00 | 53 |  |  | 0
2019-01-03 05:00 | 54 |  |  | 0
2019-01-03 06:00 | 55 |  |  | 0
2019-01-03 07:00 | 56 |  |  | 0
2019-01-03 08:00 | 57 |  |  | 0.026421
2019-01-03 09:00 | 58 |  |  | 0.18928
2019-01-03 10:00 | 59 |  |  | 0.36931
2019-01-03 11:00 | 60 |  |  | 0.45983
2019-01-03 12:00 | 61 |  |  | 0.47891
2019-01-03 13:00 | 62 |  |  | 0.45641
2019-01-03 14:00 | 63 |  |  | 0.33989
2019-01-03 15:00 | 64 |  |  | 0.18161
2019-01-03 16:00 | 65 |  |  | 0.036839
2019-01-03 17:00 | 66 |  |  | 0
2019-01-03 18:00 | 67 |  |  | 0
2019-01-03 19:00 | 68 |  |  | 0
2019-01-03 20:00 | 69 |  |  | 0
2019-01-03 21:00 | 70 |  |  | 0
2019-01-03 22:00 | 71 |  |  | 0
2019-01-03 23:00 | 72 |  |  | 0
2019-01-04 | 73 |  |  | 0
2019-01-04 01:00 | 74 |  |  | 0
2019-01-04 02:00 | 75 |  |  | 0
2019-01-04 03:00 | 76 |  |  | 0
2019-01-04 04:00 | 77 |  |  | 0
2019-01-04 05:00 | 78 |  |  | 0
2019-01-04 06:00 | 79 |  |  | 0
2019-01-04 07:00 | 80 |  |  | 0
2019-01-04 08:00 | 81 |  |  | 0.028255
2019-01-04 09:00 | 82 |  |  | 0.14119
2019-01-04 10:00 | 83 |  |  | 0.19478
2019-01-04 11:00 | 84 |  |  | 0.27746
2019-01-04 12:00 | 85 |  |  | 0.39073
2019-01-04 13:00 | 86 |  |  | 0.32755
2019-01-04 14:00 | 87 |  |  | 0.23671
2019-01-04 15:00 | 88 |  |  | 0.15961
2019-01-04 16:00 | 89 |  |  | 0.028505
2019-01-04 17:00 | 90 |  |  | 0
2019-01-04 18:00 | 91 |  |  | 0
2019-01-04 19:00 | 92 |  |  | 0
2019-01-04 20:00 | 93 |  |  | 0
2019-01-04 21:00 | 94 |  |  | 0
2019-01-04 22:00 | 95 |  |  | 0
2019-01-04 23:00 | 96 |  |  | 0
2019-01-05 | 97 |  |  | 0
2019-01-05 01:00 | 98 |  |  | 0
2019-01-05 02:00 | 99 |  |  | 0
2019-01-05 03:00 | 100 |  |  | 0
2019-01-05 04:00 | 101 |  |  | 0
2019-01-05 05:00 | 102 |  |  | 0
2019-01-05 06:00 | 103 |  |  | 0
2019-01-05 07:00 | 104 |  |  | 0
2019-01-05 08:00 | 105 |  |  | 0.0045841
2019-01-05 09:00 | 106 |  |  | 0.11494
2019-01-05 10:00 | 107 |  |  | 0.35114
2019-01-05 11:00 | 108 |  |  | 0.45016
2019-01-05 12:00 | 109 |  |  | 0.472
2019-01-05 13:00 | 110 |  |  | 0.44941
2019-01-05 14:00 | 111 |  |  | 0.32205
2019-01-05 15:00 | 112 |  |  | 0.17178
2019-01-05 16:00 | 113 |  |  | 0.034839
2019-01-05 17:00 | 114 |  |  | 0
2019-01-05 18:00 | 115 |  |  | 0
2019-01-05 19:00 | 116 |  |  | 0
2019-01-05 20:00 | 117 |  |  | 0
2019-01-05 21:00 | 118 |  |  | 0
2019-01-05 22:00 | 119 |  |  | 0
2019-01-05 23:00 | 120 |  |  | 0
2019-01-06 | 121 |  |  | 0
2019-01-06 01:00 | 122 |  |  | 0
2019-01-06 02:00 | 123 |  |  | 0
2019-01-06 03:00 | 124 |  |  | 0
2019-01-06 04:00 | 125 |  |  | 0
2019-01-06 05:00 | 126 |  |  | 0
2019-01-06 06:00 | 127 |  |  | 0
2019-01-06 07:00 | 128 |  |  | 0
2019-01-06 08:00 | 129 |  |  | 0.025421
2019-01-06 09:00 | 130 |  |  | 0.1847
2019-01-06 10:00 | 131 |  |  | 0.36431
2019-01-06 11:00 | 132 |  |  | 0.46433
2019-01-06 12:00 | 133 |  |  | 0.48358
2019-01-06 13:00 | 134 |  |  | 0.46483
2019-01-06 14:00 | 135 |  |  | 0.33772
2019-01-06 15:00 | 136 |  |  | 0.18528
2019-01-06 16:00 | 137 |  |  | 0.039673
2019-01-06 17:00 | 138 |  |  | 0
2019-01-06 18:00 | 139 |  |  | 0
2019-01-06 19:00 | 140 |  |  | 0
2019-01-06 20:00 | 141 |  |  | 0
2019-01-06 21:00 | 142 |  |  | 0
2019-01-06 22:00 | 143 |  |  | 0
2019-01-06 23:00 | 144 |  |  | 0
2019-01-07 | 145 |  |  | 0
2019-01-07 01:00 | 146 |  |  | 0
2019-01-07 02:00 | 147 |  |  | 0
2019-01-07 03:00 | 148 |  |  | 0
2019-01-07 04:00 | 149 |  |  | 0
2019-01-07 05:00 | 150 |  |  | 0
2019-01-07 06:00 | 151 |  |  | 0
2019-01-07 07:00 | 152 |  |  | 0
2019-01-07 08:00 | 153 |  |  | 0.024754
2019-01-07 09:00 | 154 |  |  | 0.18528
2019-01-07 10:00 | 155 |  |  | 0.36356
2019-01-07 11:00 | 156 |  |  | 0.46083
2019-01-07 12:00 | 157 |  |  | 0.4735
2019-01-07 13:00 | 158 |  |  | 0.46058
2019-01-07 14:00 | 159 |  |  | 0.34764
2019-01-07 15:00 | 160 |  |  | 0.1822
2019-01-07 16:00 | 161 |  |  | 0.03784
2019-01-07 17:00 | 162 |  |  | 8.3347e-05
2019-01-07 18:00 | 163 |  |  | 0
2019-01-07 19:00 | 164 |  |  | 0
2019-01-07 20:00 | 165 |  |  | 0
2019-01-07 21:00 | 166 |  |  | 0
2019-01-07 22:00 | 167 |  |  | 0
2019-01-07 23:00 | 168 |  |  | 0
2019-01-08 | 169 |  |  | 0
2019-01-08 01:00 | 170 |  |  | 0
2019-01-08 02:00 | 171 |  |  | 0
2019-01-08 03:00 | 172 |  |  | 0
2019-01-08 04:00 | 173 |  |  | 0
2019-01-08 05:00 | 174 |  |  | 0
2019-01-08 06:00 | 175 |  |  | 0
2019-01-08 07:00 | 176 |  |  | 0
2019-01-08 08:00 | 177 |  |  | 0.015419
2019-01-08 09:00 | 178 |  |  | 0.067178
2019-01-08 10:00 | 179 |  |  | 0.19512
2019-01-08 11:00 | 180 |  |  | 0.34581
2019-01-08 12:00 | 181 |  |  | 0.25171
2019-01-08 13:00 | 182 |  |  | 0.25046
2019-01-08 14:00 | 183 |  |  | 0.31705
2019-01-08 15:00 | 184 |  |  | 0.14269
2019-01-08 16:00 | 185 |  |  | 0.033756
2019-01-08 17:00 | 186 |  |  | 0
2019-01-08 18:00 | 187 |  |  | 0
2019-01-08 19:00 | 188 |  |  | 0
2019-01-08 20:00 | 189 |  |  | 0
2019-01-08 21:00 | 190 |  |  | 0
2019-01-08 22:00 | 191 |  |  | 0
2019-01-08 23:00 | 192 |  |  | 0
2019-01-09 | 193 |  |  | 0
2019-01-09 01:00 | 194 |  |  | 0
2019-01-09 02:00 | 195 |  |  | 0
2019-01-09 03:00 | 196 |  |  | 0
2019-01-09 04:00 | 197 |  |  | 0
2019-01-09 05:00 | 198 |  |  | 0
2019-01-09 06:00 | 199 |  |  | 0
2019-01-09 07:00 | 200 |  |  | 0
2019-01-09 08:00 | 201 |  |  | 0.019337
2019-01-09 09:00 | 202 |  |  | 0.17086
2019-01-09 10:00 | 203 |  |  | 0.35614
2019-01-09 11:00 | 204 |  |  | 0.45249
2019-01-09 12:00 | 205 |  |  | 0.3133
2019-01-09 13:00 | 206 |  |  | 0.49025
2019-01-09 14:00 | 207 |  |  | 0.38231
2019-01-09 15:00 | 208 |  |  | 0.22562
2019-01-09 16:00 | 209 |  |  | 0.053676
2019-01-09 17:00 | 210 |  |  | 0
2019-01-09 18:00 | 211 |  |  | 0
2019-01-09 19:00 | 212 |  |  | 0
2019-01-09 20:00 | 213 |  |  | 0
2019-01-09 21:00 | 214 |  |  | 0
2019-01-09 22:00 | 215 |  |  | 0
2019-01-09 23:00 | 216 |  |  | 0
2019-01-10 | 217 |  |  | 0
2019-01-10 01:00 | 218 |  |  | 0
2019-01-10 02:00 | 219 |  |  | 0
2019-01-10 03:00 | 220 |  |  | 0
2019-01-10 04:00 | 221 |  |  | 0
2019-01-10 05:00 | 222 |  |  | 0
2019-01-10 06:00 | 223 |  |  | 0
2019-01-10 07:00 | 224 |  |  | 0
2019-01-10 08:00 | 225 |  |  | 0.015753
2019-01-10 09:00 | 226 |  |  | 0.19312
2019-01-10 10:00 | 227 |  |  | 0.37931
2019-01-10 11:00 | 228 |  |  | 0.49625
2019-01-10 12:00 | 229 |  |  | 0.50917
2019-01-10 13:00 | 230 |  |  | 0.50025
2019-01-10 14:00 | 231 |  |  | 0.37465
2019-01-10 15:00 | 232 |  |  | 0.2187
2019-01-10 16:00 | 233 |  |  | 0.050925
2019-01-10 17:00 | 234 |  |  | 8.3347e-05
2019-01-10 18:00 | 235 |  |  | 0
2019-01-10 19:00 | 236 |  |  | 0
2019-01-10 20:00 | 237 |  |  | 0
2019-01-10 21:00 | 238 |  |  | 0
2019-01-10 22:00 | 239 |  |  | 0
2019-01-10 23:00 | 240 |  |  | 0
2019-01-11 | 241 |  |  | 0
2019-01-11 01:00 | 242 |  |  | 0
2019-01-11 02:00 | 243 |  |  | 0
2019-01-11 03:00 | 244 |  |  | 0
2019-01-11 04:00 | 245 |  |  | 0
2019-01-11 05:00 | 246 |  |  | 0
2019-01-11 06:00 | 247 |  |  | 0
2019-01-11 07:00 | 248 |  |  | 0
2019-01-11 08:00 | 249 |  |  | 0.025421
2019-01-11 09:00 | 250 |  |  | 0.19053
2019-01-11 10:00 | 251 |  |  | 0.37673
2019-01-11 11:00 | 252 |  |  | 0.487
2019-01-11 12:00 | 253 |  |  | 0.493
2019-01-11 13:00 | 254 |  |  | 0.46624
2019-01-11 14:00 | 255 |  |  | 0.36406
2019-01-11 15:00 | 256 |  |  | 0.15619
2019-01-11 16:00 | 257 |  |  | 0.031172
2019-01-11 17:00 | 258 |  |  | 8.3347e-05
2019-01-11 18:00 | 259 |  |  | 0
2019-01-11 19:00 | 260 |  |  | 0
2019-01-11 20:00 | 261 |  |  | 0
2019-01-11 21:00 | 262 |  |  | 0
2019-01-11 22:00 | 263 |  |  | 0
2019-01-11 23:00 | 264 |  |  | 0
2019-01-12 | 265 |  |  | 0
2019-01-12 01:00 | 266 |  |  | 0
2019-01-12 02:00 | 267 |  |  | 0
2019-01-12 03:00 | 268 |  |  | 0
2019-01-12 04:00 | 269 |  |  | 0
2019-01-12 05:00 | 270 |  |  | 0
2019-01-12 06:00 | 271 |  |  | 0
2019-01-12 07:00 | 272 |  |  | 0
2019-01-12 08:00 | 273 |  |  | 0.016503
2019-01-12 09:00 | 274 |  |  | 0.13927
2019-01-12 10:00 | 275 |  |  | 0.37306
2019-01-12 11:00 | 276 |  |  | 0.44324
2019-01-12 12:00 | 277 |  |  | 0.51617
2019-01-12 13:00 | 278 |  |  | 0.48491
2019-01-12 14:00 | 279 |  |  | 0.36689
2019-01-12 15:00 | 280 |  |  | 0.21212
2019-01-12 16:00 | 281 |  |  | 0.050508
2019-01-12 17:00 | 282 |  |  | 0.00016669
2019-01-12 18:00 | 283 |  |  | 0
2019-01-12 19:00 | 284 |  |  | 0
2019-01-12 20:00 | 285 |  |  | 0
2019-01-12 21:00 | 286 |  |  | 0
2019-01-12 22:00 | 287 |  |  | 0
2019-01-12 23:00 | 288 |  |  | 0
2019-01-13 | 289 |  |  | 0
2019-01-13 01:00 | 290 |  |  | 0
2019-01-13 02:00 | 291 |  |  | 0
2019-01-13 03:00 | 292 |  |  | 0
2019-01-13 04:00 | 293 |  |  | 0
2019-01-13 05:00 | 294 |  |  | 0
2019-01-13 06:00 | 295 |  |  | 0
2019-01-13 07:00 | 296 |  |  | 0
2019-01-13 08:00 | 297 |  |  | 0.025754
2019-01-13 09:00 | 298 |  |  | 0.16836
2019-01-13 10:00 | 299 |  |  | 0.35914
2019-01-13 11:00 | 300 |  |  | 0.48825
2019-01-13 12:00 | 301 |  |  | 0.48325
2019-01-13 13:00 | 302 |  |  | 0.40348
2019-01-13 14:00 | 303 |  |  | 0.32089
2019-01-13 15:00 | 304 |  |  | 0.1962
2019-01-13 16:00 | 305 |  |  | 0.041757
2019-01-13 17:00 | 306 |  |  | 0
2019-01-13 18:00 | 307 |  |  | 0
2019-01-13 19:00 | 308 |  |  | 0
2019-01-13 20:00 | 309 |  |  | 0
2019-01-13 21:00 | 310 |  |  | 0
2019-01-13 22:00 | 311 |  |  | 0
2019-01-13 23:00 | 312 |  |  | 0
2019-01-14 | 313 |  |  | 0
2019-01-14 01:00 | 314 |  |  | 0
2019-01-14 02:00 | 315 |  |  | 0
2019-01-14 03:00 | 316 |  |  | 0
2019-01-14 04:00 | 317 |  |  | 0
2019-01-14 05:00 | 318 |  |  | 0
2019-01-14 06:00 | 319 |  |  | 0
2019-01-14 07:00 | 320 |  |  | 0
2019-01-14 08:00 | 321 |  |  | 0.031339
2019-01-14 09:00 | 322 |  |  | 0.20237
2019-01-14 10:00 | 323 |  |  | 0.38581
2019-01-14 11:00 | 324 |  |  | 0.50842
2019-01-14 12:00 | 325 |  |  | 0.52625
2019-01-14 13:00 | 326 |  |  | 0.51925
2019-01-14 14:00 | 327 |  |  | 0.40548
2019-01-14 15:00 | 328 |  |  | 0.24354
2019-01-14 16:00 | 329 |  |  | 0.063761
2019-01-14 17:00 | 330 |  |  | 0.00041674
2019-01-14 18:00 | 331 |  |  | 0
2019-01-14 19:00 | 332 |  |  | 0
2019-01-14 20:00 | 333 |  |  | 0
2019-01-14 21:00 | 334 |  |  | 0
2019-01-14 22:00 | 335 |  |  | 0
2019-01-14 23:00 | 336 |  |  | 0
2019-01-15 | 337 |  |  | 0
2019-01-15 01:00 | 338 |  |  | 0
2019-01-15 02:00 | 339 |  |  | 0
2019-01-15 03:00 | 340 |  |  | 0
2019-01-15 04:00 | 341 |  |  | 0
2019-01-15 05:00 | 342 |  |  | 0
2019-01-15 06:00 | 343 |  |  | 0
2019-01-15 07:00 | 344 |  |  | 0
2019-01-15 08:00 | 345 |  |  | 0.025504
2019-01-15 09:00 | 346 |  |  | 0.19595
2019-01-15 10:00 | 347 |  |  | 0.37706
2019-01-15 11:00 | 348 |  |  | 0.50792
2019-01-15 12:00 | 349 |  |  | 0.50467
2019-01-15 13:00 | 350 |  |  | 0.49108
2019-01-15 14:00 | 351 |  |  | 0.37673
2019-01-15 15:00 | 352 |  |  | 0.23246
2019-01-15 16:00 | 353 |  |  | 0.06251
2019-01-15 17:00 | 354 |  |  | 0.00058343
2019-01-15 18:00 | 355 |  |  | 0
2019-01-15 19:00 | 356 |  |  | 0
2019-01-15 20:00 | 357 |  |  | 0
2019-01-15 21:00 | 358 |  |  | 0
2019-01-15 22:00 | 359 |  |  | 0
2019-01-15 23:00 | 360 |  |  | 0
2019-01-16 | 361 |  |  | 0
2019-01-16 01:00 | 362 |  |  | 0
2019-01-16 02:00 | 363 |  |  | 0
2019-01-16 03:00 | 364 |  |  | 0
2019-01-16 04:00 | 365 |  |  | 0
2019-01-16 05:00 | 366 |  |  | 0
2019-01-16 06:00 | 367 |  |  | 0
2019-01-16 07:00 | 368 |  |  | 0
2019-01-16 08:00 | 369 |  |  | 0.030255
2019-01-16 09:00 | 370 |  |  | 0.19145
2019-01-16 10:00 | 371 |  |  | 0.37056
2019-01-16 11:00 | 372 |  |  | 0.48625
2019-01-16 12:00 | 373 |  |  | 0.52117
2019-01-16 13:00 | 374 |  |  | 0.48941
2019-01-16 14:00 | 375 |  |  | 0.39523
2019-01-16 15:00 | 376 |  |  | 0.23937
2019-01-16 16:00 | 377 |  |  | 0.064511
2019-01-16 17:00 | 378 |  |  | 0.00050008
2019-01-16 18:00 | 379 |  |  | 0
2019-01-16 19:00 | 380 |  |  | 0
2019-01-16 20:00 | 381 |  |  | 0
2019-01-16 21:00 | 382 |  |  | 0
2019-01-16 22:00 | 383 |  |  | 0
2019-01-16 23:00 | 384 |  |  | 0
2019-01-17 | 385 |  |  | 0
2019-01-17 01:00 | 386 |  |  | 0
2019-01-17 02:00 | 387 |  |  | 0
2019-01-17 03:00 | 388 |  |  | 0
2019-01-17 04:00 | 389 |  |  | 0
2019-01-17 05:00 | 390 |  |  | 0
2019-01-17 06:00 | 391 |  |  | 0
2019-01-17 07:00 | 392 |  |  | 0
2019-01-17 08:00 | 393 |  |  | 0.025671
2019-01-17 09:00 | 394 |  |  | 0.096266
2019-01-17 10:00 | 395 |  |  | 0.3248
2019-01-17 11:00 | 396 |  |  | 0.34881
2019-01-17 12:00 | 397 |  |  | 0.36689
2019-01-17 13:00 | 398 |  |  | 0.44249
2019-01-17 14:00 | 399 |  |  | 0.34364
2019-01-17 15:00 | 400 |  |  | 0.15103
2019-01-17 16:00 | 401 |  |  | 0.049258
2019-01-17 17:00 | 402 |  |  | 0.00091682
2019-01-17 18:00 | 403 |  |  | 0
2019-01-17 19:00 | 404 |  |  | 0
2019-01-17 20:00 | 405 |  |  | 0
2019-01-17 21:00 | 406 |  |  | 0
2019-01-17 22:00 | 407 |  |  | 0
2019-01-17 23:00 | 408 |  |  | 0
2019-01-18 | 409 |  |  | 0
2019-01-18 01:00 | 410 |  |  | 0
2019-01-18 02:00 | 411 |  |  | 0
2019-01-18 03:00 | 412 |  |  | 0
2019-01-18 04:00 | 413 |  |  | 0
2019-01-18 05:00 | 414 |  |  | 0
2019-01-18 06:00 | 415 |  |  | 0
2019-01-18 07:00 | 416 |  |  | 0
2019-01-18 08:00 | 417 |  |  | 0.015003
2019-01-18 09:00 | 418 |  |  | 0.16994
2019-01-18 10:00 | 419 |  |  | 0.38573
2019-01-18 11:00 | 420 |  |  | 0.49875
2019-01-18 12:00 | 421 |  |  | 0.49667
2019-01-18 13:00 | 422 |  |  | 0.45766
2019-01-18 14:00 | 423 |  |  | 0.37198
2019-01-18 15:00 | 424 |  |  | 0.25496
2019-01-18 16:00 | 425 |  |  | 0.072929
2019-01-18 17:00 | 426 |  |  | 0.0012502
2019-01-18 18:00 | 427 |  |  | 0
2019-01-18 19:00 | 428 |  |  | 0
2019-01-18 20:00 | 429 |  |  | 0
2019-01-18 21:00 | 430 |  |  | 0
2019-01-18 22:00 | 431 |  |  | 0
2019-01-18 23:00 | 432 |  |  | 0
2019-01-19 | 433 |  |  | 0
2019-01-19 01:00 | 434 |  |  | 0
2019-01-19 02:00 | 435 |  |  | 0
2019-01-19 03:00 | 436 |  |  | 0
2019-01-19 04:00 | 437 |  |  | 0
2019-01-19 05:00 | 438 |  |  | 0
2019-01-19 06:00 | 439 |  |  | 0
2019-01-19 07:00 | 440 |  |  | 0
2019-01-19 08:00 | 441 |  |  | 0.0043341
2019-01-19 09:00 | 442 |  |  | 0.017003
2019-01-19 10:00 | 443 |  |  | 0.040257
2019-01-19 11:00 | 444 |  |  | 0.079263
2019-01-19 12:00 | 445 |  |  | 0.076929
2019-01-19 13:00 | 446 |  |  | 0.052092
2019-01-19 14:00 | 447 |  |  | 0.065094
2019-01-19 15:00 | 448 |  |  | 0.047508
2019-01-19 16:00 | 449 |  |  | 0.013586
2019-01-19 17:00 | 450 |  |  | 0
2019-01-19 18:00 | 451 |  |  | 0
2019-01-19 19:00 | 452 |  |  | 0
2019-01-19 20:00 | 453 |  |  | 0
2019-01-19 21:00 | 454 |  |  | 0
2019-01-19 22:00 | 455 |  |  | 0
2019-01-19 23:00 | 456 |  |  | 0
2019-01-20 | 457 |  |  | 0
2019-01-20 01:00 | 458 |  |  | 0
2019-01-20 02:00 | 459 |  |  | 0
2019-01-20 03:00 | 460 |  |  | 0
2019-01-20 04:00 | 461 |  |  | 0
2019-01-20 05:00 | 462 |  |  | 0
2019-01-20 06:00 | 463 |  |  | 0
2019-01-20 07:00 | 464 |  |  | 0
2019-01-20 08:00 | 465 |  |  | 0.029755
2019-01-20 09:00 | 466 |  |  | 0.16003
2019-01-20 10:00 | 467 |  |  | 0.33022
2019-01-20 11:00 | 468 |  |  | 0.47283
2019-01-20 12:00 | 469 |  |  | 0.49783
2019-01-20 13:00 | 470 |  |  | 0.45041
2019-01-20 14:00 | 471 |  |  | 0.36139
2019-01-20 15:00 | 472 |  |  | 0.23304
2019-01-20 16:00 | 473 |  |  | 0.073762
2019-01-20 17:00 | 474 |  |  | 0.0010002
2019-01-20 18:00 | 475 |  |  | 0
2019-01-20 19:00 | 476 |  |  | 0
2019-01-20 20:00 | 477 |  |  | 0
2019-01-20 21:00 | 478 |  |  | 0
2019-01-20 22:00 | 479 |  |  | 0
2019-01-20 23:00 | 480 |  |  | 0
2019-01-21 | 481 |  |  | 0
2019-01-21 01:00 | 482 |  |  | 0
2019-01-21 02:00 | 483 |  |  | 0
2019-01-21 03:00 | 484 |  |  | 0
2019-01-21 04:00 | 485 |  |  | 0
2019-01-21 05:00 | 486 |  |  | 0
2019-01-21 06:00 | 487 |  |  | 0
2019-01-21 07:00 | 488 |  |  | 0
2019-01-21 08:00 | 489 |  |  | 0.026671
2019-01-21 09:00 | 490 |  |  | 0.16269
2019-01-21 10:00 | 491 |  |  | 0.34047
2019-01-21 11:00 | 492 |  |  | 0.47225
2019-01-21 12:00 | 493 |  |  | 0.52034
2019-01-21 13:00 | 494 |  |  | 0.48191
2019-01-21 14:00 | 495 |  |  | 0.39348
2019-01-21 15:00 | 496 |  |  | 0.24721
2019-01-21 16:00 | 497 |  |  | 0.080763
2019-01-21 17:00 | 498 |  |  | 0.0014169
2019-01-21 18:00 | 499 |  |  | 0
2019-01-21 19:00 | 500 |  |  | 0
2019-01-21 20:00 | 501 |  |  | 0
2019-01-21 21:00 | 502 |  |  | 0
2019-01-21 22:00 | 503 |  |  | 0
2019-01-21 23:00 | 504 |  |  | 0
2019-01-22 | 505 |  |  | 0
2019-01-22 01:00 | 506 |  |  | 0
2019-01-22 02:00 | 507 |  |  | 0
2019-01-22 03:00 | 508 |  |  | 0
2019-01-22 04:00 | 509 |  |  | 0
2019-01-22 05:00 | 510 |  |  | 0
2019-01-22 06:00 | 511 |  |  | 0
2019-01-22 07:00 | 512 |  |  | 0
2019-01-22 08:00 | 513 |  |  | 0.036006
2019-01-22 09:00 | 514 |  |  | 0.19478
2019-01-22 10:00 | 515 |  |  | 0.37365
2019-01-22 11:00 | 516 |  |  | 0.49725
2019-01-22 12:00 | 517 |  |  | 0.54017
2019-01-22 13:00 | 518 |  |  | 0.46824
2019-01-22 14:00 | 519 |  |  | 0.37165
2019-01-22 15:00 | 520 |  |  | 0.22195
2019-01-22 16:00 | 521 |  |  | 0.076763
2019-01-22 17:00 | 522 |  |  | 0.0015003
2019-01-22 18:00 | 523 |  |  | 0
2019-01-22 19:00 | 524 |  |  | 0
2019-01-22 20:00 | 525 |  |  | 0
2019-01-22 21:00 | 526 |  |  | 0
2019-01-22 22:00 | 527 |  |  | 0
2019-01-22 23:00 | 528 |  |  | 0
2019-01-23 | 529 |  |  | 0
2019-01-23 01:00 | 530 |  |  | 0
2019-01-23 02:00 | 531 |  |  | 0
2019-01-23 03:00 | 532 |  |  | 0
2019-01-23 04:00 | 533 |  |  | 0
2019-01-23 05:00 | 534 |  |  | 0
2019-01-23 06:00 | 535 |  |  | 0
2019-01-23 07:00 | 536 |  |  | 0
2019-01-23 08:00 | 537 |  |  | 0.012919
2019-01-23 09:00 | 538 |  |  | 0.046091
2019-01-23 10:00 | 539 |  |  | 0.091015
2019-01-23 11:00 | 540 |  |  | 0.085681
2019-01-23 12:00 | 541 |  |  | 0.079013
2019-01-23 13:00 | 542 |  |  | 0.15694
2019-01-23 14:00 | 543 |  |  | 0.18636
2019-01-23 15:00 | 544 |  |  | 0.11535
2019-01-23 16:00 | 545 |  |  | 0.021754
2019-01-23 17:00 | 546 |  |  | 8.3347e-05
2019-01-23 18:00 | 547 |  |  | 0
2019-01-23 19:00 | 548 |  |  | 0
2019-01-23 20:00 | 549 |  |  | 0
2019-01-23 21:00 | 550 |  |  | 0
2019-01-23 22:00 | 551 |  |  | 0
2019-01-23 23:00 | 552 |  |  | 0
2019-01-24 | 553 |  |  | 0
2019-01-24 01:00 | 554 |  |  | 0
2019-01-24 02:00 | 555 |  |  | 0
2019-01-24 03:00 | 556 |  |  | 0
2019-01-24 04:00 | 557 |  |  | 0
2019-01-24 05:00 | 558 |  |  | 0
2019-01-24 06:00 | 559 |  |  | 0
2019-01-24 07:00 | 560 |  |  | 0
2019-01-24 08:00 | 561 |  |  | 0.0010835
2019-01-24 09:00 | 562 |  |  | 0.02067
2019-01-24 10:00 | 563 |  |  | 0.074012
2019-01-24 11:00 | 564 |  |  | 0.31514
2019-01-24 12:00 | 565 |  |  | 0.58076
2019-01-24 13:00 | 566 |  |  | 0.54051
2019-01-24 14:00 | 567 |  |  | 0.46008
2019-01-24 15:00 | 568 |  |  | 0.29047
2019-01-24 16:00 | 569 |  |  | 0.099517
2019-01-24 17:00 | 570 |  |  | 0.0020837
2019-01-24 18:00 | 571 |  |  | 0
2019-01-24 19:00 | 572 |  |  | 0
2019-01-24 20:00 | 573 |  |  | 0
2019-01-24 21:00 | 574 |  |  | 0
2019-01-24 22:00 | 575 |  |  | 0
2019-01-24 23:00 | 576 |  |  | 0
2019-01-25 | 577 |  |  | 0
2019-01-25 01:00 | 578 |  |  | 0
2019-01-25 02:00 | 579 |  |  | 0
2019-01-25 03:00 | 580 |  |  | 0
2019-01-25 04:00 | 581 |  |  | 0
2019-01-25 05:00 | 582 |  |  | 0
2019-01-25 06:00 | 583 |  |  | 0
2019-01-25 07:00 | 584 |  |  | 8.3347e-05
2019-01-25 08:00 | 585 |  |  | 0.04084
2019-01-25 09:00 | 586 |  |  | 0.22245
2019-01-25 10:00 | 587 |  |  | 0.41724
2019-01-25 11:00 | 588 |  |  | 0.55701
2019-01-25 12:00 | 589 |  |  | 0.62077
2019-01-25 13:00 | 590 |  |  | 0.56051
2019-01-25 14:00 | 591 |  |  | 0.47208
2019-01-25 15:00 | 592 |  |  | 0.30555
2019-01-25 16:00 | 593 |  |  | 0.1141
2019-01-25 17:00 | 594 |  |  | 0.0025838
2019-01-25 18:00 | 595 |  |  | 0
2019-01-25 19:00 | 596 |  |  | 0
2019-01-25 20:00 | 597 |  |  | 0
2019-01-25 21:00 | 598 |  |  | 0
2019-01-25 22:00 | 599 |  |  | 0
2019-01-25 23:00 | 600 |  |  | 0
2019-01-26 | 601 |  |  | 0
2019-01-26 01:00 | 602 |  |  | 0
2019-01-26 02:00 | 603 |  |  | 0
2019-01-26 03:00 | 604 |  |  | 0
2019-01-26 04:00 | 605 |  |  | 0
2019-01-26 05:00 | 606 |  |  | 0
2019-01-26 06:00 | 607 |  |  | 0
2019-01-26 07:00 | 608 |  |  | 0
2019-01-26 08:00 | 609 |  |  | 0.044674
2019-01-26 09:00 | 610 |  |  | 0.22462
2019-01-26 10:00 | 611 |  |  | 0.37356
2019-01-26 11:00 | 612 |  |  | 0.46441
2019-01-26 12:00 | 613 |  |  | 0.50892
2019-01-26 13:00 | 614 |  |  | 0.44432
2019-01-26 14:00 | 615 |  |  | 0.38448
2019-01-26 15:00 | 616 |  |  | 0.17578
2019-01-26 16:00 | 617 |  |  | 0.054759
2019-01-26 17:00 | 618 |  |  | 0.0034172
2019-01-26 18:00 | 619 |  |  | 0
2019-01-26 19:00 | 620 |  |  | 0
2019-01-26 20:00 | 621 |  |  | 0
2019-01-26 21:00 | 622 |  |  | 0
2019-01-26 22:00 | 623 |  |  | 0
2019-01-26 23:00 | 624 |  |  | 0
2019-01-27 | 625 |  |  | 0
2019-01-27 01:00 | 626 |  |  | 0
2019-01-27 02:00 | 627 |  |  | 0
2019-01-27 03:00 | 628 |  |  | 0
2019-01-27 04:00 | 629 |  |  | 0
2019-01-27 05:00 | 630 |  |  | 0
2019-01-27 06:00 | 631 |  |  | 0
2019-01-27 07:00 | 632 |  |  | 0
2019-01-27 08:00 | 633 |  |  | 0.015003
2019-01-27 09:00 | 634 |  |  | 0.098766
2019-01-27 10:00 | 635 |  |  | 0.11244
2019-01-27 11:00 | 636 |  |  | 0.066511
2019-01-27 12:00 | 637 |  |  | 0.049092
2019-01-27 13:00 | 638 |  |  | 0.07743
2019-01-27 14:00 | 639 |  |  | 0.06126
2019-01-27 15:00 | 640 |  |  | 0.036173
2019-01-27 16:00 | 641 |  |  | 0.012919
2019-01-27 17:00 | 642 |  |  | 0.00058343
2019-01-27 18:00 | 643 |  |  | 0
2019-01-27 19:00 | 644 |  |  | 0
2019-01-27 20:00 | 645 |  |  | 0
2019-01-27 21:00 | 646 |  |  | 0
2019-01-27 22:00 | 647 |  |  | 0
2019-01-27 23:00 | 648 |  |  | 0
2019-01-28 | 649 |  |  | 0
2019-01-28 01:00 | 650 |  |  | 0
2019-01-28 02:00 | 651 |  |  | 0
2019-01-28 03:00 | 652 |  |  | 0
2019-01-28 04:00 | 653 |  |  | 0
2019-01-28 05:00 | 654 |  |  | 0
2019-01-28 06:00 | 655 |  |  | 0
2019-01-28 07:00 | 656 |  |  | 8.3347e-05
2019-01-28 08:00 | 657 |  |  | 0.052259
2019-01-28 09:00 | 658 |  |  | 0.24729
2019-01-28 10:00 | 659 |  |  | 0.44616
2019-01-28 11:00 | 660 |  |  | 0.58118
2019-01-28 12:00 | 661 |  |  | 0.66003
2019-01-28 13:00 | 662 |  |  | 0.6166
2019-01-28 14:00 | 663 |  |  | 0.523
2019-01-28 15:00 | 664 |  |  | 0.34481
2019-01-28 16:00 | 665 |  |  | 0.14094
2019-01-28 17:00 | 666 |  |  | 0.0036673
2019-01-28 18:00 | 667 |  |  | 0
2019-01-28 19:00 | 668 |  |  | 0
2019-01-28 20:00 | 669 |  |  | 0
2019-01-28 21:00 | 670 |  |  | 0
2019-01-28 22:00 | 671 |  |  | 0
2019-01-28 23:00 | 672 |  |  | 0
2019-01-29 | 673 |  |  | 0
2019-01-29 01:00 | 674 |  |  | 0
2019-01-29 02:00 | 675 |  |  | 0
2019-01-29 03:00 | 676 |  |  | 0
2019-01-29 04:00 | 677 |  |  | 0
2019-01-29 05:00 | 678 |  |  | 0
2019-01-29 06:00 | 679 |  |  | 0
2019-01-29 07:00 | 680 |  |  | 8.3347e-05
2019-01-29 08:00 | 681 |  |  | 0.047591
2019-01-29 09:00 | 682 |  |  | 0.24204
2019-01-29 10:00 | 683 |  |  | 0.43399
2019-01-29 11:00 | 684 |  |  | 0.54459
2019-01-29 12:00 | 685 |  |  | 0.6186
2019-01-29 13:00 | 686 |  |  | 0.59768
2019-01-29 14:00 | 687 |  |  | 0.42049
2019-01-29 15:00 | 688 |  |  | 0.21129
2019-01-29 16:00 | 689 |  |  | 0.067261
2019-01-29 17:00 | 690 |  |  | 0.0045008
2019-01-29 18:00 | 691 |  |  | 0
2019-01-29 19:00 | 692 |  |  | 0
2019-01-29 20:00 | 693 |  |  | 0
2019-01-29 21:00 | 694 |  |  | 0
2019-01-29 22:00 | 695 |  |  | 0
2019-01-29 23:00 | 696 |  |  | 0
2019-01-30 | 697 |  |  | 0
2019-01-30 01:00 | 698 |  |  | 0
2019-01-30 02:00 | 699 |  |  | 0
2019-01-30 03:00 | 700 |  |  | 0
2019-01-30 04:00 | 701 |  |  | 0
2019-01-30 05:00 | 702 |  |  | 0
2019-01-30 06:00 | 703 |  |  | 0
2019-01-30 07:00 | 704 |  |  | 0
2019-01-30 08:00 | 705 |  |  | 0.031255
2019-01-30 09:00 | 706 |  |  | 0.086014
2019-01-30 10:00 | 707 |  |  | 0.070428
2019-01-30 11:00 | 708 |  |  | 0.12177
2019-01-30 12:00 | 709 |  |  | 0.27305
2019-01-30 13:00 | 710 |  |  | 0.22587
2019-01-30 14:00 | 711 |  |  | 0.22329
2019-01-30 15:00 | 712 |  |  | 0.18595
2019-01-30 16:00 | 713 |  |  | 0.096016
2019-01-30 17:00 | 714 |  |  | 0.011752
2019-01-30 18:00 | 715 |  |  | 0
2019-01-30 19:00 | 716 |  |  | 0
2019-01-30 20:00 | 717 |  |  | 0
2019-01-30 21:00 | 718 |  |  | 0
2019-01-30 22:00 | 719 |  |  | 0
2019-01-30 23:00 | 720 |  |  | 0
2019-01-31 | 721 |  |  | 0
2019-01-31 01:00 | 722 |  |  | 0
2019-01-31 02:00 | 723 |  |  | 0
2019-01-31 03:00 | 724 |  |  | 0
2019-01-31 04:00 | 725 |  |  | 0
2019-01-31 05:00 | 726 |  |  | 0
2019-01-31 06:00 | 727 |  |  | 0
2019-01-31 07:00 | 728 |  |  | 8.3347e-05
2019-01-31 08:00 | 729 |  |  | 0.024421
2019-01-31 09:00 | 730 |  |  | 0.06201
2019-01-31 10:00 | 731 |  |  | 0.20753
2019-01-31 11:00 | 732 |  |  | 0.30513
2019-01-31 12:00 | 733 |  |  | 0.27046
2019-01-31 13:00 | 734 |  |  | 0.23146
2019-01-31 14:00 | 735 |  |  | 0.34889
2019-01-31 15:00 | 736 |  |  | 0.10152
2019-01-31 16:00 | 737 |  |  | 0.034339
2019-01-31 17:00 | 738 |  |  | 0.001917
2019-01-31 18:00 | 739 |  |  | 0
2019-01-31 19:00 | 740 |  |  | 0
2019-01-31 20:00 | 741 |  |  | 0
2019-01-31 21:00 | 742 |  |  | 0
2019-01-31 22:00 | 743 |  |  | 0
2019-01-31 23:00 | 744 |  |  | 0
2019-02-01 | 745 |  |  | 0
2019-02-01 01:00 | 746 |  |  | 0
2019-02-01 02:00 | 747 |  |  | 0
2019-02-01 03:00 | 748 |  |  | 0
2019-02-01 04:00 | 749 |  |  | 0
2019-02-01 05:00 | 750 |  |  | 0
2019-02-01 06:00 | 751 |  |  | 0
2019-02-01 07:00 | 752 |  |  | 0
2019-02-01 08:00 | 753 |  |  | 0.0010002
2019-02-01 09:00 | 754 |  |  | 0.003834
2019-02-01 10:00 | 755 |  |  | 0.0095849
2019-02-01 11:00 | 756 |  |  | 0.021004
2019-02-01 12:00 | 757 |  |  | 0.029088
2019-02-01 13:00 | 758 |  |  | 0.013086
2019-02-01 14:00 | 759 |  |  | 0.01917
2019-02-01 15:00 | 760 |  |  | 0.017586
2019-02-01 16:00 | 761 |  |  | 0.010252
2019-02-01 17:00 | 762 |  |  | 0
2019-02-01 18:00 | 763 |  |  | 0
2019-02-01 19:00 | 764 |  |  | 0
2019-02-01 20:00 | 765 |  |  | 0
2019-02-01 21:00 | 766 |  |  | 0
2019-02-01 22:00 | 767 |  |  | 0
2019-02-01 23:00 | 768 |  |  | 0
2019-02-02 | 769 |  |  | 0
2019-02-02 01:00 | 770 |  |  | 0
2019-02-02 02:00 | 771 |  |  | 0
2019-02-02 03:00 | 772 |  |  | 0
2019-02-02 04:00 | 773 |  |  | 0
2019-02-02 05:00 | 774 |  |  | 0
2019-02-02 06:00 | 775 |  |  | 0
2019-02-02 07:00 | 776 |  |  | 0
2019-02-02 08:00 | 777 |  |  | 0.010168
2019-02-02 09:00 | 778 |  |  | 0.077846
2019-02-02 10:00 | 779 |  |  | 0.14069
2019-02-02 11:00 | 780 |  |  | 0.1872
2019-02-02 12:00 | 781 |  |  | 0.10027
2019-02-02 13:00 | 782 |  |  | 0.029588
2019-02-02 14:00 | 783 |  |  | 0.014752
2019-02-02 15:00 | 784 |  |  | 0.0028338
2019-02-02 16:00 | 785 |  |  | 8.3347e-05
2019-02-02 17:00 | 786 |  |  | 0
2019-02-02 18:00 | 787 |  |  | 0
2019-02-02 19:00 | 788 |  |  | 0
2019-02-02 20:00 | 789 |  |  | 0
2019-02-02 21:00 | 790 |  |  | 0
2019-02-02 22:00 | 791 |  |  | 0
2019-02-02 23:00 | 792 |  |  | 0
2019-02-03 | 793 |  |  | 0
2019-02-03 01:00 | 794 |  |  | 0
2019-02-03 02:00 | 795 |  |  | 0
2019-02-03 03:00 | 796 |  |  | 0
2019-02-03 04:00 | 797 |  |  | 0
2019-02-03 05:00 | 798 |  |  | 0
2019-02-03 06:00 | 799 |  |  | 0
2019-02-03 07:00 | 800 |  |  | 0
2019-02-03 08:00 | 801 |  |  | 0.016586
2019-02-03 09:00 | 802 |  |  | 0.065011
2019-02-03 10:00 | 803 |  |  | 0.092599
2019-02-03 11:00 | 804 |  |  | 0.15744
2019-02-03 12:00 | 805 |  |  | 0.3814
2019-02-03 13:00 | 806 |  |  | 0.47316
2019-02-03 14:00 | 807 |  |  | 0.28121
2019-02-03 15:00 | 808 |  |  | 0.30388
2019-02-03 16:00 | 809 |  |  | 0.1066
2019-02-03 17:00 | 810 |  |  | 0.011835
2019-02-03 18:00 | 811 |  |  | 0
2019-02-03 19:00 | 812 |  |  | 0
2019-02-03 20:00 | 813 |  |  | 0
2019-02-03 21:00 | 814 |  |  | 0
2019-02-03 22:00 | 815 |  |  | 0
2019-02-03 23:00 | 816 |  |  | 0
2019-02-04 | 817 |  |  | 0
2019-02-04 01:00 | 818 |  |  | 0
2019-02-04 02:00 | 819 |  |  | 0
2019-02-04 03:00 | 820 |  |  | 0
2019-02-04 04:00 | 821 |  |  | 0
2019-02-04 05:00 | 822 |  |  | 0
2019-02-04 06:00 | 823 |  |  | 0
2019-02-04 07:00 | 824 |  |  | 0.00033339
2019-02-04 08:00 | 825 |  |  | 0.062094
2019-02-04 09:00 | 826 |  |  | 0.25663
2019-02-04 10:00 | 827 |  |  | 0.44891
2019-02-04 11:00 | 828 |  |  | 0.58051
2019-02-04 12:00 | 829 |  |  | 0.64236
2019-02-04 13:00 | 830 |  |  | 0.62669
2019-02-04 14:00 | 831 |  |  | 0.51442
2019-02-04 15:00 | 832 |  |  | 0.36564
2019-02-04 16:00 | 833 |  |  | 0.16578
2019-02-04 17:00 | 834 |  |  | 0.0066678
2019-02-04 18:00 | 835 |  |  | 0
2019-02-04 19:00 | 836 |  |  | 0
2019-02-04 20:00 | 837 |  |  | 0
2019-02-04 21:00 | 838 |  |  | 0
2019-02-04 22:00 | 839 |  |  | 0
2019-02-04 23:00 | 840 |  |  | 0
2019-02-05 | 841 |  |  | 0
2019-02-05 01:00 | 842 |  |  | 0
2019-02-05 02:00 | 843 |  |  | 0
2019-02-05 03:00 | 844 |  |  | 0
2019-02-05 04:00 | 845 |  |  | 0
2019-02-05 05:00 | 846 |  |  | 0
2019-02-05 06:00 | 847 |  |  | 0
2019-02-05 07:00 | 848 |  |  | 8.3347e-05
2019-02-05 08:00 | 849 |  |  | 0.050175
2019-02-05 09:00 | 850 |  |  | 0.24829
2019-02-05 10:00 | 851 |  |  | 0.44799
2019-02-05 11:00 | 852 |  |  | 0.58768
2019-02-05 12:00 | 853 |  |  | 0.65453
2019-02-05 13:00 | 854 |  |  | 0.65678
2019-02-05 14:00 | 855 |  |  | 0.53401
2019-02-05 15:00 | 856 |  |  | 0.37831
2019-02-05 16:00 | 857 |  |  | 0.18011
2019-02-05 17:00 | 858 |  |  | 0.014336
2019-02-05 18:00 | 859 |  |  | 0
2019-02-05 19:00 | 860 |  |  | 0
2019-02-05 20:00 | 861 |  |  | 0
2019-02-05 21:00 | 862 |  |  | 0
2019-02-05 22:00 | 863 |  |  | 0
2019-02-05 23:00 | 864 |  |  | 0
2019-02-06 | 865 |  |  | 0
2019-02-06 01:00 | 866 |  |  | 0
2019-02-06 02:00 | 867 |  |  | 0
2019-02-06 03:00 | 868 |  |  | 0
2019-02-06 04:00 | 869 |  |  | 0
2019-02-06 05:00 | 870 |  |  | 0
2019-02-06 06:00 | 871 |  |  | 0
2019-02-06 07:00 | 872 |  |  | 0.00075013
2019-02-06 08:00 | 873 |  |  | 0.070845
2019-02-06 09:00 | 874 |  |  | 0.25804
2019-02-06 10:00 | 875 |  |  | 0.45441
2019-02-06 11:00 | 876 |  |  | 0.57768
2019-02-06 12:00 | 877 |  |  | 0.63944
2019-02-06 13:00 | 878 |  |  | 0.64069
2019-02-06 14:00 | 879 |  |  | 0.52359
2019-02-06 15:00 | 880 |  |  | 0.37865
2019-02-06 16:00 | 881 |  |  | 0.18395
2019-02-06 17:00 | 882 |  |  | 0.017086
2019-02-06 18:00 | 883 |  |  | 0
2019-02-06 19:00 | 884 |  |  | 0
2019-02-06 20:00 | 885 |  |  | 0
2019-02-06 21:00 | 886 |  |  | 0
2019-02-06 22:00 | 887 |  |  | 0
2019-02-06 23:00 | 888 |  |  | 0
2019-02-07 | 889 |  |  | 0
2019-02-07 01:00 | 890 |  |  | 0
2019-02-07 02:00 | 891 |  |  | 0
2019-02-07 03:00 | 892 |  |  | 0
2019-02-07 04:00 | 893 |  |  | 0
2019-02-07 05:00 | 894 |  |  | 0
2019-02-07 06:00 | 895 |  |  | 0
2019-02-07 07:00 | 896 |  |  | 0.0033339
2019-02-07 08:00 | 897 |  |  | 0.05976
2019-02-07 09:00 | 898 |  |  | 0.13311
2019-02-07 10:00 | 899 |  |  | 0.1171
2019-02-07 11:00 | 900 |  |  | 0.13569
2019-02-07 12:00 | 901 |  |  | 0.16728
2019-02-07 13:00 | 902 |  |  | 0.14369
2019-02-07 14:00 | 903 |  |  | 0.10902
2019-02-07 15:00 | 904 |  |  | 0.24646
2019-02-07 16:00 | 905 |  |  | 0.19103
2019-02-07 17:00 | 906 |  |  | 0.018086
2019-02-07 18:00 | 907 |  |  | 0
2019-02-07 19:00 | 908 |  |  | 0
2019-02-07 20:00 | 909 |  |  | 0
2019-02-07 21:00 | 910 |  |  | 0
2019-02-07 22:00 | 911 |  |  | 0
2019-02-07 23:00 | 912 |  |  | 0
2019-02-08 | 913 |  |  | 0
2019-02-08 01:00 | 914 |  |  | 0
2019-02-08 02:00 | 915 |  |  | 0
2019-02-08 03:00 | 916 |  |  | 0
2019-02-08 04:00 | 917 |  |  | 0
2019-02-08 05:00 | 918 |  |  | 0
2019-02-08 06:00 | 919 |  |  | 0
2019-02-08 07:00 | 920 |  |  | 0.0027505
2019-02-08 08:00 | 921 |  |  | 0.063511
2019-02-08 09:00 | 922 |  |  | 0.18786
2019-02-08 10:00 | 923 |  |  | 0.44249
2019-02-08 11:00 | 924 |  |  | 0.51425
2019-02-08 12:00 | 925 |  |  | 0.504
2019-02-08 13:00 | 926 |  |  | 0.47375
2019-02-08 14:00 | 927 |  |  | 0.4875
2019-02-08 15:00 | 928 |  |  | 0.32005
2019-02-08 16:00 | 929 |  |  | 0.11585
2019-02-08 17:00 | 930 |  |  | 0.019587
2019-02-08 18:00 | 931 |  |  | 0
2019-02-08 19:00 | 932 |  |  | 0
2019-02-08 20:00 | 933 |  |  | 0
2019-02-08 21:00 | 934 |  |  | 0
2019-02-08 22:00 | 935 |  |  | 0
2019-02-08 23:00 | 936 |  |  | 0
2019-02-09 | 937 |  |  | 0
2019-02-09 01:00 | 938 |  |  | 0
2019-02-09 02:00 | 939 |  |  | 0
2019-02-09 03:00 | 940 |  |  | 0
2019-02-09 04:00 | 941 |  |  | 0
2019-02-09 05:00 | 942 |  |  | 0
2019-02-09 06:00 | 943 |  |  | 0
2019-02-09 07:00 | 944 |  |  | 0.00041674
2019-02-09 08:00 | 945 |  |  | 0.048341
2019-02-09 09:00 | 946 |  |  | 0.21954
2019-02-09 10:00 | 947 |  |  | 0.3984
2019-02-09 11:00 | 948 |  |  | 0.512
2019-02-09 12:00 | 949 |  |  | 0.51834
2019-02-09 13:00 | 950 |  |  | 0.43849
2019-02-09 14:00 | 951 |  |  | 0.24504
2019-02-09 15:00 | 952 |  |  | 0.22754
2019-02-09 16:00 | 953 |  |  | 0.19062
2019-02-09 17:00 | 954 |  |  | 0.019253
2019-02-09 18:00 | 955 |  |  | 0
2019-02-09 19:00 | 956 |  |  | 0
2019-02-09 20:00 | 957 |  |  | 0
2019-02-09 21:00 | 958 |  |  | 0
2019-02-09 22:00 | 959 |  |  | 0
2019-02-09 23:00 | 960 |  |  | 0
2019-02-10 | 961 |  |  | 0
2019-02-10 01:00 | 962 |  |  | 0
2019-02-10 02:00 | 963 |  |  | 0
2019-02-10 03:00 | 964 |  |  | 0
2019-02-10 04:00 | 965 |  |  | 0
2019-02-10 05:00 | 966 |  |  | 0
2019-02-10 06:00 | 967 |  |  | 0
2019-02-10 07:00 | 968 |  |  | 0
2019-02-10 08:00 | 969 |  |  | 0.023004
2019-02-10 09:00 | 970 |  |  | 0.059843
2019-02-10 10:00 | 971 |  |  | 0.10627
2019-02-10 11:00 | 972 |  |  | 0.13544
2019-02-10 12:00 | 973 |  |  | 0.25963
2019-02-10 13:00 | 974 |  |  | 0.25713
2019-02-10 14:00 | 975 |  |  | 0.2963
2019-02-10 15:00 | 976 |  |  | 0.26321
2019-02-10 16:00 | 977 |  |  | 0.10568
2019-02-10 17:00 | 978 |  |  | 0.0060843
2019-02-10 18:00 | 979 |  |  | 0
2019-02-10 19:00 | 980 |  |  | 0
2019-02-10 20:00 | 981 |  |  | 0
2019-02-10 21:00 | 982 |  |  | 0
2019-02-10 22:00 | 983 |  |  | 0
2019-02-10 23:00 | 984 |  |  | 0
2019-02-11 | 985 |  |  | 0
2019-02-11 01:00 | 986 |  |  | 0
2019-02-11 02:00 | 987 |  |  | 0
2019-02-11 03:00 | 988 |  |  | 0
2019-02-11 04:00 | 989 |  |  | 0
2019-02-11 05:00 | 990 |  |  | 0
2019-02-11 06:00 | 991 |  |  | 0
2019-02-11 07:00 | 992 |  |  | 0.00041674
2019-02-11 08:00 | 993 |  |  | 0.040673
2019-02-11 09:00 | 994 |  |  | 0.28596
2019-02-11 10:00 | 995 |  |  | 0.49383
2019-02-11 11:00 | 996 |  |  | 0.6286
2019-02-11 12:00 | 997 |  |  | 0.70495
2019-02-11 13:00 | 998 |  |  | 0.72845
2019-02-11 14:00 | 999 |  |  | 0.61827
2019-02-11 15:00 | 1000 |  |  | 0.45424
2019-02-11 16:00 | 1001 |  |  | 0.24479
2019-02-11 17:00 | 1002 |  |  | 0.031005
2019-02-11 18:00 | 1003 |  |  | 0
2019-02-11 19:00 | 1004 |  |  | 0
2019-02-11 20:00 | 1005 |  |  | 0
2019-02-11 21:00 | 1006 |  |  | 0
2019-02-11 22:00 | 1007 |  |  | 0
2019-02-11 23:00 | 1008 |  |  | 0
2019-02-12 | 1009 |  |  | 0
2019-02-12 01:00 | 1010 |  |  | 0
2019-02-12 02:00 | 1011 |  |  | 0
2019-02-12 03:00 | 1012 |  |  | 0
2019-02-12 04:00 | 1013 |  |  | 0
2019-02-12 05:00 | 1014 |  |  | 0
2019-02-12 06:00 | 1015 |  |  | 0
2019-02-12 07:00 | 1016 |  |  | 0.0017503
2019-02-12 08:00 | 1017 |  |  | 0.076013
2019-02-12 09:00 | 1018 |  |  | 0.2903
2019-02-12 10:00 | 1019 |  |  | 0.47258
2019-02-12 11:00 | 1020 |  |  | 0.59977
2019-02-12 12:00 | 1021 |  |  | 0.64802
2019-02-12 13:00 | 1022 |  |  | 0.64702
2019-02-12 14:00 | 1023 |  |  | 0.47975
2019-02-12 15:00 | 1024 |  |  | 0.17745
2019-02-12 16:00 | 1025 |  |  | 0.062594
2019-02-12 17:00 | 1026 |  |  | 0.016503
2019-02-12 18:00 | 1027 |  |  | 0
2019-02-12 19:00 | 1028 |  |  | 0
2019-02-12 20:00 | 1029 |  |  | 0
2019-02-12 21:00 | 1030 |  |  | 0
2019-02-12 22:00 | 1031 |  |  | 0
2019-02-12 23:00 | 1032 |  |  | 0
2019-02-13 | 1033 |  |  | 0
2019-02-13 01:00 | 1034 |  |  | 0
2019-02-13 02:00 | 1035 |  |  | 0
2019-02-13 03:00 | 1036 |  |  | 0
2019-02-13 04:00 | 1037 |  |  | 0
2019-02-13 05:00 | 1038 |  |  | 0
2019-02-13 06:00 | 1039 |  |  | 0
2019-02-13 07:00 | 1040 |  |  | 0.0020837
2019-02-13 08:00 | 1041 |  |  | 0.071012
2019-02-13 09:00 | 1042 |  |  | 0.26763
2019-02-13 10:00 | 1043 |  |  | 0.45899
2019-02-13 11:00 | 1044 |  |  | 0.59727
2019-02-13 12:00 | 1045 |  |  | 0.66803
2019-02-13 13:00 | 1046 |  |  | 0.67286
2019-02-13 14:00 | 1047 |  |  | 0.56493
2019-02-13 15:00 | 1048 |  |  | 0.39632
2019-02-13 16:00 | 1049 |  |  | 0.20853
2019-02-13 17:00 | 1050 |  |  | 0.028838
2019-02-13 18:00 | 1051 |  |  | 0
2019-02-13 19:00 | 1052 |  |  | 0
2019-02-13 20:00 | 1053 |  |  | 0
2019-02-13 21:00 | 1054 |  |  | 0
2019-02-13 22:00 | 1055 |  |  | 0
2019-02-13 23:00 | 1056 |  |  | 0
2019-02-14 | 1057 |  |  | 0
2019-02-14 01:00 | 1058 |  |  | 0
2019-02-14 02:00 | 1059 |  |  | 0
2019-02-14 03:00 | 1060 |  |  | 0
2019-02-14 04:00 | 1061 |  |  | 0
2019-02-14 05:00 | 1062 |  |  | 0
2019-02-14 06:00 | 1063 |  |  | 0
2019-02-14 07:00 | 1064 |  |  | 0.0028338
2019-02-14 08:00 | 1065 |  |  | 0.076596
2019-02-14 09:00 | 1066 |  |  | 0.26579
2019-02-14 10:00 | 1067 |  |  | 0.45849
2019-02-14 11:00 | 1068 |  |  | 0.5921
2019-02-14 12:00 | 1069 |  |  | 0.64661
2019-02-14 13:00 | 1070 |  |  | 0.66328
2019-02-14 14:00 | 1071 |  |  | 0.59502
2019-02-14 15:00 | 1072 |  |  | 0.43557
2019-02-14 16:00 | 1073 |  |  | 0.23862
2019-02-14 17:00 | 1074 |  |  | 0.035173
2019-02-14 18:00 | 1075 |  |  | 0
2019-02-14 19:00 | 1076 |  |  | 0
2019-02-14 20:00 | 1077 |  |  | 0
2019-02-14 21:00 | 1078 |  |  | 0
2019-02-14 22:00 | 1079 |  |  | 0
2019-02-14 23:00 | 1080 |  |  | 0
2019-02-15 | 1081 |  |  | 0
2019-02-15 01:00 | 1082 |  |  | 0
2019-02-15 02:00 | 1083 |  |  | 0
2019-02-15 03:00 | 1084 |  |  | 0
2019-02-15 04:00 | 1085 |  |  | 0
2019-02-15 05:00 | 1086 |  |  | 0
2019-02-15 06:00 | 1087 |  |  | 0
2019-02-15 07:00 | 1088 |  |  | 0.0033339
2019-02-15 08:00 | 1089 |  |  | 0.073262
2019-02-15 09:00 | 1090 |  |  | 0.25421
2019-02-15 10:00 | 1091 |  |  | 0.45199
2019-02-15 11:00 | 1092 |  |  | 0.58901
2019-02-15 12:00 | 1093 |  |  | 0.65244
2019-02-15 13:00 | 1094 |  |  | 0.66111
2019-02-15 14:00 | 1095 |  |  | 0.56968
2019-02-15 15:00 | 1096 |  |  | 0.41099
2019-02-15 16:00 | 1097 |  |  | 0.22279
2019-02-15 17:00 | 1098 |  |  | 0.034756
2019-02-15 18:00 | 1099 |  |  | 0
2019-02-15 19:00 | 1100 |  |  | 0
2019-02-15 20:00 | 1101 |  |  | 0
2019-02-15 21:00 | 1102 |  |  | 0
2019-02-15 22:00 | 1103 |  |  | 0
2019-02-15 23:00 | 1104 |  |  | 0
2019-02-16 | 1105 |  |  | 0
2019-02-16 01:00 | 1106 |  |  | 0
2019-02-16 02:00 | 1107 |  |  | 0
2019-02-16 03:00 | 1108 |  |  | 0
2019-02-16 04:00 | 1109 |  |  | 0
2019-02-16 05:00 | 1110 |  |  | 0
2019-02-16 06:00 | 1111 |  |  | 0
2019-02-16 07:00 | 1112 |  |  | 0.0043341
2019-02-16 08:00 | 1113 |  |  | 0.075013
2019-02-16 09:00 | 1114 |  |  | 0.24179
2019-02-16 10:00 | 1115 |  |  | 0.42574
2019-02-16 11:00 | 1116 |  |  | 0.55918
2019-02-16 12:00 | 1117 |  |  | 0.63319
2019-02-16 13:00 | 1118 |  |  | 0.63694
2019-02-16 14:00 | 1119 |  |  | 0.56268
2019-02-16 15:00 | 1120 |  |  | 0.41107
2019-02-16 16:00 | 1121 |  |  | 0.21487
2019-02-16 17:00 | 1122 |  |  | 0.03734
2019-02-16 18:00 | 1123 |  |  | 0
2019-02-16 19:00 | 1124 |  |  | 0
2019-02-16 20:00 | 1125 |  |  | 0
2019-02-16 21:00 | 1126 |  |  | 0
2019-02-16 22:00 | 1127 |  |  | 0
2019-02-16 23:00 | 1128 |  |  | 0
2019-02-17 | 1129 |  |  | 0
2019-02-17 01:00 | 1130 |  |  | 0
2019-02-17 02:00 | 1131 |  |  | 0
2019-02-17 03:00 | 1132 |  |  | 0
2019-02-17 04:00 | 1133 |  |  | 0
2019-02-17 05:00 | 1134 |  |  | 0
2019-02-17 06:00 | 1135 |  |  | 0
2019-02-17 07:00 | 1136 |  |  | 0.0050842
2019-02-17 08:00 | 1137 |  |  | 0.07868
2019-02-17 09:00 | 1138 |  |  | 0.26571
2019-02-17 10:00 | 1139 |  |  | 0.45399
2019-02-17 11:00 | 1140 |  |  | 0.57776
2019-02-17 12:00 | 1141 |  |  | 0.64302
2019-02-17 13:00 | 1142 |  |  | 0.65178
2019-02-17 14:00 | 1143 |  |  | 0.58093
2019-02-17 15:00 | 1144 |  |  | 0.41149
2019-02-17 16:00 | 1145 |  |  | 0.2187
2019-02-17 17:00 | 1146 |  |  | 0.038173
2019-02-17 18:00 | 1147 |  |  | 0
2019-02-17 19:00 | 1148 |  |  | 0
2019-02-17 20:00 | 1149 |  |  | 0
2019-02-17 21:00 | 1150 |  |  | 0
2019-02-17 22:00 | 1151 |  |  | 0
2019-02-17 23:00 | 1152 |  |  | 0
2019-02-18 | 1153 |  |  | 0
2019-02-18 01:00 | 1154 |  |  | 0
2019-02-18 02:00 | 1155 |  |  | 0
2019-02-18 03:00 | 1156 |  |  | 0
2019-02-18 04:00 | 1157 |  |  | 0
2019-02-18 05:00 | 1158 |  |  | 0
2019-02-18 06:00 | 1159 |  |  | 0
2019-02-18 07:00 | 1160 |  |  | 0.0056676
2019-02-18 08:00 | 1161 |  |  | 0.081597
2019-02-18 09:00 | 1162 |  |  | 0.26413
2019-02-18 10:00 | 1163 |  |  | 0.45508
2019-02-18 11:00 | 1164 |  |  | 0.58735
2019-02-18 12:00 | 1165 |  |  | 0.65211
2019-02-18 13:00 | 1166 |  |  | 0.67186
2019-02-18 14:00 | 1167 |  |  | 0.59877
2019-02-18 15:00 | 1168 |  |  | 0.41707
2019-02-18 16:00 | 1169 |  |  | 0.2172
2019-02-18 17:00 | 1170 |  |  | 0.04209
2019-02-18 18:00 | 1171 |  |  | 0
2019-02-18 19:00 | 1172 |  |  | 0
2019-02-18 20:00 | 1173 |  |  | 0
2019-02-18 21:00 | 1174 |  |  | 0
2019-02-18 22:00 | 1175 |  |  | 0
2019-02-18 23:00 | 1176 |  |  | 0
2019-02-19 | 1177 |  |  | 0
2019-02-19 01:00 | 1178 |  |  | 0
2019-02-19 02:00 | 1179 |  |  | 0
2019-02-19 03:00 | 1180 |  |  | 0
2019-02-19 04:00 | 1181 |  |  | 0
2019-02-19 05:00 | 1182 |  |  | 0
2019-02-19 06:00 | 1183 |  |  | 0
2019-02-19 07:00 | 1184 |  |  | 0.0067511
2019-02-19 08:00 | 1185 |  |  | 0.083514
2019-02-19 09:00 | 1186 |  |  | 0.25438
2019-02-19 10:00 | 1187 |  |  | 0.43424
2019-02-19 11:00 | 1188 |  |  | 0.56443
2019-02-19 12:00 | 1189 |  |  | 0.64952
2019-02-19 13:00 | 1190 |  |  | 0.65686
2019-02-19 14:00 | 1191 |  |  | 0.57151
2019-02-19 15:00 | 1192 |  |  | 0.40548
2019-02-19 16:00 | 1193 |  |  | 0.21279
2019-02-19 17:00 | 1194 |  |  | 0.04184
2019-02-19 18:00 | 1195 |  |  | 0
2019-02-19 19:00 | 1196 |  |  | 0
2019-02-19 20:00 | 1197 |  |  | 0
2019-02-19 21:00 | 1198 |  |  | 0
2019-02-19 22:00 | 1199 |  |  | 0
2019-02-19 23:00 | 1200 |  |  | 0
2019-02-20 | 1201 |  |  | 0
2019-02-20 01:00 | 1202 |  |  | 0
2019-02-20 02:00 | 1203 |  |  | 0
2019-02-20 03:00 | 1204 |  |  | 0
2019-02-20 04:00 | 1205 |  |  | 0
2019-02-20 05:00 | 1206 |  |  | 0
2019-02-20 06:00 | 1207 |  |  | 0
2019-02-20 07:00 | 1208 |  |  | 0.0075846
2019-02-20 08:00 | 1209 |  |  | 0.086931
2019-02-20 09:00 | 1210 |  |  | 0.24312
2019-02-20 10:00 | 1211 |  |  | 0.41524
2019-02-20 11:00 | 1212 |  |  | 0.54084
2019-02-20 12:00 | 1213 |  |  | 0.58685
2019-02-20 13:00 | 1214 |  |  | 0.64211
2019-02-20 14:00 | 1215 |  |  | 0.58043
2019-02-20 15:00 | 1216 |  |  | 0.4189
2019-02-20 16:00 | 1217 |  |  | 0.2292
2019-02-20 17:00 | 1218 |  |  | 0.051092
2019-02-20 18:00 | 1219 |  |  | 8.3347e-05
2019-02-20 19:00 | 1220 |  |  | 0
2019-02-20 20:00 | 1221 |  |  | 0
2019-02-20 21:00 | 1222 |  |  | 0
2019-02-20 22:00 | 1223 |  |  | 0
2019-02-20 23:00 | 1224 |  |  | 0
2019-02-21 | 1225 |  |  | 0
2019-02-21 01:00 | 1226 |  |  | 0
2019-02-21 02:00 | 1227 |  |  | 0
2019-02-21 03:00 | 1228 |  |  | 0
2019-02-21 04:00 | 1229 |  |  | 0
2019-02-21 05:00 | 1230 |  |  | 0
2019-02-21 06:00 | 1231 |  |  | 0
2019-02-21 07:00 | 1232 |  |  | 0.0071679
2019-02-21 08:00 | 1233 |  |  | 0.083181
2019-02-21 09:00 | 1234 |  |  | 0.24729
2019-02-21 10:00 | 1235 |  |  | 0.41224
2019-02-21 11:00 | 1236 |  |  | 0.53776
2019-02-21 12:00 | 1237 |  |  | 0.61277
2019-02-21 13:00 | 1238 |  |  | 0.64694
2019-02-21 14:00 | 1239 |  |  | 0.60318
2019-02-21 15:00 | 1240 |  |  | 0.44657
2019-02-21 16:00 | 1241 |  |  | 0.25113
2019-02-21 17:00 | 1242 |  |  | 0.055676
2019-02-21 18:00 | 1243 |  |  | 8.3347e-05
2019-02-21 19:00 | 1244 |  |  | 0
2019-02-21 20:00 | 1245 |  |  | 0
2019-02-21 21:00 | 1246 |  |  | 0
2019-02-21 22:00 | 1247 |  |  | 0
2019-02-21 23:00 | 1248 |  |  | 0
2019-02-22 | 1249 |  |  | 0
2019-02-22 01:00 | 1250 |  |  | 0
2019-02-22 02:00 | 1251 |  |  | 0
2019-02-22 03:00 | 1252 |  |  | 0
2019-02-22 04:00 | 1253 |  |  | 0
2019-02-22 05:00 | 1254 |  |  | 0
2019-02-22 06:00 | 1255 |  |  | 0
2019-02-22 07:00 | 1256 |  |  | 0.0088348
2019-02-22 08:00 | 1257 |  |  | 0.073096
2019-02-22 09:00 | 1258 |  |  | 0.2713
2019-02-22 10:00 | 1259 |  |  | 0.47966
2019-02-22 11:00 | 1260 |  |  | 0.6101
2019-02-22 12:00 | 1261 |  |  | 0.68078
2019-02-22 13:00 | 1262 |  |  | 0.68661
2019-02-22 14:00 | 1263 |  |  | 0.64127
2019-02-22 15:00 | 1264 |  |  | 0.47175
2019-02-22 16:00 | 1265 |  |  | 0.28171
2019-02-22 17:00 | 1266 |  |  | 0.066511
2019-02-22 18:00 | 1267 |  |  | 8.3347e-05
2019-02-22 19:00 | 1268 |  |  | 0
2019-02-22 20:00 | 1269 |  |  | 0
2019-02-22 21:00 | 1270 |  |  | 0
2019-02-22 22:00 | 1271 |  |  | 0
2019-02-22 23:00 | 1272 |  |  | 0
2019-02-23 | 1273 |  |  | 0
2019-02-23 01:00 | 1274 |  |  | 0
2019-02-23 02:00 | 1275 |  |  | 0
2019-02-23 03:00 | 1276 |  |  | 0
2019-02-23 04:00 | 1277 |  |  | 0
2019-02-23 05:00 | 1278 |  |  | 0
2019-02-23 06:00 | 1279 |  |  | 0
2019-02-23 07:00 | 1280 |  |  | 0.0078346
2019-02-23 08:00 | 1281 |  |  | 0.060677
2019-02-23 09:00 | 1282 |  |  | 0.091932
2019-02-23 10:00 | 1283 |  |  | 0.37706
2019-02-23 11:00 | 1284 |  |  | 0.58751
2019-02-23 12:00 | 1285 |  |  | 0.64927
2019-02-23 13:00 | 1286 |  |  | 0.30388
2019-02-23 14:00 | 1287 |  |  | 0.10427
2019-02-23 15:00 | 1288 |  |  | 0.073096
2019-02-23 16:00 | 1289 |  |  | 0.043174
2019-02-23 17:00 | 1290 |  |  | 0.0075846
2019-02-23 18:00 | 1291 |  |  | 0
2019-02-23 19:00 | 1292 |  |  | 0
2019-02-23 20:00 | 1293 |  |  | 0
2019-02-23 21:00 | 1294 |  |  | 0
2019-02-23 22:00 | 1295 |  |  | 0
2019-02-23 23:00 | 1296 |  |  | 0
2019-02-24 | 1297 |  |  | 0
2019-02-24 01:00 | 1298 |  |  | 0
2019-02-24 02:00 | 1299 |  |  | 0
2019-02-24 03:00 | 1300 |  |  | 0
2019-02-24 04:00 | 1301 |  |  | 0
2019-02-24 05:00 | 1302 |  |  | 0
2019-02-24 06:00 | 1303 |  |  | 0
2019-02-24 07:00 | 1304 |  |  | 0.0089182
2019-02-24 08:00 | 1305 |  |  | 0.095099
2019-02-24 09:00 | 1306 |  |  | 0.28921
2019-02-24 10:00 | 1307 |  |  | 0.4765
2019-02-24 11:00 | 1308 |  |  | 0.60935
2019-02-24 12:00 | 1309 |  |  | 0.6877
2019-02-24 13:00 | 1310 |  |  | 0.70112
2019-02-24 14:00 | 1311 |  |  | 0.65419
2019-02-24 15:00 | 1312 |  |  | 0.48441
2019-02-24 16:00 | 1313 |  |  | 0.30338
2019-02-24 17:00 | 1314 |  |  | 0.068095
2019-02-24 18:00 | 1315 |  |  | 0.00016669
2019-02-24 19:00 | 1316 |  |  | 0
2019-02-24 20:00 | 1317 |  |  | 0
2019-02-24 21:00 | 1318 |  |  | 0
2019-02-24 22:00 | 1319 |  |  | 0
2019-02-24 23:00 | 1320 |  |  | 0
2019-02-25 | 1321 |  |  | 0
2019-02-25 01:00 | 1322 |  |  | 0
2019-02-25 02:00 | 1323 |  |  | 0
2019-02-25 03:00 | 1324 |  |  | 0
2019-02-25 04:00 | 1325 |  |  | 0
2019-02-25 05:00 | 1326 |  |  | 0
2019-02-25 06:00 | 1327 |  |  | 0
2019-02-25 07:00 | 1328 |  |  | 0.0093349
2019-02-25 08:00 | 1329 |  |  | 0.093599
2019-02-25 09:00 | 1330 |  |  | 0.28455
2019-02-25 10:00 | 1331 |  |  | 0.46658
2019-02-25 11:00 | 1332 |  |  | 0.60243
2019-02-25 12:00 | 1333 |  |  | 0.6827
2019-02-25 13:00 | 1334 |  |  | 0.69328
2019-02-25 14:00 | 1335 |  |  | 0.64719
2019-02-25 15:00 | 1336 |  |  | 0.47175
2019-02-25 16:00 | 1337 |  |  | 0.25071
2019-02-25 17:00 | 1338 |  |  | 0.05726
2019-02-25 18:00 | 1339 |  |  | 0.00025004
2019-02-25 19:00 | 1340 |  |  | 0
2019-02-25 20:00 | 1341 |  |  | 0
2019-02-25 21:00 | 1342 |  |  | 0
2019-02-25 22:00 | 1343 |  |  | 0
2019-02-25 23:00 | 1344 |  |  | 0
2019-02-26 | 1345 |  |  | 0
2019-02-26 01:00 | 1346 |  |  | 0
2019-02-26 02:00 | 1347 |  |  | 0
2019-02-26 03:00 | 1348 |  |  | 0
2019-02-26 04:00 | 1349 |  |  | 0
2019-02-26 05:00 | 1350 |  |  | 0
2019-02-26 06:00 | 1351 |  |  | 0
2019-02-26 07:00 | 1352 |  |  | 0.0082514
2019-02-26 08:00 | 1353 |  |  | 0.087265
2019-02-26 09:00 | 1354 |  |  | 0.24112
2019-02-26 10:00 | 1355 |  |  | 0.3794
2019-02-26 11:00 | 1356 |  |  | 0.46974
2019-02-26 12:00 | 1357 |  |  | 0.6722
2019-02-26 13:00 | 1358 |  |  | 0.65286
2019-02-26 14:00 | 1359 |  |  | 0.5155
2019-02-26 15:00 | 1360 |  |  | 0.47825
2019-02-26 16:00 | 1361 |  |  | 0.27313
2019-02-26 17:00 | 1362 |  |  | 0.081847
2019-02-26 18:00 | 1363 |  |  | 0.00075013
2019-02-26 19:00 | 1364 |  |  | 0
2019-02-26 20:00 | 1365 |  |  | 0
2019-02-26 21:00 | 1366 |  |  | 0
2019-02-26 22:00 | 1367 |  |  | 0
2019-02-26 23:00 | 1368 |  |  | 0
2019-02-27 | 1369 |  |  | 0
2019-02-27 01:00 | 1370 |  |  | 0
2019-02-27 02:00 | 1371 |  |  | 0
2019-02-27 03:00 | 1372 |  |  | 0
2019-02-27 04:00 | 1373 |  |  | 0
2019-02-27 05:00 | 1374 |  |  | 0
2019-02-27 06:00 | 1375 |  |  | 0
2019-02-27 07:00 | 1376 |  |  | 0.0085848
2019-02-27 08:00 | 1377 |  |  | 0.10402
2019-02-27 09:00 | 1378 |  |  | 0.30138
2019-02-27 10:00 | 1379 |  |  | 0.49075
2019-02-27 11:00 | 1380 |  |  | 0.61902
2019-02-27 12:00 | 1381 |  |  | 0.6727
2019-02-27 13:00 | 1382 |  |  | 0.67153
2019-02-27 14:00 | 1383 |  |  | 0.6186
2019-02-27 15:00 | 1384 |  |  | 0.47941
2019-02-27 16:00 | 1385 |  |  | 0.28771
2019-02-27 17:00 | 1386 |  |  | 0.075763
2019-02-27 18:00 | 1387 |  |  | 0.00033339
2019-02-27 19:00 | 1388 |  |  | 0
2019-02-27 20:00 | 1389 |  |  | 0
2019-02-27 21:00 | 1390 |  |  | 0
2019-02-27 22:00 | 1391 |  |  | 0
2019-02-27 23:00 | 1392 |  |  | 0
2019-02-28 | 1393 |  |  | 0
2019-02-28 01:00 | 1394 |  |  | 0
2019-02-28 02:00 | 1395 |  |  | 0
2019-02-28 03:00 | 1396 |  |  | 0
2019-02-28 04:00 | 1397 |  |  | 0
2019-02-28 05:00 | 1398 |  |  | 0
2019-02-28 06:00 | 1399 |  |  | 0
2019-02-28 07:00 | 1400 |  |  | 0.012585
2019-02-28 08:00 | 1401 |  |  | 0.098683
2019-02-28 09:00 | 1402 |  |  | 0.27871
2019-02-28 10:00 | 1403 |  |  | 0.45899
2019-02-28 11:00 | 1404 |  |  | 0.58818
2019-02-28 12:00 | 1405 |  |  | 0.6286
2019-02-28 13:00 | 1406 |  |  | 0.63469
2019-02-28 14:00 | 1407 |  |  | 0.61952
2019-02-28 15:00 | 1408 |  |  | 0.44691
2019-02-28 16:00 | 1409 |  |  | 0.28538
2019-02-28 17:00 | 1410 |  |  | 0.083764
2019-02-28 18:00 | 1411 |  |  | 0.00066678
2019-02-28 19:00 | 1412 |  |  | 0
2019-02-28 20:00 | 1413 |  |  | 0
2019-02-28 21:00 | 1414 |  |  | 0
2019-02-28 22:00 | 1415 |  |  | 0
2019-02-28 23:00 | 1416 |  |  | 0
2019-03-01 | 1417 |  |  | 0
2019-03-01 01:00 | 1418 |  |  | 0
2019-03-01 02:00 | 1419 |  |  | 0
2019-03-01 03:00 | 1420 |  |  | 0
2019-03-01 04:00 | 1421 |  |  | 0
2019-03-01 05:00 | 1422 |  |  | 0
2019-03-01 06:00 | 1423 |  |  | 0
2019-03-01 07:00 | 1424 |  |  | 0.011835
2019-03-01 08:00 | 1425 |  |  | 0.1131
2019-03-01 09:00 | 1426 |  |  | 0.31864
2019-03-01 10:00 | 1427 |  |  | 0.51317
2019-03-01 11:00 | 1428 |  |  | 0.63361
2019-03-01 12:00 | 1429 |  |  | 0.70912
2019-03-01 13:00 | 1430 |  |  | 0.74912
2019-03-01 14:00 | 1431 |  |  | 0.69995
2019-03-01 15:00 | 1432 |  |  | 0.55293
2019-03-01 16:00 | 1433 |  |  | 0.35656
2019-03-01 17:00 | 1434 |  |  | 0.1126
2019-03-01 18:00 | 1435 |  |  | 0.00066678
2019-03-01 19:00 | 1436 |  |  | 0
2019-03-01 20:00 | 1437 |  |  | 0
2019-03-01 21:00 | 1438 |  |  | 0
2019-03-01 22:00 | 1439 |  |  | 0
2019-03-01 23:00 | 1440 |  |  | 0
2019-03-02 | 1441 |  |  | 0
2019-03-02 01:00 | 1442 |  |  | 0
2019-03-02 02:00 | 1443 |  |  | 0
2019-03-02 03:00 | 1444 |  |  | 0
2019-03-02 04:00 | 1445 |  |  | 0
2019-03-02 05:00 | 1446 |  |  | 0
2019-03-02 06:00 | 1447 |  |  | 0
2019-03-02 07:00 | 1448 |  |  | 0.01967
2019-03-02 08:00 | 1449 |  |  | 0.14444
2019-03-02 09:00 | 1450 |  |  | 0.20153
2019-03-02 10:00 | 1451 |  |  | 0.32689
2019-03-02 11:00 | 1452 |  |  | 0.3223
2019-03-02 12:00 | 1453 |  |  | 0.64761
2019-03-02 13:00 | 1454 |  |  | 0.33056
2019-03-02 14:00 | 1455 |  |  | 0.39415
2019-03-02 15:00 | 1456 |  |  | 0.34272
2019-03-02 16:00 | 1457 |  |  | 0.21187
2019-03-02 17:00 | 1458 |  |  | 0.054342
2019-03-02 18:00 | 1459 |  |  | 0.0029172
2019-03-02 19:00 | 1460 |  |  | 0
2019-03-02 20:00 | 1461 |  |  | 0
2019-03-02 21:00 | 1462 |  |  | 0
2019-03-02 22:00 | 1463 |  |  | 0
2019-03-02 23:00 | 1464 |  |  | 0
2019-03-03 | 1465 |  |  | 0
2019-03-03 01:00 | 1466 |  |  | 0
2019-03-03 02:00 | 1467 |  |  | 0
2019-03-03 03:00 | 1468 |  |  | 0
2019-03-03 04:00 | 1469 |  |  | 0
2019-03-03 05:00 | 1470 |  |  | 0
2019-03-03 06:00 | 1471 |  |  | 0
2019-03-03 07:00 | 1472 |  |  | 0.017003
2019-03-03 08:00 | 1473 |  |  | 0.12477
2019-03-03 09:00 | 1474 |  |  | 0.32489
2019-03-03 10:00 | 1475 |  |  | 0.49475
2019-03-03 11:00 | 1476 |  |  | 0.62069
2019-03-03 12:00 | 1477 |  |  | 0.67911
2019-03-03 13:00 | 1478 |  |  | 0.64519
2019-03-03 14:00 | 1479 |  |  | 0.34106
2019-03-03 15:00 | 1480 |  |  | 0.36198
2019-03-03 16:00 | 1481 |  |  | 0.10477
2019-03-03 17:00 | 1482 |  |  | 0.1171
2019-03-03 18:00 | 1483 |  |  | 0.0016669
2019-03-03 19:00 | 1484 |  |  | 0
2019-03-03 20:00 | 1485 |  |  | 0
2019-03-03 21:00 | 1486 |  |  | 0
2019-03-03 22:00 | 1487 |  |  | 0
2019-03-03 23:00 | 1488 |  |  | 0
2019-03-04 | 1489 |  |  | 0
2019-03-04 01:00 | 1490 |  |  | 0
2019-03-04 02:00 | 1491 |  |  | 0
2019-03-04 03:00 | 1492 |  |  | 0
2019-03-04 04:00 | 1493 |  |  | 0
2019-03-04 05:00 | 1494 |  |  | 0
2019-03-04 06:00 | 1495 |  |  | 0
2019-03-04 07:00 | 1496 |  |  | 0.020087
2019-03-04 08:00 | 1497 |  |  | 0.10168
2019-03-04 09:00 | 1498 |  |  | 0.25163
2019-03-04 10:00 | 1499 |  |  | 0.28688
2019-03-04 11:00 | 1500 |  |  | 0.34456
2019-03-04 12:00 | 1501 |  |  | 0.56909
2019-03-04 13:00 | 1502 |  |  | 0.63361
2019-03-04 14:00 | 1503 |  |  | 0.47058
2019-03-04 15:00 | 1504 |  |  | 0.36523
2019-03-04 16:00 | 1505 |  |  | 0.26279
2019-03-04 17:00 | 1506 |  |  | 0.089932
2019-03-04 18:00 | 1507 |  |  | 0.0010835
2019-03-04 19:00 | 1508 |  |  | 0
2019-03-04 20:00 | 1509 |  |  | 0
2019-03-04 21:00 | 1510 |  |  | 0
2019-03-04 22:00 | 1511 |  |  | 0
2019-03-04 23:00 | 1512 |  |  | 0
2019-03-05 | 1513 |  |  | 0
2019-03-05 01:00 | 1514 |  |  | 0
2019-03-05 02:00 | 1515 |  |  | 0
2019-03-05 03:00 | 1516 |  |  | 0
2019-03-05 04:00 | 1517 |  |  | 0
2019-03-05 05:00 | 1518 |  |  | 0
2019-03-05 06:00 | 1519 |  |  | 0
2019-03-05 07:00 | 1520 |  |  | 0.024087
2019-03-05 08:00 | 1521 |  |  | 0.13086
2019-03-05 09:00 | 1522 |  |  | 0.31372
2019-03-05 10:00 | 1523 |  |  | 0.524
2019-03-05 11:00 | 1524 |  |  | 0.64302
2019-03-05 12:00 | 1525 |  |  | 0.71245
2019-03-05 13:00 | 1526 |  |  | 0.72712
2019-03-05 14:00 | 1527 |  |  | 0.68303
2019-03-05 15:00 | 1528 |  |  | 0.55768
2019-03-05 16:00 | 1529 |  |  | 0.34964
2019-03-05 17:00 | 1530 |  |  | 0.12094
2019-03-05 18:00 | 1531 |  |  | 0.0010002
2019-03-05 19:00 | 1532 |  |  | 0
2019-03-05 20:00 | 1533 |  |  | 0
2019-03-05 21:00 | 1534 |  |  | 0
2019-03-05 22:00 | 1535 |  |  | 0
2019-03-05 23:00 | 1536 |  |  | 0
2019-03-06 | 1537 |  |  | 0
2019-03-06 01:00 | 1538 |  |  | 0
2019-03-06 02:00 | 1539 |  |  | 0
2019-03-06 03:00 | 1540 |  |  | 0
2019-03-06 04:00 | 1541 |  |  | 0
2019-03-06 05:00 | 1542 |  |  | 0
2019-03-06 06:00 | 1543 |  |  | 0
2019-03-06 07:00 | 1544 |  |  | 0.02242
2019-03-06 08:00 | 1545 |  |  | 0.13519
2019-03-06 09:00 | 1546 |  |  | 0.28346
2019-03-06 10:00 | 1547 |  |  | 0.34997
2019-03-06 11:00 | 1548 |  |  | 0.38023
2019-03-06 12:00 | 1549 |  |  | 0.22662
2019-03-06 13:00 | 1550 |  |  | 0.33897
2019-03-06 14:00 | 1551 |  |  | 0.23787
2019-03-06 15:00 | 1552 |  |  | 0.24662
2019-03-06 16:00 | 1553 |  |  | 0.061094
2019-03-06 17:00 | 1554 |  |  | 0.0052509
2019-03-06 18:00 | 1555 |  |  | 0
2019-03-06 19:00 | 1556 |  |  | 0
2019-03-06 20:00 | 1557 |  |  | 0
2019-03-06 21:00 | 1558 |  |  | 0
2019-03-06 22:00 | 1559 |  |  | 0
2019-03-06 23:00 | 1560 |  |  | 0
2019-03-07 | 1561 |  |  | 0
2019-03-07 01:00 | 1562 |  |  | 0
2019-03-07 02:00 | 1563 |  |  | 0
2019-03-07 03:00 | 1564 |  |  | 0
2019-03-07 04:00 | 1565 |  |  | 0
2019-03-07 05:00 | 1566 |  |  | 0
2019-03-07 06:00 | 1567 |  |  | 0
2019-03-07 07:00 | 1568 |  |  | 8.3347e-05
2019-03-07 08:00 | 1569 |  |  | 0.010168
2019-03-07 09:00 | 1570 |  |  | 0.10877
2019-03-07 10:00 | 1571 |  |  | 0.19828
2019-03-07 11:00 | 1572 |  |  | 0.68703
2019-03-07 12:00 | 1573 |  |  | 0.46949
2019-03-07 13:00 | 1574 |  |  | 0.56334
2019-03-07 14:00 | 1575 |  |  | 0.6942
2019-03-07 15:00 | 1576 |  |  | 0.56759
2019-03-07 16:00 | 1577 |  |  | 0.28205
2019-03-07 17:00 | 1578 |  |  | 0.095933
2019-03-07 18:00 | 1579 |  |  | 0.0018336
2019-03-07 19:00 | 1580 |  |  | 0
2019-03-07 20:00 | 1581 |  |  | 0
2019-03-07 21:00 | 1582 |  |  | 0
2019-03-07 22:00 | 1583 |  |  | 0
2019-03-07 23:00 | 1584 |  |  | 0
2019-03-08 | 1585 |  |  | 0
2019-03-08 01:00 | 1586 |  |  | 0
2019-03-08 02:00 | 1587 |  |  | 0
2019-03-08 03:00 | 1588 |  |  | 0
2019-03-08 04:00 | 1589 |  |  | 0
2019-03-08 05:00 | 1590 |  |  | 0
2019-03-08 06:00 | 1591 |  |  | 0
2019-03-08 07:00 | 1592 |  |  | 0.027005
2019-03-08 08:00 | 1593 |  |  | 0.11735
2019-03-08 09:00 | 1594 |  |  | 0.32164
2019-03-08 10:00 | 1595 |  |  | 0.51084
2019-03-08 11:00 | 1596 |  |  | 0.64619
2019-03-08 12:00 | 1597 |  |  | 0.72462
2019-03-08 13:00 | 1598 |  |  | 0.67528
2019-03-08 14:00 | 1599 |  |  | 0.66286
2019-03-08 15:00 | 1600 |  |  | 0.53009
2019-03-08 16:00 | 1601 |  |  | 0.32989
2019-03-08 17:00 | 1602 |  |  | 0.09735
2019-03-08 18:00 | 1603 |  |  | 0.0029172
2019-03-08 19:00 | 1604 |  |  | 0
2019-03-08 20:00 | 1605 |  |  | 0
2019-03-08 21:00 | 1606 |  |  | 0
2019-03-08 22:00 | 1607 |  |  | 0
2019-03-08 23:00 | 1608 |  |  | 0
2019-03-09 | 1609 |  |  | 0
2019-03-09 01:00 | 1610 |  |  | 0
2019-03-09 02:00 | 1611 |  |  | 0
2019-03-09 03:00 | 1612 |  |  | 0
2019-03-09 04:00 | 1613 |  |  | 0
2019-03-09 05:00 | 1614 |  |  | 0
2019-03-09 06:00 | 1615 |  |  | 8.3347e-05
2019-03-09 07:00 | 1616 |  |  | 0.025671
2019-03-09 08:00 | 1617 |  |  | 0.13286
2019-03-09 09:00 | 1618 |  |  | 0.30772
2019-03-09 10:00 | 1619 |  |  | 0.50583
2019-03-09 11:00 | 1620 |  |  | 0.65286
2019-03-09 12:00 | 1621 |  |  | 0.72554
2019-03-09 13:00 | 1622 |  |  | 0.74796
2019-03-09 14:00 | 1623 |  |  | 0.68328
2019-03-09 15:00 | 1624 |  |  | 0.57385
2019-03-09 16:00 | 1625 |  |  | 0.35356
2019-03-09 17:00 | 1626 |  |  | 0.10243
2019-03-09 18:00 | 1627 |  |  | 0.0039173
2019-03-09 19:00 | 1628 |  |  | 0
2019-03-09 20:00 | 1629 |  |  | 0
2019-03-09 21:00 | 1630 |  |  | 0
2019-03-09 22:00 | 1631 |  |  | 0
2019-03-09 23:00 | 1632 |  |  | 0
2019-03-10 | 1633 |  |  | 0
2019-03-10 01:00 | 1634 |  |  | 0
2019-03-10 02:00 | 1635 |  |  | 0
2019-03-10 03:00 | 1636 |  |  | 0
2019-03-10 04:00 | 1637 |  |  | 0
2019-03-10 05:00 | 1638 |  |  | 0
2019-03-10 06:00 | 1639 |  |  | 0
2019-03-10 07:00 | 1640 |  |  | 0.02192
2019-03-10 08:00 | 1641 |  |  | 0.10827
2019-03-10 09:00 | 1642 |  |  | 0.27538
2019-03-10 10:00 | 1643 |  |  | 0.51792
2019-03-10 11:00 | 1644 |  |  | 0.63161
2019-03-10 12:00 | 1645 |  |  | 0.73237
2019-03-10 13:00 | 1646 |  |  | 0.73821
2019-03-10 14:00 | 1647 |  |  | 0.69645
2019-03-10 15:00 | 1648 |  |  | 0.5796
2019-03-10 16:00 | 1649 |  |  | 0.3233
2019-03-10 17:00 | 1650 |  |  | 0.090932
2019-03-10 18:00 | 1651 |  |  | 0.001917
2019-03-10 19:00 | 1652 |  |  | 0
2019-03-10 20:00 | 1653 |  |  | 0
2019-03-10 21:00 | 1654 |  |  | 0
2019-03-10 22:00 | 1655 |  |  | 0
2019-03-10 23:00 | 1656 |  |  | 0
2019-03-11 | 1657 |  |  | 0
2019-03-11 01:00 | 1658 |  |  | 0
2019-03-11 02:00 | 1659 |  |  | 0
2019-03-11 03:00 | 1660 |  |  | 0
2019-03-11 04:00 | 1661 |  |  | 0
2019-03-11 05:00 | 1662 |  |  | 0
2019-03-11 06:00 | 1663 |  |  | 8.3347e-05
2019-03-11 07:00 | 1664 |  |  | 0.01942
2019-03-11 08:00 | 1665 |  |  | 0.15961
2019-03-11 09:00 | 1666 |  |  | 0.39857
2019-03-11 10:00 | 1667 |  |  | 0.59727
2019-03-11 11:00 | 1668 |  |  | 0.72537
2019-03-11 12:00 | 1669 |  |  | 0.46683
2019-03-11 13:00 | 1670 |  |  | 0.483
2019-03-11 14:00 | 1671 |  |  | 0.57276
2019-03-11 15:00 | 1672 |  |  | 0.56851
2019-03-11 16:00 | 1673 |  |  | 0.23104
2019-03-11 17:00 | 1674 |  |  | 0.066094
2019-03-11 18:00 | 1675 |  |  | 0.0072512
2019-03-11 19:00 | 1676 |  |  | 0
2019-03-11 20:00 | 1677 |  |  | 0
2019-03-11 21:00 | 1678 |  |  | 0
2019-03-11 22:00 | 1679 |  |  | 0
2019-03-11 23:00 | 1680 |  |  | 0
2019-03-12 | 1681 |  |  | 0
2019-03-12 01:00 | 1682 |  |  | 0
2019-03-12 02:00 | 1683 |  |  | 0
2019-03-12 03:00 | 1684 |  |  | 0
2019-03-12 04:00 | 1685 |  |  | 0
2019-03-12 05:00 | 1686 |  |  | 0
2019-03-12 06:00 | 1687 |  |  | 0.00016669
2019-03-12 07:00 | 1688 |  |  | 0.021004
2019-03-12 08:00 | 1689 |  |  | 0.16128
2019-03-12 09:00 | 1690 |  |  | 0.39157
2019-03-12 10:00 | 1691 |  |  | 0.57993
2019-03-12 11:00 | 1692 |  |  | 0.71429
2019-03-12 12:00 | 1693 |  |  | 0.78521
2019-03-12 13:00 | 1694 |  |  | 0.77655
2019-03-12 14:00 | 1695 |  |  | 0.75529
2019-03-12 15:00 | 1696 |  |  | 0.60193
2019-03-12 16:00 | 1697 |  |  | 0.40057
2019-03-12 17:00 | 1698 |  |  | 0.13419
2019-03-12 18:00 | 1699 |  |  | 0.004084
2019-03-12 19:00 | 1700 |  |  | 0
2019-03-12 20:00 | 1701 |  |  | 0
2019-03-12 21:00 | 1702 |  |  | 0
2019-03-12 22:00 | 1703 |  |  | 0
2019-03-12 23:00 | 1704 |  |  | 0
2019-03-13 | 1705 |  |  | 0
2019-03-13 01:00 | 1706 |  |  | 0
2019-03-13 02:00 | 1707 |  |  | 0
2019-03-13 03:00 | 1708 |  |  | 0
2019-03-13 04:00 | 1709 |  |  | 0
2019-03-13 05:00 | 1710 |  |  | 0
2019-03-13 06:00 | 1711 |  |  | 0.00016669
2019-03-13 07:00 | 1712 |  |  | 0.023504
2019-03-13 08:00 | 1713 |  |  | 0.16236
2019-03-13 09:00 | 1714 |  |  | 0.37923
2019-03-13 10:00 | 1715 |  |  | 0.58035
2019-03-13 11:00 | 1716 |  |  | 0.70395
2019-03-13 12:00 | 1717 |  |  | 0.76538
2019-03-13 13:00 | 1718 |  |  | 0.80055
2019-03-13 14:00 | 1719 |  |  | 0.78388
2019-03-13 15:00 | 1720 |  |  | 0.67461
2019-03-13 16:00 | 1721 |  |  | 0.45699
2019-03-13 17:00 | 1722 |  |  | 0.18636
2019-03-13 18:00 | 1723 |  |  | 0.0043341
2019-03-13 19:00 | 1724 |  |  | 0
2019-03-13 20:00 | 1725 |  |  | 0
2019-03-13 21:00 | 1726 |  |  | 0
2019-03-13 22:00 | 1727 |  |  | 0
2019-03-13 23:00 | 1728 |  |  | 0
2019-03-14 | 1729 |  |  | 0
2019-03-14 01:00 | 1730 |  |  | 0
2019-03-14 02:00 | 1731 |  |  | 0
2019-03-14 03:00 | 1732 |  |  | 0
2019-03-14 04:00 | 1733 |  |  | 0
2019-03-14 05:00 | 1734 |  |  | 0
2019-03-14 06:00 | 1735 |  |  | 0.00050008
2019-03-14 07:00 | 1736 |  |  | 0.023421
2019-03-14 08:00 | 1737 |  |  | 0.15678
2019-03-14 09:00 | 1738 |  |  | 0.38898
2019-03-14 10:00 | 1739 |  |  | 0.55784
2019-03-14 11:00 | 1740 |  |  | 0.65428
2019-03-14 12:00 | 1741 |  |  | 0.67395
2019-03-14 13:00 | 1742 |  |  | 0.70728
2019-03-14 14:00 | 1743 |  |  | 0.65886
2019-03-14 15:00 | 1744 |  |  | 0.46883
2019-03-14 16:00 | 1745 |  |  | 0.37648
2019-03-14 17:00 | 1746 |  |  | 0.15453
2019-03-14 18:00 | 1747 |  |  | 0.0060843
2019-03-14 19:00 | 1748 |  |  | 0
2019-03-14 20:00 | 1749 |  |  | 0
2019-03-14 21:00 | 1750 |  |  | 0
2019-03-14 22:00 | 1751 |  |  | 0
2019-03-14 23:00 | 1752 |  |  | 0
2019-03-15 | 1753 |  |  | 0
2019-03-15 01:00 | 1754 |  |  | 0
2019-03-15 02:00 | 1755 |  |  | 0
2019-03-15 03:00 | 1756 |  |  | 0
2019-03-15 04:00 | 1757 |  |  | 0
2019-03-15 05:00 | 1758 |  |  | 0
2019-03-15 06:00 | 1759 |  |  | 0.0010835
2019-03-15 07:00 | 1760 |  |  | 0.029338
2019-03-15 08:00 | 1761 |  |  | 0.1752
2019-03-15 09:00 | 1762 |  |  | 0.38181
2019-03-15 10:00 | 1763 |  |  | 0.55634
2019-03-15 11:00 | 1764 |  |  | 0.68261
2019-03-15 12:00 | 1765 |  |  | 0.7217
2019-03-15 13:00 | 1766 |  |  | 0.67761
2019-03-15 14:00 | 1767 |  |  | 0.6782
2019-03-15 15:00 | 1768 |  |  | 0.31297
2019-03-15 16:00 | 1769 |  |  | 0.18386
2019-03-15 17:00 | 1770 |  |  | 0.1787
2019-03-15 18:00 | 1771 |  |  | 0.014336
2019-03-15 19:00 | 1772 |  |  | 0
2019-03-15 20:00 | 1773 |  |  | 0
2019-03-15 21:00 | 1774 |  |  | 0
2019-03-15 22:00 | 1775 |  |  | 0
2019-03-15 23:00 | 1776 |  |  | 0
2019-03-16 | 1777 |  |  | 0
2019-03-16 01:00 | 1778 |  |  | 0
2019-03-16 02:00 | 1779 |  |  | 0
2019-03-16 03:00 | 1780 |  |  | 0
2019-03-16 04:00 | 1781 |  |  | 0
2019-03-16 05:00 | 1782 |  |  | 0
2019-03-16 06:00 | 1783 |  |  | 0.00016669
2019-03-16 07:00 | 1784 |  |  | 0.039173
2019-03-16 08:00 | 1785 |  |  | 0.14819
2019-03-16 09:00 | 1786 |  |  | 0.30963
2019-03-16 10:00 | 1787 |  |  | 0.46874
2019-03-16 11:00 | 1788 |  |  | 0.6236
2019-03-16 12:00 | 1789 |  |  | 0.75738
2019-03-16 13:00 | 1790 |  |  | 0.75213
2019-03-16 14:00 | 1791 |  |  | 0.72445
2019-03-16 15:00 | 1792 |  |  | 0.61802
2019-03-16 16:00 | 1793 |  |  | 0.42565
2019-03-16 17:00 | 1794 |  |  | 0.18136
2019-03-16 18:00 | 1795 |  |  | 0.0073346
2019-03-16 19:00 | 1796 |  |  | 0
2019-03-16 20:00 | 1797 |  |  | 0
2019-03-16 21:00 | 1798 |  |  | 0
2019-03-16 22:00 | 1799 |  |  | 0
2019-03-16 23:00 | 1800 |  |  | 0
2019-03-17 | 1801 |  |  | 0
2019-03-17 01:00 | 1802 |  |  | 0
2019-03-17 02:00 | 1803 |  |  | 0
2019-03-17 03:00 | 1804 |  |  | 0
2019-03-17 04:00 | 1805 |  |  | 0
2019-03-17 05:00 | 1806 |  |  | 0
2019-03-17 06:00 | 1807 |  |  | 0.0015003
2019-03-17 07:00 | 1808 |  |  | 0.04134
2019-03-17 08:00 | 1809 |  |  | 0.044841
2019-03-17 09:00 | 1810 |  |  | 0.091765
2019-03-17 10:00 | 1811 |  |  | 0.080263
2019-03-17 11:00 | 1812 |  |  | 0.090432
2019-03-17 12:00 | 1813 |  |  | 0.15761
2019-03-17 13:00 | 1814 |  |  | 0.19162
2019-03-17 14:00 | 1815 |  |  | 0.16136
2019-03-17 15:00 | 1816 |  |  | 0.15228
2019-03-17 16:00 | 1817 |  |  | 0.061927
2019-03-17 17:00 | 1818 |  |  | 0.028338
2019-03-17 18:00 | 1819 |  |  | 0.0015003
2019-03-17 19:00 | 1820 |  |  | 0
2019-03-17 20:00 | 1821 |  |  | 0
2019-03-17 21:00 | 1822 |  |  | 0
2019-03-17 22:00 | 1823 |  |  | 0
2019-03-17 23:00 | 1824 |  |  | 0
2019-03-18 | 1825 |  |  | 0
2019-03-18 01:00 | 1826 |  |  | 0
2019-03-18 02:00 | 1827 |  |  | 0
2019-03-18 03:00 | 1828 |  |  | 0
2019-03-18 04:00 | 1829 |  |  | 0
2019-03-18 05:00 | 1830 |  |  | 0
2019-03-18 06:00 | 1831 |  |  | 0.0025004
2019-03-18 07:00 | 1832 |  |  | 0.039423
2019-03-18 08:00 | 1833 |  |  | 0.13294
2019-03-18 09:00 | 1834 |  |  | 0.3924
2019-03-18 10:00 | 1835 |  |  | 0.59568
2019-03-18 11:00 | 1836 |  |  | 0.70878
2019-03-18 12:00 | 1837 |  |  | 0.78905
2019-03-18 13:00 | 1838 |  |  | 0.80605
2019-03-18 14:00 | 1839 |  |  | 0.77338
2019-03-18 15:00 | 1840 |  |  | 0.66203
2019-03-18 16:00 | 1841 |  |  | 0.48233
2019-03-18 17:00 | 1842 |  |  | 0.21429
2019-03-18 18:00 | 1843 |  |  | 0.011669
2019-03-18 19:00 | 1844 |  |  | 0
2019-03-18 20:00 | 1845 |  |  | 0
2019-03-18 21:00 | 1846 |  |  | 0
2019-03-18 22:00 | 1847 |  |  | 0
2019-03-18 23:00 | 1848 |  |  | 0
2019-03-19 | 1849 |  |  | 0
2019-03-19 01:00 | 1850 |  |  | 0
2019-03-19 02:00 | 1851 |  |  | 0
2019-03-19 03:00 | 1852 |  |  | 0
2019-03-19 04:00 | 1853 |  |  | 0
2019-03-19 05:00 | 1854 |  |  | 0
2019-03-19 06:00 | 1855 |  |  | 0.001917
2019-03-19 07:00 | 1856 |  |  | 0.030588
2019-03-19 08:00 | 1857 |  |  | 0.18036
2019-03-19 09:00 | 1858 |  |  | 0.40757
2019-03-19 10:00 | 1859 |  |  | 0.58943
2019-03-19 11:00 | 1860 |  |  | 0.74671
2019-03-19 12:00 | 1861 |  |  | 0.81347
2019-03-19 13:00 | 1862 |  |  | 0.81739
2019-03-19 14:00 | 1863 |  |  | 0.77671
2019-03-19 15:00 | 1864 |  |  | 0.64761
2019-03-19 16:00 | 1865 |  |  | 0.46991
2019-03-19 17:00 | 1866 |  |  | 0.21145
2019-03-19 18:00 | 1867 |  |  | 0.011502
2019-03-19 19:00 | 1868 |  |  | 0
2019-03-19 20:00 | 1869 |  |  | 0
2019-03-19 21:00 | 1870 |  |  | 0
2019-03-19 22:00 | 1871 |  |  | 0
2019-03-19 23:00 | 1872 |  |  | 0
2019-03-20 | 1873 |  |  | 0
2019-03-20 01:00 | 1874 |  |  | 0
2019-03-20 02:00 | 1875 |  |  | 0
2019-03-20 03:00 | 1876 |  |  | 0
2019-03-20 04:00 | 1877 |  |  | 0
2019-03-20 05:00 | 1878 |  |  | 0
2019-03-20 06:00 | 1879 |  |  | 0.0022504
2019-03-20 07:00 | 1880 |  |  | 0.053092
2019-03-20 08:00 | 1881 |  |  | 0.13944
2019-03-20 09:00 | 1882 |  |  | 0.38723
2019-03-20 10:00 | 1883 |  |  | 0.58443
2019-03-20 11:00 | 1884 |  |  | 0.76079
2019-03-20 12:00 | 1885 |  |  | 0.61219
2019-03-20 13:00 | 1886 |  |  | 0.77571
2019-03-20 14:00 | 1887 |  |  | 0.73696
2019-03-20 15:00 | 1888 |  |  | 0.63444
2019-03-20 16:00 | 1889 |  |  | 0.44774
2019-03-20 17:00 | 1890 |  |  | 0.18661
2019-03-20 18:00 | 1891 |  |  | 0.012169
2019-03-20 19:00 | 1892 |  |  | 0
2019-03-20 20:00 | 1893 |  |  | 0
2019-03-20 21:00 | 1894 |  |  | 0
2019-03-20 22:00 | 1895 |  |  | 0
2019-03-20 23:00 | 1896 |  |  | 0
2019-03-21 | 1897 |  |  | 0
2019-03-21 01:00 | 1898 |  |  | 0
2019-03-21 02:00 | 1899 |  |  | 0
2019-03-21 03:00 | 1900 |  |  | 0
2019-03-21 04:00 | 1901 |  |  | 0
2019-03-21 05:00 | 1902 |  |  | 0
2019-03-21 06:00 | 1903 |  |  | 0.0031672
2019-03-21 07:00 | 1904 |  |  | 0.04059
2019-03-21 08:00 | 1905 |  |  | 0.18603
2019-03-21 09:00 | 1906 |  |  | 0.40407
2019-03-21 10:00 | 1907 |  |  | 0.58026
2019-03-21 11:00 | 1908 |  |  | 0.70662
2019-03-21 12:00 | 1909 |  |  | 0.77296
2019-03-21 13:00 | 1910 |  |  | 0.78138
2019-03-21 14:00 | 1911 |  |  | 0.74487
2019-03-21 15:00 | 1912 |  |  | 0.63652
2019-03-21 16:00 | 1913 |  |  | 0.44182
2019-03-21 17:00 | 1914 |  |  | 0.20028
2019-03-21 18:00 | 1915 |  |  | 0.015586
2019-03-21 19:00 | 1916 |  |  | 0
2019-03-21 20:00 | 1917 |  |  | 0
2019-03-21 21:00 | 1918 |  |  | 0
2019-03-21 22:00 | 1919 |  |  | 0
2019-03-21 23:00 | 1920 |  |  | 0
2019-03-22 | 1921 |  |  | 0
2019-03-22 01:00 | 1922 |  |  | 0
2019-03-22 02:00 | 1923 |  |  | 0
2019-03-22 03:00 | 1924 |  |  | 0
2019-03-22 04:00 | 1925 |  |  | 0
2019-03-22 05:00 | 1926 |  |  | 0
2019-03-22 06:00 | 1927 |  |  | 0.0034172
2019-03-22 07:00 | 1928 |  |  | 0.03909
2019-03-22 08:00 | 1929 |  |  | 0.18911
2019-03-22 09:00 | 1930 |  |  | 0.40773
2019-03-22 10:00 | 1931 |  |  | 0.58801
2019-03-22 11:00 | 1932 |  |  | 0.70445
2019-03-22 12:00 | 1933 |  |  | 0.76521
2019-03-22 13:00 | 1934 |  |  | 0.77663
2019-03-22 14:00 | 1935 |  |  | 0.73187
2019-03-22 15:00 | 1936 |  |  | 0.62919
2019-03-22 16:00 | 1937 |  |  | 0.44957
2019-03-22 17:00 | 1938 |  |  | 0.19695
2019-03-22 18:00 | 1939 |  |  | 0.014169
2019-03-22 19:00 | 1940 |  |  | 0
2019-03-22 20:00 | 1941 |  |  | 0
2019-03-22 21:00 | 1942 |  |  | 0
2019-03-22 22:00 | 1943 |  |  | 0
2019-03-22 23:00 | 1944 |  |  | 0
2019-03-23 | 1945 |  |  | 0
2019-03-23 01:00 | 1946 |  |  | 0
2019-03-23 02:00 | 1947 |  |  | 0
2019-03-23 03:00 | 1948 |  |  | 0
2019-03-23 04:00 | 1949 |  |  | 0
2019-03-23 05:00 | 1950 |  |  | 0
2019-03-23 06:00 | 1951 |  |  | 0.0040007
2019-03-23 07:00 | 1952 |  |  | 0.040673
2019-03-23 08:00 | 1953 |  |  | 0.18878
2019-03-23 09:00 | 1954 |  |  | 0.39932
2019-03-23 10:00 | 1955 |  |  | 0.57335
2019-03-23 11:00 | 1956 |  |  | 0.6892
2019-03-23 12:00 | 1957 |  |  | 0.74412
2019-03-23 13:00 | 1958 |  |  | 0.74571
2019-03-23 14:00 | 1959 |  |  | 0.70003
2019-03-23 15:00 | 1960 |  |  | 0.59977
2019-03-23 16:00 | 1961 |  |  | 0.43199
2019-03-23 17:00 | 1962 |  |  | 0.18786
2019-03-23 18:00 | 1963 |  |  | 0.015169
2019-03-23 19:00 | 1964 |  |  | 0
2019-03-23 20:00 | 1965 |  |  | 0
2019-03-23 21:00 | 1966 |  |  | 0
2019-03-23 22:00 | 1967 |  |  | 0
2019-03-23 23:00 | 1968 |  |  | 0
2019-03-24 | 1969 |  |  | 0
2019-03-24 01:00 | 1970 |  |  | 0
2019-03-24 02:00 | 1971 |  |  | 0
2019-03-24 03:00 | 1972 |  |  | 0
2019-03-24 04:00 | 1973 |  |  | 0
2019-03-24 05:00 | 1974 |  |  | 0
2019-03-24 06:00 | 1975 |  |  | 0.0047508
2019-03-24 07:00 | 1976 |  |  | 0.044841
2019-03-24 08:00 | 1977 |  |  | 0.18678
2019-03-24 09:00 | 1978 |  |  | 0.39215
2019-03-24 10:00 | 1979 |  |  | 0.56651
2019-03-24 11:00 | 1980 |  |  | 0.6882
2019-03-24 12:00 | 1981 |  |  | 0.74821
2019-03-24 13:00 | 1982 |  |  | 0.75088
2019-03-24 14:00 | 1983 |  |  | 0.7092
2019-03-24 15:00 | 1984 |  |  | 0.61319
2019-03-24 16:00 | 1985 |  |  | 0.43491
2019-03-24 17:00 | 1986 |  |  | 0.18811
2019-03-24 18:00 | 1987 |  |  | 0.019087
2019-03-24 19:00 | 1988 |  |  | 0
2019-03-24 20:00 | 1989 |  |  | 0
2019-03-24 21:00 | 1990 |  |  | 0
2019-03-24 22:00 | 1991 |  |  | 0
2019-03-24 23:00 | 1992 |  |  | 0
2019-03-25 | 1993 |  |  | 0
2019-03-25 01:00 | 1994 |  |  | 0
2019-03-25 02:00 | 1995 |  |  | 0
2019-03-25 03:00 | 1996 |  |  | 0
2019-03-25 04:00 | 1997 |  |  | 0
2019-03-25 05:00 | 1998 |  |  | 0
2019-03-25 06:00 | 1999 |  |  | 0.0042507
2019-03-25 07:00 | 2000 |  |  | 0.038673
2019-03-25 08:00 | 2001 |  |  | 0.19487
2019-03-25 09:00 | 2002 |  |  | 0.4119
2019-03-25 10:00 | 2003 |  |  | 0.5816
2019-03-25 11:00 | 2004 |  |  | 0.68853
2019-03-25 12:00 | 2005 |  |  | 0.74354
2019-03-25 13:00 | 2006 |  |  | 0.74879
2019-03-25 14:00 | 2007 |  |  | 0.70203
2019-03-25 15:00 | 2008 |  |  | 0.59402
2019-03-25 16:00 | 2009 |  |  | 0.40923
2019-03-25 17:00 | 2010 |  |  | 0.21204
2019-03-25 18:00 | 2011 |  |  | 0.021837
2019-03-25 19:00 | 2012 |  |  | 0
2019-03-25 20:00 | 2013 |  |  | 0
2019-03-25 21:00 | 2014 |  |  | 0
2019-03-25 22:00 | 2015 |  |  | 0
2019-03-25 23:00 | 2016 |  |  | 0
2019-03-26 | 2017 |  |  | 0
2019-03-26 01:00 | 2018 |  |  | 0
2019-03-26 02:00 | 2019 |  |  | 0
2019-03-26 03:00 | 2020 |  |  | 0
2019-03-26 04:00 | 2021 |  |  | 0
2019-03-26 05:00 | 2022 |  |  | 0
2019-03-26 06:00 | 2023 |  |  | 0.0092515
2019-03-26 07:00 | 2024 |  |  | 0.050008
2019-03-26 08:00 | 2025 |  |  | 0.14586
2019-03-26 09:00 | 2026 |  |  | 0.36014
2019-03-26 10:00 | 2027 |  |  | 0.60718
2019-03-26 11:00 | 2028 |  |  | 0.72895
2019-03-26 12:00 | 2029 |  |  | 0.79738
2019-03-26 13:00 | 2030 |  |  | 0.82697
2019-03-26 14:00 | 2031 |  |  | 0.77905
2019-03-26 15:00 | 2032 |  |  | 0.66694
2019-03-26 16:00 | 2033 |  |  | 0.49408
2019-03-26 17:00 | 2034 |  |  | 0.23621
2019-03-26 18:00 | 2035 |  |  | 0.025421
2019-03-26 19:00 | 2036 |  |  | 0
2019-03-26 20:00 | 2037 |  |  | 0
2019-03-26 21:00 | 2038 |  |  | 0
2019-03-26 22:00 | 2039 |  |  | 0
2019-03-26 23:00 | 2040 |  |  | 0
2019-03-27 | 2041 |  |  | 0
2019-03-27 01:00 | 2042 |  |  | 0
2019-03-27 02:00 | 2043 |  |  | 0
2019-03-27 03:00 | 2044 |  |  | 0
2019-03-27 04:00 | 2045 |  |  | 0
2019-03-27 05:00 | 2046 |  |  | 0
2019-03-27 06:00 | 2047 |  |  | 0.0032505
2019-03-27 07:00 | 2048 |  |  | 0.055426
2019-03-27 08:00 | 2049 |  |  | 0.19828
2019-03-27 09:00 | 2050 |  |  | 0.41474
2019-03-27 10:00 | 2051 |  |  | 0.6026
2019-03-27 11:00 | 2052 |  |  | 0.72412
2019-03-27 12:00 | 2053 |  |  | 0.78055
2019-03-27 13:00 | 2054 |  |  | 0.79172
2019-03-27 14:00 | 2055 |  |  | 0.74379
2019-03-27 15:00 | 2056 |  |  | 0.63619
2019-03-27 16:00 | 2057 |  |  | 0.47616
2019-03-27 17:00 | 2058 |  |  | 0.2152
2019-03-27 18:00 | 2059 |  |  | 0.021087
2019-03-27 19:00 | 2060 |  |  | 0
2019-03-27 20:00 | 2061 |  |  | 0
2019-03-27 21:00 | 2062 |  |  | 0
2019-03-27 22:00 | 2063 |  |  | 0
2019-03-27 23:00 | 2064 |  |  | 0
2019-03-28 | 2065 |  |  | 0
2019-03-28 01:00 | 2066 |  |  | 0
2019-03-28 02:00 | 2067 |  |  | 0
2019-03-28 03:00 | 2068 |  |  | 0
2019-03-28 04:00 | 2069 |  |  | 0
2019-03-28 05:00 | 2070 |  |  | 0
2019-03-28 06:00 | 2071 |  |  | 0.0076679
2019-03-28 07:00 | 2072 |  |  | 0.053342
2019-03-28 08:00 | 2073 |  |  | 0.20312
2019-03-28 09:00 | 2074 |  |  | 0.41182
2019-03-28 10:00 | 2075 |  |  | 0.58526
2019-03-28 11:00 | 2076 |  |  | 0.71004
2019-03-28 12:00 | 2077 |  |  | 0.76288
2019-03-28 13:00 | 2078 |  |  | 0.77596
2019-03-28 14:00 | 2079 |  |  | 0.72812
2019-03-28 15:00 | 2080 |  |  | 0.62019
2019-03-28 16:00 | 2081 |  |  | 0.44849
2019-03-28 17:00 | 2082 |  |  | 0.2007
2019-03-28 18:00 | 2083 |  |  | 0.021587
2019-03-28 19:00 | 2084 |  |  | 0
2019-03-28 20:00 | 2085 |  |  | 0
2019-03-28 21:00 | 2086 |  |  | 0
2019-03-28 22:00 | 2087 |  |  | 0
2019-03-28 23:00 | 2088 |  |  | 0
2019-03-29 | 2089 |  |  | 0
2019-03-29 01:00 | 2090 |  |  | 0
2019-03-29 02:00 | 2091 |  |  | 0
2019-03-29 03:00 | 2092 |  |  | 0
2019-03-29 04:00 | 2093 |  |  | 0
2019-03-29 05:00 | 2094 |  |  | 0
2019-03-29 06:00 | 2095 |  |  | 0.0029172
2019-03-29 07:00 | 2096 |  |  | 0.029005
2019-03-29 08:00 | 2097 |  |  | 0.19187
2019-03-29 09:00 | 2098 |  |  | 0.3869
2019-03-29 10:00 | 2099 |  |  | 0.56534
2019-03-29 11:00 | 2100 |  |  | 0.68778
2019-03-29 12:00 | 2101 |  |  | 0.74554
2019-03-29 13:00 | 2102 |  |  | 0.74029
2019-03-29 14:00 | 2103 |  |  | 0.71937
2019-03-29 15:00 | 2104 |  |  | 0.62519
2019-03-29 16:00 | 2105 |  |  | 0.42732
2019-03-29 17:00 | 2106 |  |  | 0.18253
2019-03-29 18:00 | 2107 |  |  | 0.021254
2019-03-29 19:00 | 2108 |  |  | 0
2019-03-29 20:00 | 2109 |  |  | 0
2019-03-29 21:00 | 2110 |  |  | 0
2019-03-29 22:00 | 2111 |  |  | 0
2019-03-29 23:00 | 2112 |  |  | 0
2019-03-30 | 2113 |  |  | 0
2019-03-30 01:00 | 2114 |  |  | 0
2019-03-30 02:00 | 2115 |  |  | 0
2019-03-30 03:00 | 2116 |  |  | 0
2019-03-30 04:00 | 2117 |  |  | 0
2019-03-30 05:00 | 2118 |  |  | 0
2019-03-30 06:00 | 2119 |  |  | 0.0085848
2019-03-30 07:00 | 2120 |  |  | 0.055676
2019-03-30 08:00 | 2121 |  |  | 0.21087
2019-03-30 09:00 | 2122 |  |  | 0.41982
2019-03-30 10:00 | 2123 |  |  | 0.59168
2019-03-30 11:00 | 2124 |  |  | 0.70078
2019-03-30 12:00 | 2125 |  |  | 0.76479
2019-03-30 13:00 | 2126 |  |  | 0.75946
2019-03-30 14:00 | 2127 |  |  | 0.7092
2019-03-30 15:00 | 2128 |  |  | 0.59843
2019-03-30 16:00 | 2129 |  |  | 0.44357
2019-03-30 17:00 | 2130 |  |  | 0.20978
2019-03-30 18:00 | 2131 |  |  | 0.028171
2019-03-30 19:00 | 2132 |  |  | 0
2019-03-30 20:00 | 2133 |  |  | 0
2019-03-30 21:00 | 2134 |  |  | 0
2019-03-30 22:00 | 2135 |  |  | 0
2019-03-30 23:00 | 2136 |  |  | 0
2019-03-31 | 2137 |  |  | 0
2019-03-31 01:00 | 2138 |  |  | 0
2019-03-31 02:00 | 2139 |  |  | 0
2019-03-31 03:00 | 2140 |  |  | 0
2019-03-31 04:00 | 2141 |  |  | 0
2019-03-31 05:00 | 2142 |  |  | 0
2019-03-31 06:00 | 2143 |  |  | 0.0094182
2019-03-31 07:00 | 2144 |  |  | 0.058343
2019-03-31 08:00 | 2145 |  |  | 0.21212
2019-03-31 09:00 | 2146 |  |  | 0.41282
2019-03-31 10:00 | 2147 |  |  | 0.57843
2019-03-31 11:00 | 2148 |  |  | 0.69737
2019-03-31 12:00 | 2149 |  |  | 0.75554
2019-03-31 13:00 | 2150 |  |  | 0.75929
2019-03-31 14:00 | 2151 |  |  | 0.70453
2019-03-31 15:00 | 2152 |  |  | 0.61369
2019-03-31 16:00 | 2153 |  |  | 0.45066
2019-03-31 17:00 | 2154 |  |  | 0.2212
2019-03-31 18:00 | 2155 |  |  | 0.025338
2019-03-31 19:00 | 2156 |  |  | 0
2019-03-31 20:00 | 2157 |  |  | 0
2019-03-31 21:00 | 2158 |  |  | 0
2019-03-31 22:00 | 2159 |  |  | 0
2019-03-31 23:00 | 2160 |  |  | 0
2019-04-01 | 2161 |  |  | 0
2019-04-01 01:00 | 2162 |  |  | 0
2019-04-01 02:00 | 2163 |  |  | 0
2019-04-01 03:00 | 2164 |  |  | 0
2019-04-01 04:00 | 2165 |  |  | 0
2019-04-01 05:00 | 2166 |  |  | 0
2019-04-01 06:00 | 2167 |  |  | 0.011502
2019-04-01 07:00 | 2168 |  |  | 0.071512
2019-04-01 08:00 | 2169 |  |  | 0.2207
2019-04-01 09:00 | 2170 |  |  | 0.3924
2019-04-01 10:00 | 2171 |  |  | 0.51009
2019-04-01 11:00 | 2172 |  |  | 0.5936
2019-04-01 12:00 | 2173 |  |  | 0.70853
2019-04-01 13:00 | 2174 |  |  | 0.7067
2019-04-01 14:00 | 2175 |  |  | 0.6216
2019-04-01 15:00 | 2176 |  |  | 0.31239
2019-04-01 16:00 | 2177 |  |  | 0.32172
2019-04-01 17:00 | 2178 |  |  | 0.13594
2019-04-01 18:00 | 2179 |  |  | 0.016003
2019-04-01 19:00 | 2180 |  |  | 0
2019-04-01 20:00 | 2181 |  |  | 0
2019-04-01 21:00 | 2182 |  |  | 0
2019-04-01 22:00 | 2183 |  |  | 0
2019-04-01 23:00 | 2184 |  |  | 0
2019-04-02 | 2185 |  |  | 0
2019-04-02 01:00 | 2186 |  |  | 0
2019-04-02 02:00 | 2187 |  |  | 0
2019-04-02 03:00 | 2188 |  |  | 0
2019-04-02 04:00 | 2189 |  |  | 0
2019-04-02 05:00 | 2190 |  |  | 0
2019-04-02 06:00 | 2191 |  |  | 0.014002
2019-04-02 07:00 | 2192 |  |  | 0.086514
2019-04-02 08:00 | 2193 |  |  | 0.14836
2019-04-02 09:00 | 2194 |  |  | 0.32147
2019-04-02 10:00 | 2195 |  |  | 0.49233
2019-04-02 11:00 | 2196 |  |  | 0.5295
2019-04-02 12:00 | 2197 |  |  | 0.55768
2019-04-02 13:00 | 2198 |  |  | 0.5826
2019-04-02 14:00 | 2199 |  |  | 0.37323
2019-04-02 15:00 | 2200 |  |  | 0.21445
2019-04-02 16:00 | 2201 |  |  | 0.11477
2019-04-02 17:00 | 2202 |  |  | 0.065678
2019-04-02 18:00 | 2203 |  |  | 0.015086
2019-04-02 19:00 | 2204 |  |  | 0
2019-04-02 20:00 | 2205 |  |  | 0
2019-04-02 21:00 | 2206 |  |  | 0
2019-04-02 22:00 | 2207 |  |  | 0
2019-04-02 23:00 | 2208 |  |  | 0
2019-04-03 | 2209 |  |  | 0
2019-04-03 01:00 | 2210 |  |  | 0
2019-04-03 02:00 | 2211 |  |  | 0
2019-04-03 03:00 | 2212 |  |  | 0
2019-04-03 04:00 | 2213 |  |  | 0
2019-04-03 05:00 | 2214 |  |  | 0
2019-04-03 06:00 | 2215 |  |  | 0.003834
2019-04-03 07:00 | 2216 |  |  | 0.072012
2019-04-03 08:00 | 2217 |  |  | 0.095849
2019-04-03 09:00 | 2218 |  |  | 0.16128
2019-04-03 10:00 | 2219 |  |  | 0.3749
2019-04-03 11:00 | 2220 |  |  | 0.41915
2019-04-03 12:00 | 2221 |  |  | 0.19737
2019-04-03 13:00 | 2222 |  |  | 0.093016
2019-04-03 14:00 | 2223 |  |  | 0.065511
2019-04-03 15:00 | 2224 |  |  | 0.071595
2019-04-03 16:00 | 2225 |  |  | 0.028505
2019-04-03 17:00 | 2226 |  |  | 0.015669
2019-04-03 18:00 | 2227 |  |  | 0.0012502
2019-04-03 19:00 | 2228 |  |  | 0
2019-04-03 20:00 | 2229 |  |  | 0
2019-04-03 21:00 | 2230 |  |  | 0
2019-04-03 22:00 | 2231 |  |  | 0
2019-04-03 23:00 | 2232 |  |  | 0
2019-04-04 | 2233 |  |  | 0
2019-04-04 01:00 | 2234 |  |  | 0
2019-04-04 02:00 | 2235 |  |  | 0
2019-04-04 03:00 | 2236 |  |  | 0
2019-04-04 04:00 | 2237 |  |  | 0
2019-04-04 05:00 | 2238 |  |  | 0
2019-04-04 06:00 | 2239 |  |  | 0.017253
2019-04-04 07:00 | 2240 |  |  | 0.056509
2019-04-04 08:00 | 2241 |  |  | 0.082597
2019-04-04 09:00 | 2242 |  |  | 0.12519
2019-04-04 10:00 | 2243 |  |  | 0.18961
2019-04-04 11:00 | 2244 |  |  | 0.15253
2019-04-04 12:00 | 2245 |  |  | 0.5045
2019-04-04 13:00 | 2246 |  |  | 0.33331
2019-04-04 14:00 | 2247 |  |  | 0.19303
2019-04-04 15:00 | 2248 |  |  | 0.14144
2019-04-04 16:00 | 2249 |  |  | 0.07868
2019-04-04 17:00 | 2250 |  |  | 0.007918
2019-04-04 18:00 | 2251 |  |  | 0
2019-04-04 19:00 | 2252 |  |  | 0
2019-04-04 20:00 | 2253 |  |  | 0
2019-04-04 21:00 | 2254 |  |  | 0
2019-04-04 22:00 | 2255 |  |  | 0
2019-04-04 23:00 | 2256 |  |  | 0
2019-04-05 | 2257 |  |  | 0
2019-04-05 01:00 | 2258 |  |  | 0
2019-04-05 02:00 | 2259 |  |  | 0
2019-04-05 03:00 | 2260 |  |  | 0
2019-04-05 04:00 | 2261 |  |  | 0
2019-04-05 05:00 | 2262 |  |  | 0
2019-04-05 06:00 | 2263 |  |  | 0.024004
2019-04-05 07:00 | 2264 |  |  | 0.097516
2019-04-05 08:00 | 2265 |  |  | 0.26896
2019-04-05 09:00 | 2266 |  |  | 0.46008
2019-04-05 10:00 | 2267 |  |  | 0.63352
2019-04-05 11:00 | 2268 |  |  | 0.74046
2019-04-05 12:00 | 2269 |  |  | 0.7943
2019-04-05 13:00 | 2270 |  |  | 0.81639
2019-04-05 14:00 | 2271 |  |  | 0.7743
2019-04-05 15:00 | 2272 |  |  | 0.67136
2019-04-05 16:00 | 2273 |  |  | 0.51817
2019-04-05 17:00 | 2274 |  |  | 0.26196
2019-04-05 18:00 | 2275 |  |  | 0.028505
2019-04-05 19:00 | 2276 |  |  | 0
2019-04-05 20:00 | 2277 |  |  | 0
2019-04-05 21:00 | 2278 |  |  | 0
2019-04-05 22:00 | 2279 |  |  | 0
2019-04-05 23:00 | 2280 |  |  | 0
2019-04-06 | 2281 |  |  | 0
2019-04-06 01:00 | 2282 |  |  | 0
2019-04-06 02:00 | 2283 |  |  | 0
2019-04-06 03:00 | 2284 |  |  | 0
2019-04-06 04:00 | 2285 |  |  | 0
2019-04-06 05:00 | 2286 |  |  | 0
2019-04-06 06:00 | 2287 |  |  | 0.016586
2019-04-06 07:00 | 2288 |  |  | 0.10927
2019-04-06 08:00 | 2289 |  |  | 0.17028
2019-04-06 09:00 | 2290 |  |  | 0.40065
2019-04-06 10:00 | 2291 |  |  | 0.44482
2019-04-06 11:00 | 2292 |  |  | 0.60652
2019-04-06 12:00 | 2293 |  |  | 0.42515
2019-04-06 13:00 | 2294 |  |  | 0.16911
2019-04-06 14:00 | 2295 |  |  | 0.35006
2019-04-06 15:00 | 2296 |  |  | 0.13494
2019-04-06 16:00 | 2297 |  |  | 0.036423
2019-04-06 17:00 | 2298 |  |  | 0.003834
2019-04-06 18:00 | 2299 |  |  | 0.0020837
2019-04-06 19:00 | 2300 |  |  | 0
2019-04-06 20:00 | 2301 |  |  | 0
2019-04-06 21:00 | 2302 |  |  | 0
2019-04-06 22:00 | 2303 |  |  | 0
2019-04-06 23:00 | 2304 |  |  | 0
2019-04-07 | 2305 |  |  | 0
2019-04-07 01:00 | 2306 |  |  | 0
2019-04-07 02:00 | 2307 |  |  | 0
2019-04-07 03:00 | 2308 |  |  | 0
2019-04-07 04:00 | 2309 |  |  | 0
2019-04-07 05:00 | 2310 |  |  | 0
2019-04-07 06:00 | 2311 |  |  | 0.0053342
2019-04-07 07:00 | 2312 |  |  | 0.052425
2019-04-07 08:00 | 2313 |  |  | 0.088431
2019-04-07 09:00 | 2314 |  |  | 0.16494
2019-04-07 10:00 | 2315 |  |  | 0.1797
2019-04-07 11:00 | 2316 |  |  | 0.14052
2019-04-07 12:00 | 2317 |  |  | 0.20545
2019-04-07 13:00 | 2318 |  |  | 0.2102
2019-04-07 14:00 | 2319 |  |  | 0.063094
2019-04-07 15:00 | 2320 |  |  | 0.070095
2019-04-07 16:00 | 2321 |  |  | 0.18603
2019-04-07 17:00 | 2322 |  |  | 0.1141
2019-04-07 18:00 | 2323 |  |  | 0.036256
2019-04-07 19:00 | 2324 |  |  | 0
2019-04-07 20:00 | 2325 |  |  | 0
2019-04-07 21:00 | 2326 |  |  | 0
2019-04-07 22:00 | 2327 |  |  | 0
2019-04-07 23:00 | 2328 |  |  | 0
2019-04-08 | 2329 |  |  | 0
2019-04-08 01:00 | 2330 |  |  | 0
2019-04-08 02:00 | 2331 |  |  | 0
2019-04-08 03:00 | 2332 |  |  | 0
2019-04-08 04:00 | 2333 |  |  | 0
2019-04-08 05:00 | 2334 |  |  | 0
2019-04-08 06:00 | 2335 |  |  | 0.013086
2019-04-08 07:00 | 2336 |  |  | 0.062677
2019-04-08 08:00 | 2337 |  |  | 0.25721
2019-04-08 09:00 | 2338 |  |  | 0.47725
2019-04-08 10:00 | 2339 |  |  | 0.64902
2019-04-08 11:00 | 2340 |  |  | 0.76196
2019-04-08 12:00 | 2341 |  |  | 0.81555
2019-04-08 13:00 | 2342 |  |  | 0.82105
2019-04-08 14:00 | 2343 |  |  | 0.77505
2019-04-08 15:00 | 2344 |  |  | 0.68153
2019-04-08 16:00 | 2345 |  |  | 0.52659
2019-04-08 17:00 | 2346 |  |  | 0.30047
2019-04-08 18:00 | 2347 |  |  | 0.047758
2019-04-08 19:00 | 2348 |  |  | 0
2019-04-08 20:00 | 2349 |  |  | 0
2019-04-08 21:00 | 2350 |  |  | 0
2019-04-08 22:00 | 2351 |  |  | 0
2019-04-08 23:00 | 2352 |  |  | 0
2019-04-09 | 2353 |  |  | 0
2019-04-09 01:00 | 2354 |  |  | 0
2019-04-09 02:00 | 2355 |  |  | 0
2019-04-09 03:00 | 2356 |  |  | 0
2019-04-09 04:00 | 2357 |  |  | 0
2019-04-09 05:00 | 2358 |  |  | 0
2019-04-09 06:00 | 2359 |  |  | 0.024504
2019-04-09 07:00 | 2360 |  |  | 0.061927
2019-04-09 08:00 | 2361 |  |  | 0.25379
2019-04-09 09:00 | 2362 |  |  | 0.46191
2019-04-09 10:00 | 2363 |  |  | 0.6156
2019-04-09 11:00 | 2364 |  |  | 0.71904
2019-04-09 12:00 | 2365 |  |  | 0.8043
2019-04-09 13:00 | 2366 |  |  | 0.7888
2019-04-09 14:00 | 2367 |  |  | 0.77188
2019-04-09 15:00 | 2368 |  |  | 0.42332
2019-04-09 16:00 | 2369 |  |  | 0.26688
2019-04-09 17:00 | 2370 |  |  | 0.17778
2019-04-09 18:00 | 2371 |  |  | 0.025338
2019-04-09 19:00 | 2372 |  |  | 8.3347e-05
2019-04-09 20:00 | 2373 |  |  | 0
2019-04-09 21:00 | 2374 |  |  | 0
2019-04-09 22:00 | 2375 |  |  | 0
2019-04-09 23:00 | 2376 |  |  | 0
2019-04-10 | 2377 |  |  | 0
2019-04-10 01:00 | 2378 |  |  | 0
2019-04-10 02:00 | 2379 |  |  | 0
2019-04-10 03:00 | 2380 |  |  | 0
2019-04-10 04:00 | 2381 |  |  | 0
2019-04-10 05:00 | 2382 |  |  | 0
2019-04-10 06:00 | 2383 |  |  | 0.014336
2019-04-10 07:00 | 2384 |  |  | 0.073762
2019-04-10 08:00 | 2385 |  |  | 0.22262
2019-04-10 09:00 | 2386 |  |  | 0.40065
2019-04-10 10:00 | 2387 |  |  | 0.43941
2019-04-10 11:00 | 2388 |  |  | 0.64044
2019-04-10 12:00 | 2389 |  |  | 0.34972
2019-04-10 13:00 | 2390 |  |  | 0.35114
2019-04-10 14:00 | 2391 |  |  | 0.3293
2019-04-10 15:00 | 2392 |  |  | 0.35023
2019-04-10 16:00 | 2393 |  |  | 0.061427
2019-04-10 17:00 | 2394 |  |  | 0.11827
2019-04-10 18:00 | 2395 |  |  | 0.02117
2019-04-10 19:00 | 2396 |  |  | 0
2019-04-10 20:00 | 2397 |  |  | 0
2019-04-10 21:00 | 2398 |  |  | 0
2019-04-10 22:00 | 2399 |  |  | 0
2019-04-10 23:00 | 2400 |  |  | 0
2019-04-11 | 2401 |  |  | 0
2019-04-11 01:00 | 2402 |  |  | 0
2019-04-11 02:00 | 2403 |  |  | 0
2019-04-11 03:00 | 2404 |  |  | 0
2019-04-11 04:00 | 2405 |  |  | 0
2019-04-11 05:00 | 2406 |  |  | 0
2019-04-11 06:00 | 2407 |  |  | 0.007918
2019-04-11 07:00 | 2408 |  |  | 0.02292
2019-04-11 08:00 | 2409 |  |  | 0.076763
2019-04-11 09:00 | 2410 |  |  | 0.1832
2019-04-11 10:00 | 2411 |  |  | 0.28821
2019-04-11 11:00 | 2412 |  |  | 0.33006
2019-04-11 12:00 | 2413 |  |  | 0.25621
2019-04-11 13:00 | 2414 |  |  | 0.14494
2019-04-11 14:00 | 2415 |  |  | 0.041674
2019-04-11 15:00 | 2416 |  |  | 0.069428
2019-04-11 16:00 | 2417 |  |  | 0.043007
2019-04-11 17:00 | 2418 |  |  | 0.0048341
2019-04-11 18:00 | 2419 |  |  | 0.0033339
2019-04-11 19:00 | 2420 |  |  | 0
2019-04-11 20:00 | 2421 |  |  | 0
2019-04-11 21:00 | 2422 |  |  | 0
2019-04-11 22:00 | 2423 |  |  | 0
2019-04-11 23:00 | 2424 |  |  | 0
2019-04-12 | 2425 |  |  | 0
2019-04-12 01:00 | 2426 |  |  | 0
2019-04-12 02:00 | 2427 |  |  | 0
2019-04-12 03:00 | 2428 |  |  | 0
2019-04-12 04:00 | 2429 |  |  | 0
2019-04-12 05:00 | 2430 |  |  | 0
2019-04-12 06:00 | 2431 |  |  | 0.0020003
2019-04-12 07:00 | 2432 |  |  | 0.015586
2019-04-12 08:00 | 2433 |  |  | 0.10252
2019-04-12 09:00 | 2434 |  |  | 0.1967
2019-04-12 10:00 | 2435 |  |  | 0.18103
2019-04-12 11:00 | 2436 |  |  | 0.079513
2019-04-12 12:00 | 2437 |  |  | 0.43907
2019-04-12 13:00 | 2438 |  |  | 0.56009
2019-04-12 14:00 | 2439 |  |  | 0.65811
2019-04-12 15:00 | 2440 |  |  | 0.39457
2019-04-12 16:00 | 2441 |  |  | 0.37848
2019-04-12 17:00 | 2442 |  |  | 0.1026
2019-04-12 18:00 | 2443 |  |  | 0.022837
2019-04-12 19:00 | 2444 |  |  | 0.00025004
2019-04-12 20:00 | 2445 |  |  | 0
2019-04-12 21:00 | 2446 |  |  | 0
2019-04-12 22:00 | 2447 |  |  | 0
2019-04-12 23:00 | 2448 |  |  | 0
2019-04-13 | 2449 |  |  | 0
2019-04-13 01:00 | 2450 |  |  | 0
2019-04-13 02:00 | 2451 |  |  | 0
2019-04-13 03:00 | 2452 |  |  | 0
2019-04-13 04:00 | 2453 |  |  | 0
2019-04-13 05:00 | 2454 |  |  | 0
2019-04-13 06:00 | 2455 |  |  | 0.00016669
2019-04-13 07:00 | 2456 |  |  | 0.010252
2019-04-13 08:00 | 2457 |  |  | 0.064594
2019-04-13 09:00 | 2458 |  |  | 0.16661
2019-04-13 10:00 | 2459 |  |  | 0.2227
2019-04-13 11:00 | 2460 |  |  | 0.42707
2019-04-13 12:00 | 2461 |  |  | 0.52784
2019-04-13 13:00 | 2462 |  |  | 0.43691
2019-04-13 14:00 | 2463 |  |  | 0.22729
2019-04-13 15:00 | 2464 |  |  | 0.10035
2019-04-13 16:00 | 2465 |  |  | 0.033672
2019-04-13 17:00 | 2466 |  |  | 0.075429
2019-04-13 18:00 | 2467 |  |  | 0.014419
2019-04-13 19:00 | 2468 |  |  | 0
2019-04-13 20:00 | 2469 |  |  | 0
2019-04-13 21:00 | 2470 |  |  | 0
2019-04-13 22:00 | 2471 |  |  | 0
2019-04-13 23:00 | 2472 |  |  | 0
2019-04-14 | 2473 |  |  | 0
2019-04-14 01:00 | 2474 |  |  | 0
2019-04-14 02:00 | 2475 |  |  | 0
2019-04-14 03:00 | 2476 |  |  | 0
2019-04-14 04:00 | 2477 |  |  | 0
2019-04-14 05:00 | 2478 |  |  | 0
2019-04-14 06:00 | 2479 |  |  | 0.018003
2019-04-14 07:00 | 2480 |  |  | 0.094766
2019-04-14 08:00 | 2481 |  |  | 0.29888
2019-04-14 09:00 | 2482 |  |  | 0.49683
2019-04-14 10:00 | 2483 |  |  | 0.52059
2019-04-14 11:00 | 2484 |  |  | 0.50125
2019-04-14 12:00 | 2485 |  |  | 0.8779
2019-04-14 13:00 | 2486 |  |  | 0.35148
2019-04-14 14:00 | 2487 |  |  | 0.40115
2019-04-14 15:00 | 2488 |  |  | 0.49342
2019-04-14 16:00 | 2489 |  |  | 0.34747
2019-04-14 17:00 | 2490 |  |  | 0.21412
2019-04-14 18:00 | 2491 |  |  | 0.045091
2019-04-14 19:00 | 2492 |  |  | 0.00016669
2019-04-14 20:00 | 2493 |  |  | 0
2019-04-14 21:00 | 2494 |  |  | 0
2019-04-14 22:00 | 2495 |  |  | 0
2019-04-14 23:00 | 2496 |  |  | 0
2019-04-15 | 2497 |  |  | 0
2019-04-15 01:00 | 2498 |  |  | 0
2019-04-15 02:00 | 2499 |  |  | 0
2019-04-15 03:00 | 2500 |  |  | 0
2019-04-15 04:00 | 2501 |  |  | 0
2019-04-15 05:00 | 2502 |  |  | 8.3347e-05
2019-04-15 06:00 | 2503 |  |  | 0.028255
2019-04-15 07:00 | 2504 |  |  | 0.085514
2019-04-15 08:00 | 2505 |  |  | 0.26554
2019-04-15 09:00 | 2506 |  |  | 0.49283
2019-04-15 10:00 | 2507 |  |  | 0.65369
2019-04-15 11:00 | 2508 |  |  | 0.47175
2019-04-15 12:00 | 2509 |  |  | 0.13411
2019-04-15 13:00 | 2510 |  |  | 0.81214
2019-04-15 14:00 | 2511 |  |  | 0.74646
2019-04-15 15:00 | 2512 |  |  | 0.70112
2019-04-15 16:00 | 2513 |  |  | 0.41782
2019-04-15 17:00 | 2514 |  |  | 0.15203
2019-04-15 18:00 | 2515 |  |  | 0.057676
2019-04-15 19:00 | 2516 |  |  | 0
2019-04-15 20:00 | 2517 |  |  | 0
2019-04-15 21:00 | 2518 |  |  | 0
2019-04-15 22:00 | 2519 |  |  | 0
2019-04-15 23:00 | 2520 |  |  | 0
2019-04-16 | 2521 |  |  | 0
2019-04-16 01:00 | 2522 |  |  | 0
2019-04-16 02:00 | 2523 |  |  | 0
2019-04-16 03:00 | 2524 |  |  | 0
2019-04-16 04:00 | 2525 |  |  | 0
2019-04-16 05:00 | 2526 |  |  | 0.00091682
2019-04-16 06:00 | 2527 |  |  | 0.025588
2019-04-16 07:00 | 2528 |  |  | 0.084264
2019-04-16 08:00 | 2529 |  |  | 0.21945
2019-04-16 09:00 | 2530 |  |  | 0.28671
2019-04-16 10:00 | 2531 |  |  | 0.60202
2019-04-16 11:00 | 2532 |  |  | 0.3108
2019-04-16 12:00 | 2533 |  |  | 0.23762
2019-04-16 13:00 | 2534 |  |  | 0.3834
2019-04-16 14:00 | 2535 |  |  | 0.56659
2019-04-16 15:00 | 2536 |  |  | 0.33172
2019-04-16 16:00 | 2537 |  |  | 0.31839
2019-04-16 17:00 | 2538 |  |  | 0.2117
2019-04-16 18:00 | 2539 |  |  | 0.026671
2019-04-16 19:00 | 2540 |  |  | 0.00025004
2019-04-16 20:00 | 2541 |  |  | 0
2019-04-16 21:00 | 2542 |  |  | 0
2019-04-16 22:00 | 2543 |  |  | 0
2019-04-16 23:00 | 2544 |  |  | 0
2019-04-17 | 2545 |  |  | 0
2019-04-17 01:00 | 2546 |  |  | 0
2019-04-17 02:00 | 2547 |  |  | 0
2019-04-17 03:00 | 2548 |  |  | 0
2019-04-17 04:00 | 2549 |  |  | 0
2019-04-17 05:00 | 2550 |  |  | 0.00050008
2019-04-17 06:00 | 2551 |  |  | 0.027421
2019-04-17 07:00 | 2552 |  |  | 0.091932
2019-04-17 08:00 | 2553 |  |  | 0.27038
2019-04-17 09:00 | 2554 |  |  | 0.45824
2019-04-17 10:00 | 2555 |  |  | 0.60477
2019-04-17 11:00 | 2556 |  |  | 0.68778
2019-04-17 12:00 | 2557 |  |  | 0.78321
2019-04-17 13:00 | 2558 |  |  | 0.77105
2019-04-17 14:00 | 2559 |  |  | 0.72745
2019-04-17 15:00 | 2560 |  |  | 0.62735
2019-04-17 16:00 | 2561 |  |  | 0.45566
2019-04-17 17:00 | 2562 |  |  | 0.26913
2019-04-17 18:00 | 2563 |  |  | 0.054676
2019-04-17 19:00 | 2564 |  |  | 0.0010002
2019-04-17 20:00 | 2565 |  |  | 0
2019-04-17 21:00 | 2566 |  |  | 0
2019-04-17 22:00 | 2567 |  |  | 0
2019-04-17 23:00 | 2568 |  |  | 0
2019-04-18 | 2569 |  |  | 0
2019-04-18 01:00 | 2570 |  |  | 0
2019-04-18 02:00 | 2571 |  |  | 0
2019-04-18 03:00 | 2572 |  |  | 0
2019-04-18 04:00 | 2573 |  |  | 0
2019-04-18 05:00 | 2574 |  |  | 0.0018336
2019-04-18 06:00 | 2575 |  |  | 0.034589
2019-04-18 07:00 | 2576 |  |  | 0.10052
2019-04-18 08:00 | 2577 |  |  | 0.26088
2019-04-18 09:00 | 2578 |  |  | 0.45099
2019-04-18 10:00 | 2579 |  |  | 0.60043
2019-04-18 11:00 | 2580 |  |  | 0.73304
2019-04-18 12:00 | 2581 |  |  | 0.73971
2019-04-18 13:00 | 2582 |  |  | 0.66003
2019-04-18 14:00 | 2583 |  |  | 0.62535
2019-04-18 15:00 | 2584 |  |  | 0.3799
2019-04-18 16:00 | 2585 |  |  | 0.26513
2019-04-18 17:00 | 2586 |  |  | 0.10827
2019-04-18 18:00 | 2587 |  |  | 0.035673
2019-04-18 19:00 | 2588 |  |  | 0.00033339
2019-04-18 20:00 | 2589 |  |  | 0
2019-04-18 21:00 | 2590 |  |  | 0
2019-04-18 22:00 | 2591 |  |  | 0
2019-04-18 23:00 | 2592 |  |  | 0
2019-04-19 | 2593 |  |  | 0
2019-04-19 01:00 | 2594 |  |  | 0
2019-04-19 02:00 | 2595 |  |  | 0
2019-04-19 03:00 | 2596 |  |  | 0
2019-04-19 04:00 | 2597 |  |  | 0
2019-04-19 05:00 | 2598 |  |  | 0.00075013
2019-04-19 06:00 | 2599 |  |  | 0.02117
2019-04-19 07:00 | 2600 |  |  | 0.0976
2019-04-19 08:00 | 2601 |  |  | 0.24029
2019-04-19 09:00 | 2602 |  |  | 0.49117
2019-04-19 10:00 | 2603 |  |  | 0.63702
2019-04-19 11:00 | 2604 |  |  | 0.74704
2019-04-19 12:00 | 2605 |  |  | 0.80572
2019-04-19 13:00 | 2606 |  |  | 0.64394
2019-04-19 14:00 | 2607 |  |  | 0.46508
2019-04-19 15:00 | 2608 |  |  | 0.36898
2019-04-19 16:00 | 2609 |  |  | 0.22829
2019-04-19 17:00 | 2610 |  |  | 0.11019
2019-04-19 18:00 | 2611 |  |  | 0.033422
2019-04-19 19:00 | 2612 |  |  | 0.0010002
2019-04-19 20:00 | 2613 |  |  | 0
2019-04-19 21:00 | 2614 |  |  | 0
2019-04-19 22:00 | 2615 |  |  | 0
2019-04-19 23:00 | 2616 |  |  | 0
2019-04-20 | 2617 |  |  | 0
2019-04-20 01:00 | 2618 |  |  | 0
2019-04-20 02:00 | 2619 |  |  | 0
2019-04-20 03:00 | 2620 |  |  | 0
2019-04-20 04:00 | 2621 |  |  | 0
2019-04-20 05:00 | 2622 |  |  | 0.0017503
2019-04-20 06:00 | 2623 |  |  | 0.030838
2019-04-20 07:00 | 2624 |  |  | 0.094516
2019-04-20 08:00 | 2625 |  |  | 0.27696
2019-04-20 09:00 | 2626 |  |  | 0.46991
2019-04-20 10:00 | 2627 |  |  | 0.62652
2019-04-20 11:00 | 2628 |  |  | 0.66519
2019-04-20 12:00 | 2629 |  |  | 0.63719
2019-04-20 13:00 | 2630 |  |  | 0.82297
2019-04-20 14:00 | 2631 |  |  | 0.76354
2019-04-20 15:00 | 2632 |  |  | 0.68303
2019-04-20 16:00 | 2633 |  |  | 0.33989
2019-04-20 17:00 | 2634 |  |  | 0.16119
2019-04-20 18:00 | 2635 |  |  | 0.035173
2019-04-20 19:00 | 2636 |  |  | 0.00041674
2019-04-20 20:00 | 2637 |  |  | 0
2019-04-20 21:00 | 2638 |  |  | 0
2019-04-20 22:00 | 2639 |  |  | 0
2019-04-20 23:00 | 2640 |  |  | 0
2019-04-21 | 2641 |  |  | 0
2019-04-21 01:00 | 2642 |  |  | 0
2019-04-21 02:00 | 2643 |  |  | 0
2019-04-21 03:00 | 2644 |  |  | 0
2019-04-21 04:00 | 2645 |  |  | 0
2019-04-21 05:00 | 2646 |  |  | 0.0010002
2019-04-21 06:00 | 2647 |  |  | 0.038673
2019-04-21 07:00 | 2648 |  |  | 0.12744
2019-04-21 08:00 | 2649 |  |  | 0.24046
2019-04-21 09:00 | 2650 |  |  | 0.25938
2019-04-21 10:00 | 2651 |  |  | 0.28721
2019-04-21 11:00 | 2652 |  |  | 0.26463
2019-04-21 12:00 | 2653 |  |  | 0.38248
2019-04-21 13:00 | 2654 |  |  | 0.33322
2019-04-21 14:00 | 2655 |  |  | 0.43907
2019-04-21 15:00 | 2656 |  |  | 0.51484
2019-04-21 16:00 | 2657 |  |  | 0.17278
2019-04-21 17:00 | 2658 |  |  | 0.16061
2019-04-21 18:00 | 2659 |  |  | 0.035423
2019-04-21 19:00 | 2660 |  |  | 0.0012502
2019-04-21 20:00 | 2661 |  |  | 0
2019-04-21 21:00 | 2662 |  |  | 0
2019-04-21 22:00 | 2663 |  |  | 0
2019-04-21 23:00 | 2664 |  |  | 0
2019-04-22 | 2665 |  |  | 0
2019-04-22 01:00 | 2666 |  |  | 0
2019-04-22 02:00 | 2667 |  |  | 0
2019-04-22 03:00 | 2668 |  |  | 0
2019-04-22 04:00 | 2669 |  |  | 0
2019-04-22 05:00 | 2670 |  |  | 0
2019-04-22 06:00 | 2671 |  |  | 0.011752
2019-04-22 07:00 | 2672 |  |  | 0.045258
2019-04-22 08:00 | 2673 |  |  | 0.16578
2019-04-22 09:00 | 2674 |  |  | 0.43366
2019-04-22 10:00 | 2675 |  |  | 0.50983
2019-04-22 11:00 | 2676 |  |  | 0.42382
2019-04-22 12:00 | 2677 |  |  | 0.3794
2019-04-22 13:00 | 2678 |  |  | 0.42532
2019-04-22 14:00 | 2679 |  |  | 0.34439
2019-04-22 15:00 | 2680 |  |  | 0.19595
2019-04-22 16:00 | 2681 |  |  | 0.07868
2019-04-22 17:00 | 2682 |  |  | 0.025838
2019-04-22 18:00 | 2683 |  |  | 0.0056676
2019-04-22 19:00 | 2684 |  |  | 0.00066678
2019-04-22 20:00 | 2685 |  |  | 0
2019-04-22 21:00 | 2686 |  |  | 0
2019-04-22 22:00 | 2687 |  |  | 0
2019-04-22 23:00 | 2688 |  |  | 0
2019-04-23 | 2689 |  |  | 0
2019-04-23 01:00 | 2690 |  |  | 0
2019-04-23 02:00 | 2691 |  |  | 0
2019-04-23 03:00 | 2692 |  |  | 0
2019-04-23 04:00 | 2693 |  |  | 0
2019-04-23 05:00 | 2694 |  |  | 0
2019-04-23 06:00 | 2695 |  |  | 0.0049175
2019-04-23 07:00 | 2696 |  |  | 0.019337
2019-04-23 08:00 | 2697 |  |  | 0.029005
2019-04-23 09:00 | 2698 |  |  | 0.069262
2019-04-23 10:00 | 2699 |  |  | 0.075429
2019-04-23 11:00 | 2700 |  |  | 0.12852
2019-04-23 12:00 | 2701 |  |  | 0.083931
2019-04-23 13:00 | 2702 |  |  | 0.076429
2019-04-23 14:00 | 2703 |  |  | 0.050508
2019-04-23 15:00 | 2704 |  |  | 0.057093
2019-04-23 16:00 | 2705 |  |  | 0.043341
2019-04-23 17:00 | 2706 |  |  | 0.014169
2019-04-23 18:00 | 2707 |  |  | 0.0030838
2019-04-23 19:00 | 2708 |  |  | 0
2019-04-23 20:00 | 2709 |  |  | 0
2019-04-23 21:00 | 2710 |  |  | 0
2019-04-23 22:00 | 2711 |  |  | 0
2019-04-23 23:00 | 2712 |  |  | 0
2019-04-24 | 2713 |  |  | 0
2019-04-24 01:00 | 2714 |  |  | 0
2019-04-24 02:00 | 2715 |  |  | 0
2019-04-24 03:00 | 2716 |  |  | 0
2019-04-24 04:00 | 2717 |  |  | 0
2019-04-24 05:00 | 2718 |  |  | 0.0012502
2019-04-24 06:00 | 2719 |  |  | 0.028255
2019-04-24 07:00 | 2720 |  |  | 0.063677
2019-04-24 08:00 | 2721 |  |  | 0.06051
2019-04-24 09:00 | 2722 |  |  | 0.054509
2019-04-24 10:00 | 2723 |  |  | 0.046424
2019-04-24 11:00 | 2724 |  |  | 0.076679
2019-04-24 12:00 | 2725 |  |  | 0.2112
2019-04-24 13:00 | 2726 |  |  | 0.22704
2019-04-24 14:00 | 2727 |  |  | 0.67728
2019-04-24 15:00 | 2728 |  |  | 0.69353
2019-04-24 16:00 | 2729 |  |  | 0.17436
2019-04-24 17:00 | 2730 |  |  | 0.16136
2019-04-24 18:00 | 2731 |  |  | 0.034339
2019-04-24 19:00 | 2732 |  |  | 0.00091682
2019-04-24 20:00 | 2733 |  |  | 0
2019-04-24 21:00 | 2734 |  |  | 0
2019-04-24 22:00 | 2735 |  |  | 0
2019-04-24 23:00 | 2736 |  |  | 0
2019-04-25 | 2737 |  |  | 0
2019-04-25 01:00 | 2738 |  |  | 0
2019-04-25 02:00 | 2739 |  |  | 0
2019-04-25 03:00 | 2740 |  |  | 0
2019-04-25 04:00 | 2741 |  |  | 0
2019-04-25 05:00 | 2742 |  |  | 0.0015836
2019-04-25 06:00 | 2743 |  |  | 0.025338
2019-04-25 07:00 | 2744 |  |  | 0.12535
2019-04-25 08:00 | 2745 |  |  | 0.086181
2019-04-25 09:00 | 2746 |  |  | 0.046341
2019-04-25 10:00 | 2747 |  |  | 0.094182
2019-04-25 11:00 | 2748 |  |  | 0.10893
2019-04-25 12:00 | 2749 |  |  | 0.15886
2019-04-25 13:00 | 2750 |  |  | 0.11785
2019-04-25 14:00 | 2751 |  |  | 0.030672
2019-04-25 15:00 | 2752 |  |  | 0.035506
2019-04-25 16:00 | 2753 |  |  | 0.10118
2019-04-25 17:00 | 2754 |  |  | 0.076346
2019-04-25 18:00 | 2755 |  |  | 0.0086681
2019-04-25 19:00 | 2756 |  |  | 0
2019-04-25 20:00 | 2757 |  |  | 0
2019-04-25 21:00 | 2758 |  |  | 0
2019-04-25 22:00 | 2759 |  |  | 0
2019-04-25 23:00 | 2760 |  |  | 0
2019-04-26 | 2761 |  |  | 0
2019-04-26 01:00 | 2762 |  |  | 0
2019-04-26 02:00 | 2763 |  |  | 0
2019-04-26 03:00 | 2764 |  |  | 0
2019-04-26 04:00 | 2765 |  |  | 0
2019-04-26 05:00 | 2766 |  |  | 0.0010835
2019-04-26 06:00 | 2767 |  |  | 0.016419
2019-04-26 07:00 | 2768 |  |  | 0.077846
2019-04-26 08:00 | 2769 |  |  | 0.088181
2019-04-26 09:00 | 2770 |  |  | 0.45166
2019-04-26 10:00 | 2771 |  |  | 0.59293
2019-04-26 11:00 | 2772 |  |  | 0.62669
2019-04-26 12:00 | 2773 |  |  | 0.82947
2019-04-26 13:00 | 2774 |  |  | 0.84747
2019-04-26 14:00 | 2775 |  |  | 0.32997
2019-04-26 15:00 | 2776 |  |  | 0.15269
2019-04-26 16:00 | 2777 |  |  | 0.084514
2019-04-26 17:00 | 2778 |  |  | 0.01992
2019-04-26 18:00 | 2779 |  |  | 0.014252
2019-04-26 19:00 | 2780 |  |  | 0.0045008
2019-04-26 20:00 | 2781 |  |  | 0
2019-04-26 21:00 | 2782 |  |  | 0
2019-04-26 22:00 | 2783 |  |  | 0
2019-04-26 23:00 | 2784 |  |  | 0
2019-04-27 | 2785 |  |  | 0
2019-04-27 01:00 | 2786 |  |  | 0
2019-04-27 02:00 | 2787 |  |  | 0
2019-04-27 03:00 | 2788 |  |  | 0
2019-04-27 04:00 | 2789 |  |  | 0
2019-04-27 05:00 | 2790 |  |  | 0.0022504
2019-04-27 06:00 | 2791 |  |  | 0.02242
2019-04-27 07:00 | 2792 |  |  | 0.097016
2019-04-27 08:00 | 2793 |  |  | 0.31039
2019-04-27 09:00 | 2794 |  |  | 0.51125
2019-04-27 10:00 | 2795 |  |  | 0.67478
2019-04-27 11:00 | 2796 |  |  | 0.77496
2019-04-27 12:00 | 2797 |  |  | 0.8223
2019-04-27 13:00 | 2798 |  |  | 0.78413
2019-04-27 14:00 | 2799 |  |  | 0.73971
2019-04-27 15:00 | 2800 |  |  | 0.66803
2019-04-27 16:00 | 2801 |  |  | 0.56368
2019-04-27 17:00 | 2802 |  |  | 0.34706
2019-04-27 18:00 | 2803 |  |  | 0.12694
2019-04-27 19:00 | 2804 |  |  | 0.0022504
2019-04-27 20:00 | 2805 |  |  | 0
2019-04-27 21:00 | 2806 |  |  | 0
2019-04-27 22:00 | 2807 |  |  | 0
2019-04-27 23:00 | 2808 |  |  | 0
2019-04-28 | 2809 |  |  | 0
2019-04-28 01:00 | 2810 |  |  | 0
2019-04-28 02:00 | 2811 |  |  | 0
2019-04-28 03:00 | 2812 |  |  | 0
2019-04-28 04:00 | 2813 |  |  | 0
2019-04-28 05:00 | 2814 |  |  | 0.0026671
2019-04-28 06:00 | 2815 |  |  | 0.038506
2019-04-28 07:00 | 2816 |  |  | 0.10343
2019-04-28 08:00 | 2817 |  |  | 0.32597
2019-04-28 09:00 | 2818 |  |  | 0.54176
2019-04-28 10:00 | 2819 |  |  | 0.70078
2019-04-28 11:00 | 2820 |  |  | 0.80463
2019-04-28 12:00 | 2821 |  |  | 0.84656
2019-04-28 13:00 | 2822 |  |  | 0.89282
2019-04-28 14:00 | 2823 |  |  | 0.86739
2019-04-28 15:00 | 2824 |  |  | 0.77446
2019-04-28 16:00 | 2825 |  |  | 0.61952
2019-04-28 17:00 | 2826 |  |  | 0.40007
2019-04-28 18:00 | 2827 |  |  | 0.15769
2019-04-28 19:00 | 2828 |  |  | 0.0032505
2019-04-28 20:00 | 2829 |  |  | 0
2019-04-28 21:00 | 2830 |  |  | 0
2019-04-28 22:00 | 2831 |  |  | 0
2019-04-28 23:00 | 2832 |  |  | 0
2019-04-29 | 2833 |  |  | 0
2019-04-29 01:00 | 2834 |  |  | 0
2019-04-29 02:00 | 2835 |  |  | 0
2019-04-29 03:00 | 2836 |  |  | 0
2019-04-29 04:00 | 2837 |  |  | 0
2019-04-29 05:00 | 2838 |  |  | 0.0026671
2019-04-29 06:00 | 2839 |  |  | 0.024254
2019-04-29 07:00 | 2840 |  |  | 0.10235
2019-04-29 08:00 | 2841 |  |  | 0.31155
2019-04-29 09:00 | 2842 |  |  | 0.50917
2019-04-29 10:00 | 2843 |  |  | 0.44107
2019-04-29 11:00 | 2844 |  |  | 0.69095
2019-04-29 12:00 | 2845 |  |  | 0.82772
2019-04-29 13:00 | 2846 |  |  | 0.83489
2019-04-29 14:00 | 2847 |  |  | 0.7918
2019-04-29 15:00 | 2848 |  |  | 0.69903
2019-04-29 16:00 | 2849 |  |  | 0.55176
2019-04-29 17:00 | 2850 |  |  | 0.36414
2019-04-29 18:00 | 2851 |  |  | 0.11244
2019-04-29 19:00 | 2852 |  |  | 0.0068345
2019-04-29 20:00 | 2853 |  |  | 0
2019-04-29 21:00 | 2854 |  |  | 0
2019-04-29 22:00 | 2855 |  |  | 0
2019-04-29 23:00 | 2856 |  |  | 0
2019-04-30 | 2857 |  |  | 0
2019-04-30 01:00 | 2858 |  |  | 0
2019-04-30 02:00 | 2859 |  |  | 0
2019-04-30 03:00 | 2860 |  |  | 0
2019-04-30 04:00 | 2861 |  |  | 0
2019-04-30 05:00 | 2862 |  |  | 0.0046674
2019-04-30 06:00 | 2863 |  |  | 0.026254
2019-04-30 07:00 | 2864 |  |  | 0.10218
2019-04-30 08:00 | 2865 |  |  | 0.31647
2019-04-30 09:00 | 2866 |  |  | 0.51684
2019-04-30 10:00 | 2867 |  |  | 0.6722
2019-04-30 11:00 | 2868 |  |  | 0.76921
2019-04-30 12:00 | 2869 |  |  | 0.81405
2019-04-30 13:00 | 2870 |  |  | 0.80955
2019-04-30 14:00 | 2871 |  |  | 0.77721
2019-04-30 15:00 | 2872 |  |  | 0.6852
2019-04-30 16:00 | 2873 |  |  | 0.54492
2019-04-30 17:00 | 2874 |  |  | 0.34981
2019-04-30 18:00 | 2875 |  |  | 0.1256
2019-04-30 19:00 | 2876 |  |  | 0.0048341
2019-04-30 20:00 | 2877 |  |  | 0
2019-04-30 21:00 | 2878 |  |  | 0
2019-04-30 22:00 | 2879 |  |  | 0
2019-04-30 23:00 | 2880 |  |  | 0
2019-05-01 | 2881 |  |  | 0
2019-05-01 01:00 | 2882 |  |  | 0
2019-05-01 02:00 | 2883 |  |  | 0
2019-05-01 03:00 | 2884 |  |  | 0
2019-05-01 04:00 | 2885 |  |  | 0
2019-05-01 05:00 | 2886 |  |  | 0.0044174
2019-05-01 06:00 | 2887 |  |  | 0.027838
2019-05-01 07:00 | 2888 |  |  | 0.10835
2019-05-01 08:00 | 2889 |  |  | 0.31155
2019-05-01 09:00 | 2890 |  |  | 0.5085
2019-05-01 10:00 | 2891 |  |  | 0.65853
2019-05-01 11:00 | 2892 |  |  | 0.74512
2019-05-01 12:00 | 2893 |  |  | 0.79238
2019-05-01 13:00 | 2894 |  |  | 0.80405
2019-05-01 14:00 | 2895 |  |  | 0.75779
2019-05-01 15:00 | 2896 |  |  | 0.67853
2019-05-01 16:00 | 2897 |  |  | 0.52767
2019-05-01 17:00 | 2898 |  |  | 0.32947
2019-05-01 18:00 | 2899 |  |  | 0.11402
2019-05-01 19:00 | 2900 |  |  | 0.0044174
2019-05-01 20:00 | 2901 |  |  | 0
2019-05-01 21:00 | 2902 |  |  | 0
2019-05-01 22:00 | 2903 |  |  | 0
2019-05-01 23:00 | 2904 |  |  | 0
2019-05-02 | 2905 |  |  | 0
2019-05-02 01:00 | 2906 |  |  | 0
2019-05-02 02:00 | 2907 |  |  | 0
2019-05-02 03:00 | 2908 |  |  | 0
2019-05-02 04:00 | 2909 |  |  | 0
2019-05-02 05:00 | 2910 |  |  | 0.0090848
2019-05-02 06:00 | 2911 |  |  | 0.056426
2019-05-02 07:00 | 2912 |  |  | 0.11127
2019-05-02 08:00 | 2913 |  |  | 0.29005
2019-05-02 09:00 | 2914 |  |  | 0.45833
2019-05-02 10:00 | 2915 |  |  | 0.52659
2019-05-02 11:00 | 2916 |  |  | 0.64777
2019-05-02 12:00 | 2917 |  |  | 0.44874
2019-05-02 13:00 | 2918 |  |  | 0.40457
2019-05-02 14:00 | 2919 |  |  | 0.39515
2019-05-02 15:00 | 2920 |  |  | 0.27363
2019-05-02 16:00 | 2921 |  |  | 0.21612
2019-05-02 17:00 | 2922 |  |  | 0.1291
2019-05-02 18:00 | 2923 |  |  | 0.044091
2019-05-02 19:00 | 2924 |  |  | 0.013336
2019-05-02 20:00 | 2925 |  |  | 0
2019-05-02 21:00 | 2926 |  |  | 0
2019-05-02 22:00 | 2927 |  |  | 0
2019-05-02 23:00 | 2928 |  |  | 0
2019-05-03 | 2929 |  |  | 0
2019-05-03 01:00 | 2930 |  |  | 0
2019-05-03 02:00 | 2931 |  |  | 0
2019-05-03 03:00 | 2932 |  |  | 0
2019-05-03 04:00 | 2933 |  |  | 0
2019-05-03 05:00 | 2934 |  |  | 0.0069178
2019-05-03 06:00 | 2935 |  |  | 0.056926
2019-05-03 07:00 | 2936 |  |  | 0.11194
2019-05-03 08:00 | 2937 |  |  | 0.34789
2019-05-03 09:00 | 2938 |  |  | 0.46841
2019-05-03 10:00 | 2939 |  |  | 0.56843
2019-05-03 11:00 | 2940 |  |  | 0.60927
2019-05-03 12:00 | 2941 |  |  | 0.37498
2019-05-03 13:00 | 2942 |  |  | 0.07818
2019-05-03 14:00 | 2943 |  |  | 0.060427
2019-05-03 15:00 | 2944 |  |  | 0.30222
2019-05-03 16:00 | 2945 |  |  | 0.49067
2019-05-03 17:00 | 2946 |  |  | 0.17503
2019-05-03 18:00 | 2947 |  |  | 0.054259
2019-05-03 19:00 | 2948 |  |  | 0.0013336
2019-05-03 20:00 | 2949 |  |  | 0
2019-05-03 21:00 | 2950 |  |  | 0
2019-05-03 22:00 | 2951 |  |  | 0
2019-05-03 23:00 | 2952 |  |  | 0
2019-05-04 | 2953 |  |  | 0
2019-05-04 01:00 | 2954 |  |  | 0
2019-05-04 02:00 | 2955 |  |  | 0
2019-05-04 03:00 | 2956 |  |  | 0
2019-05-04 04:00 | 2957 |  |  | 0
2019-05-04 05:00 | 2958 |  |  | 0.012419
2019-05-04 06:00 | 2959 |  |  | 0.061427
2019-05-04 07:00 | 2960 |  |  | 0.11035
2019-05-04 08:00 | 2961 |  |  | 0.14994
2019-05-04 09:00 | 2962 |  |  | 0.40873
2019-05-04 10:00 | 2963 |  |  | 0.45583
2019-05-04 11:00 | 2964 |  |  | 0.71212
2019-05-04 12:00 | 2965 |  |  | 0.67686
2019-05-04 13:00 | 2966 |  |  | 0.81022
2019-05-04 14:00 | 2967 |  |  | 0.69687
2019-05-04 15:00 | 2968 |  |  | 0.46849
2019-05-04 16:00 | 2969 |  |  | 0.58651
2019-05-04 17:00 | 2970 |  |  | 0.36189
2019-05-04 18:00 | 2971 |  |  | 0.11577
2019-05-04 19:00 | 2972 |  |  | 0.0076679
2019-05-04 20:00 | 2973 |  |  | 0
2019-05-04 21:00 | 2974 |  |  | 0
2019-05-04 22:00 | 2975 |  |  | 0
2019-05-04 23:00 | 2976 |  |  | 0
2019-05-05 | 2977 |  |  | 0
2019-05-05 01:00 | 2978 |  |  | 0
2019-05-05 02:00 | 2979 |  |  | 0
2019-05-05 03:00 | 2980 |  |  | 0
2019-05-05 04:00 | 2981 |  |  | 0
2019-05-05 05:00 | 2982 |  |  | 0.0030838
2019-05-05 06:00 | 2983 |  |  | 0.044757
2019-05-05 07:00 | 2984 |  |  | 0.13577
2019-05-05 08:00 | 2985 |  |  | 0.18103
2019-05-05 09:00 | 2986 |  |  | 0.32314
2019-05-05 10:00 | 2987 |  |  | 0.42715
2019-05-05 11:00 | 2988 |  |  | 0.57518
2019-05-05 12:00 | 2989 |  |  | 0.59018
2019-05-05 13:00 | 2990 |  |  | 0.60793
2019-05-05 14:00 | 2991 |  |  | 0.63711
2019-05-05 15:00 | 2992 |  |  | 0.31464
2019-05-05 16:00 | 2993 |  |  | 0.25954
2019-05-05 17:00 | 2994 |  |  | 0.20053
2019-05-05 18:00 | 2995 |  |  | 0.13652
2019-05-05 19:00 | 2996 |  |  | 0.0092515
2019-05-05 20:00 | 2997 |  |  | 0
2019-05-05 21:00 | 2998 |  |  | 0
2019-05-05 22:00 | 2999 |  |  | 0
2019-05-05 23:00 | 3000 |  |  | 0
2019-05-06 | 3001 |  |  | 0
2019-05-06 01:00 | 3002 |  |  | 0
2019-05-06 02:00 | 3003 |  |  | 0
2019-05-06 03:00 | 3004 |  |  | 0
2019-05-06 04:00 | 3005 |  |  | 0
2019-05-06 05:00 | 3006 |  |  | 0.0067511
2019-05-06 06:00 | 3007 |  |  | 0.026338
2019-05-06 07:00 | 3008 |  |  | 0.11485
2019-05-06 08:00 | 3009 |  |  | 0.33872
2019-05-06 09:00 | 3010 |  |  | 0.54201
2019-05-06 10:00 | 3011 |  |  | 0.69537
2019-05-06 11:00 | 3012 |  |  | 0.7993
2019-05-06 12:00 | 3013 |  |  | 0.84547
2019-05-06 13:00 | 3014 |  |  | 0.84664
2019-05-06 14:00 | 3015 |  |  | 0.80313
2019-05-06 15:00 | 3016 |  |  | 0.7067
2019-05-06 16:00 | 3017 |  |  | 0.56068
2019-05-06 17:00 | 3018 |  |  | 0.36564
2019-05-06 18:00 | 3019 |  |  | 0.13969
2019-05-06 19:00 | 3020 |  |  | 0.0074179
2019-05-06 20:00 | 3021 |  |  | 0
2019-05-06 21:00 | 3022 |  |  | 0
2019-05-06 22:00 | 3023 |  |  | 0
2019-05-06 23:00 | 3024 |  |  | 0
2019-05-07 | 3025 |  |  | 0
2019-05-07 01:00 | 3026 |  |  | 0
2019-05-07 02:00 | 3027 |  |  | 0
2019-05-07 03:00 | 3028 |  |  | 0
2019-05-07 04:00 | 3029 |  |  | 0
2019-05-07 05:00 | 3030 |  |  | 0.011419
2019-05-07 06:00 | 3031 |  |  | 0.053592
2019-05-07 07:00 | 3032 |  |  | 0.14552
2019-05-07 08:00 | 3033 |  |  | 0.2728
2019-05-07 09:00 | 3034 |  |  | 0.46808
2019-05-07 10:00 | 3035 |  |  | 0.68228
2019-05-07 11:00 | 3036 |  |  | 0.72062
2019-05-07 12:00 | 3037 |  |  | 0.60418
2019-05-07 13:00 | 3038 |  |  | 0.49142
2019-05-07 14:00 | 3039 |  |  | 0.51534
2019-05-07 15:00 | 3040 |  |  | 0.60452
2019-05-07 16:00 | 3041 |  |  | 0.19353
2019-05-07 17:00 | 3042 |  |  | 0.06051
2019-05-07 18:00 | 3043 |  |  | 0.013919
2019-05-07 19:00 | 3044 |  |  | 0
2019-05-07 20:00 | 3045 |  |  | 0
2019-05-07 21:00 | 3046 |  |  | 0
2019-05-07 22:00 | 3047 |  |  | 0
2019-05-07 23:00 | 3048 |  |  | 0
2019-05-08 | 3049 |  |  | 0
2019-05-08 01:00 | 3050 |  |  | 0
2019-05-08 02:00 | 3051 |  |  | 0
2019-05-08 03:00 | 3052 |  |  | 0
2019-05-08 04:00 | 3053 |  |  | 0
2019-05-08 05:00 | 3054 |  |  | 0.0012502
2019-05-08 06:00 | 3055 |  |  | 0.014002
2019-05-08 07:00 | 3056 |  |  | 0.052842
2019-05-08 08:00 | 3057 |  |  | 0.12477
2019-05-08 09:00 | 3058 |  |  | 0.10643
2019-05-08 10:00 | 3059 |  |  | 0.042924
2019-05-08 11:00 | 3060 |  |  | 0.046841
2019-05-08 12:00 | 3061 |  |  | 0.059677
2019-05-08 13:00 | 3062 |  |  | 0.090932
2019-05-08 14:00 | 3063 |  |  | 0.064927
2019-05-08 15:00 | 3064 |  |  | 0.062844
2019-05-08 16:00 | 3065 |  |  | 0.049258
2019-05-08 17:00 | 3066 |  |  | 0.028588
2019-05-08 18:00 | 3067 |  |  | 0.0027505
2019-05-08 19:00 | 3068 |  |  | 0
2019-05-08 20:00 | 3069 |  |  | 0
2019-05-08 21:00 | 3070 |  |  | 0
2019-05-08 22:00 | 3071 |  |  | 0
2019-05-08 23:00 | 3072 |  |  | 0
2019-05-09 | 3073 |  |  | 0
2019-05-09 01:00 | 3074 |  |  | 0
2019-05-09 02:00 | 3075 |  |  | 0
2019-05-09 03:00 | 3076 |  |  | 0
2019-05-09 04:00 | 3077 |  |  | 0
2019-05-09 05:00 | 3078 |  |  | 0.002167
2019-05-09 06:00 | 3079 |  |  | 0.023587
2019-05-09 07:00 | 3080 |  |  | 0.063177
2019-05-09 08:00 | 3081 |  |  | 0.14536
2019-05-09 09:00 | 3082 |  |  | 0.46808
2019-05-09 10:00 | 3083 |  |  | 0.63036
2019-05-09 11:00 | 3084 |  |  | 0.56218
2019-05-09 12:00 | 3085 |  |  | 0.73154
2019-05-09 13:00 | 3086 |  |  | 0.81164
2019-05-09 14:00 | 3087 |  |  | 0.77646
2019-05-09 15:00 | 3088 |  |  | 0.68378
2019-05-09 16:00 | 3089 |  |  | 0.54167
2019-05-09 17:00 | 3090 |  |  | 0.34897
2019-05-09 18:00 | 3091 |  |  | 0.13786
2019-05-09 19:00 | 3092 |  |  | 0.0082514
2019-05-09 20:00 | 3093 |  |  | 0
2019-05-09 21:00 | 3094 |  |  | 0
2019-05-09 22:00 | 3095 |  |  | 0
2019-05-09 23:00 | 3096 |  |  | 0
2019-05-10 | 3097 |  |  | 0
2019-05-10 01:00 | 3098 |  |  | 0
2019-05-10 02:00 | 3099 |  |  | 0
2019-05-10 03:00 | 3100 |  |  | 0
2019-05-10 04:00 | 3101 |  |  | 0
2019-05-10 05:00 | 3102 |  |  | 0.0087515
2019-05-10 06:00 | 3103 |  |  | 0.033756
2019-05-10 07:00 | 3104 |  |  | 0.12352
2019-05-10 08:00 | 3105 |  |  | 0.32505
2019-05-10 09:00 | 3106 |  |  | 0.51767
2019-05-10 10:00 | 3107 |  |  | 0.66553
2019-05-10 11:00 | 3108 |  |  | 0.74621
2019-05-10 12:00 | 3109 |  |  | 0.75621
2019-05-10 13:00 | 3110 |  |  | 0.56768
2019-05-10 14:00 | 3111 |  |  | 0.47808
2019-05-10 15:00 | 3112 |  |  | 0.33814
2019-05-10 16:00 | 3113 |  |  | 0.32555
2019-05-10 17:00 | 3114 |  |  | 0.32255
2019-05-10 18:00 | 3115 |  |  | 0.12177
2019-05-10 19:00 | 3116 |  |  | 0.006001
2019-05-10 20:00 | 3117 |  |  | 0
2019-05-10 21:00 | 3118 |  |  | 0
2019-05-10 22:00 | 3119 |  |  | 0
2019-05-10 23:00 | 3120 |  |  | 0
2019-05-11 | 3121 |  |  | 0
2019-05-11 01:00 | 3122 |  |  | 0
2019-05-11 02:00 | 3123 |  |  | 0
2019-05-11 03:00 | 3124 |  |  | 0
2019-05-11 04:00 | 3125 |  |  | 0
2019-05-11 05:00 | 3126 |  |  | 0.01717
2019-05-11 06:00 | 3127 |  |  | 0.070012
2019-05-11 07:00 | 3128 |  |  | 0.12277
2019-05-11 08:00 | 3129 |  |  | 0.32947
2019-05-11 09:00 | 3130 |  |  | 0.44157
2019-05-11 10:00 | 3131 |  |  | 0.65886
2019-05-11 11:00 | 3132 |  |  | 0.44499
2019-05-11 12:00 | 3133 |  |  | 0.18411
2019-05-11 13:00 | 3134 |  |  | 0.49825
2019-05-11 14:00 | 3135 |  |  | 0.62544
2019-05-11 15:00 | 3136 |  |  | 0.49283
2019-05-11 16:00 | 3137 |  |  | 0.5841
2019-05-11 17:00 | 3138 |  |  | 0.28305
2019-05-11 18:00 | 3139 |  |  | 0.15786
2019-05-11 19:00 | 3140 |  |  | 0.0064177
2019-05-11 20:00 | 3141 |  |  | 0
2019-05-11 21:00 | 3142 |  |  | 0
2019-05-11 22:00 | 3143 |  |  | 0
2019-05-11 23:00 | 3144 |  |  | 0
2019-05-12 | 3145 |  |  | 0
2019-05-12 01:00 | 3146 |  |  | 0
2019-05-12 02:00 | 3147 |  |  | 0
2019-05-12 03:00 | 3148 |  |  | 0
2019-05-12 04:00 | 3149 |  |  | 0
2019-05-12 05:00 | 3150 |  |  | 0.009835
2019-05-12 06:00 | 3151 |  |  | 0.028588
2019-05-12 07:00 | 3152 |  |  | 0.057843
2019-05-12 08:00 | 3153 |  |  | 0.2733
2019-05-12 09:00 | 3154 |  |  | 0.53709
2019-05-12 10:00 | 3155 |  |  | 0.66178
2019-05-12 11:00 | 3156 |  |  | 0.71645
2019-05-12 12:00 | 3157 |  |  | 0.84864
2019-05-12 13:00 | 3158 |  |  | 0.75621
2019-05-12 14:00 | 3159 |  |  | 0.53551
2019-05-12 15:00 | 3160 |  |  | 0.1917
2019-05-12 16:00 | 3161 |  |  | 0.26896
2019-05-12 17:00 | 3162 |  |  | 0.10502
2019-05-12 18:00 | 3163 |  |  | 0.11719
2019-05-12 19:00 | 3164 |  |  | 0.01892
2019-05-12 20:00 | 3165 |  |  | 0
2019-05-12 21:00 | 3166 |  |  | 0
2019-05-12 22:00 | 3167 |  |  | 0
2019-05-12 23:00 | 3168 |  |  | 0
2019-05-13 | 3169 |  |  | 0
2019-05-13 01:00 | 3170 |  |  | 0
2019-05-13 02:00 | 3171 |  |  | 0
2019-05-13 03:00 | 3172 |  |  | 0
2019-05-13 04:00 | 3173 |  |  | 0
2019-05-13 05:00 | 3174 |  |  | 0.0029172
2019-05-13 06:00 | 3175 |  |  | 0.043424
2019-05-13 07:00 | 3176 |  |  | 0.17995
2019-05-13 08:00 | 3177 |  |  | 0.13794
2019-05-13 09:00 | 3178 |  |  | 0.17403
2019-05-13 10:00 | 3179 |  |  | 0.54434
2019-05-13 11:00 | 3180 |  |  | 0.65836
2019-05-13 12:00 | 3181 |  |  | 0.71754
2019-05-13 13:00 | 3182 |  |  | 0.82055
2019-05-13 14:00 | 3183 |  |  | 0.76071
2019-05-13 15:00 | 3184 |  |  | 0.62694
2019-05-13 16:00 | 3185 |  |  | 0.39123
2019-05-13 17:00 | 3186 |  |  | 0.41974
2019-05-13 18:00 | 3187 |  |  | 0.14294
2019-05-13 19:00 | 3188 |  |  | 0.012585
2019-05-13 20:00 | 3189 |  |  | 0
2019-05-13 21:00 | 3190 |  |  | 0
2019-05-13 22:00 | 3191 |  |  | 0
2019-05-13 23:00 | 3192 |  |  | 0
2019-05-14 | 3193 |  |  | 0
2019-05-14 01:00 | 3194 |  |  | 0
2019-05-14 02:00 | 3195 |  |  | 0
2019-05-14 03:00 | 3196 |  |  | 0
2019-05-14 04:00 | 3197 |  |  | 0
2019-05-14 05:00 | 3198 |  |  | 0.010918
2019-05-14 06:00 | 3199 |  |  | 0.030755
2019-05-14 07:00 | 3200 |  |  | 0.12077
2019-05-14 08:00 | 3201 |  |  | 0.32522
2019-05-14 09:00 | 3202 |  |  | 0.51309
2019-05-14 10:00 | 3203 |  |  | 0.64836
2019-05-14 11:00 | 3204 |  |  | 0.6201
2019-05-14 12:00 | 3205 |  |  | 0.60393
2019-05-14 13:00 | 3206 |  |  | 0.30738
2019-05-14 14:00 | 3207 |  |  | 0.079013
2019-05-14 15:00 | 3208 |  |  | 0.046591
2019-05-14 16:00 | 3209 |  |  | 0.048258
2019-05-14 17:00 | 3210 |  |  | 0.028505
2019-05-14 18:00 | 3211 |  |  | 0.010168
2019-05-14 19:00 | 3212 |  |  | 0.00025004
2019-05-14 20:00 | 3213 |  |  | 0
2019-05-14 21:00 | 3214 |  |  | 0
2019-05-14 22:00 | 3215 |  |  | 0
2019-05-14 23:00 | 3216 |  |  | 0
2019-05-15 | 3217 |  |  | 0
2019-05-15 01:00 | 3218 |  |  | 0
2019-05-15 02:00 | 3219 |  |  | 0
2019-05-15 03:00 | 3220 |  |  | 0
2019-05-15 04:00 | 3221 |  |  | 0
2019-05-15 05:00 | 3222 |  |  | 0.016753
2019-05-15 06:00 | 3223 |  |  | 0.030005
2019-05-15 07:00 | 3224 |  |  | 0.12327
2019-05-15 08:00 | 3225 |  |  | 0.34447
2019-05-15 09:00 | 3226 |  |  | 0.54592
2019-05-15 10:00 | 3227 |  |  | 0.68786
2019-05-15 11:00 | 3228 |  |  | 0.79047
2019-05-15 12:00 | 3229 |  |  | 0.81547
2019-05-15 13:00 | 3230 |  |  | 0.78055
2019-05-15 14:00 | 3231 |  |  | 0.78171
2019-05-15 15:00 | 3232 |  |  | 0.7082
2019-05-15 16:00 | 3233 |  |  | 0.52775
2019-05-15 17:00 | 3234 |  |  | 0.36814
2019-05-15 18:00 | 3235 |  |  | 0.15528
2019-05-15 19:00 | 3236 |  |  | 0.014169
2019-05-15 20:00 | 3237 |  |  | 0
2019-05-15 21:00 | 3238 |  |  | 0
2019-05-15 22:00 | 3239 |  |  | 0
2019-05-15 23:00 | 3240 |  |  | 0
2019-05-16 | 3241 |  |  | 0
2019-05-16 01:00 | 3242 |  |  | 0
2019-05-16 02:00 | 3243 |  |  | 0
2019-05-16 03:00 | 3244 |  |  | 0
2019-05-16 04:00 | 3245 |  |  | 0
2019-05-16 05:00 | 3246 |  |  | 0.011752
2019-05-16 06:00 | 3247 |  |  | 0.033589
2019-05-16 07:00 | 3248 |  |  | 0.12535
2019-05-16 08:00 | 3249 |  |  | 0.33322
2019-05-16 09:00 | 3250 |  |  | 0.52717
2019-05-16 10:00 | 3251 |  |  | 0.66611
2019-05-16 11:00 | 3252 |  |  | 0.62927
2019-05-16 12:00 | 3253 |  |  | 0.70812
2019-05-16 13:00 | 3254 |  |  | 0.77296
2019-05-16 14:00 | 3255 |  |  | 0.79422
2019-05-16 15:00 | 3256 |  |  | 0.50475
2019-05-16 16:00 | 3257 |  |  | 0.060843
2019-05-16 17:00 | 3258 |  |  | 0.01842
2019-05-16 18:00 | 3259 |  |  | 0.008168
2019-05-16 19:00 | 3260 |  |  | 0.0012502
2019-05-16 20:00 | 3261 |  |  | 0
2019-05-16 21:00 | 3262 |  |  | 0
2019-05-16 22:00 | 3263 |  |  | 0
2019-05-16 23:00 | 3264 |  |  | 0
2019-05-17 | 3265 |  |  | 0
2019-05-17 01:00 | 3266 |  |  | 0
2019-05-17 02:00 | 3267 |  |  | 0
2019-05-17 03:00 | 3268 |  |  | 0
2019-05-17 04:00 | 3269 |  |  | 0
2019-05-17 05:00 | 3270 |  |  | 0.0029172
2019-05-17 06:00 | 3271 |  |  | 0.012169
2019-05-17 07:00 | 3272 |  |  | 0.035589
2019-05-17 08:00 | 3273 |  |  | 0.053926
2019-05-17 09:00 | 3274 |  |  | 0.055593
2019-05-17 10:00 | 3275 |  |  | 0.077763
2019-05-17 11:00 | 3276 |  |  | 0.10318
2019-05-17 12:00 | 3277 |  |  | 0.12752
2019-05-17 13:00 | 3278 |  |  | 0.10485
2019-05-17 14:00 | 3279 |  |  | 0.12577
2019-05-17 15:00 | 3280 |  |  | 0.12469
2019-05-17 16:00 | 3281 |  |  | 0.042174
2019-05-17 17:00 | 3282 |  |  | 0.024671
2019-05-17 18:00 | 3283 |  |  | 0.009835
2019-05-17 19:00 | 3284 |  |  | 0
2019-05-17 20:00 | 3285 |  |  | 0
2019-05-17 21:00 | 3286 |  |  | 0
2019-05-17 22:00 | 3287 |  |  | 0
2019-05-17 23:00 | 3288 |  |  | 0
2019-05-18 | 3289 |  |  | 0
2019-05-18 01:00 | 3290 |  |  | 0
2019-05-18 02:00 | 3291 |  |  | 0
2019-05-18 03:00 | 3292 |  |  | 0
2019-05-18 04:00 | 3293 |  |  | 0
2019-05-18 05:00 | 3294 |  |  | 8.3347e-05
2019-05-18 06:00 | 3295 |  |  | 0.0040007
2019-05-18 07:00 | 3296 |  |  | 0.018753
2019-05-18 08:00 | 3297 |  |  | 0.051759
2019-05-18 09:00 | 3298 |  |  | 0.046674
2019-05-18 10:00 | 3299 |  |  | 0.10143
2019-05-18 11:00 | 3300 |  |  | 0.16178
2019-05-18 12:00 | 3301 |  |  | 0.20728
2019-05-18 13:00 | 3302 |  |  | 0.20162
2019-05-18 14:00 | 3303 |  |  | 0.089598
2019-05-18 15:00 | 3304 |  |  | 0.076179
2019-05-18 16:00 | 3305 |  |  | 0.12869
2019-05-18 17:00 | 3306 |  |  | 0.053926
2019-05-18 18:00 | 3307 |  |  | 0.028838
2019-05-18 19:00 | 3308 |  |  | 0.0036673
2019-05-18 20:00 | 3309 |  |  | 0
2019-05-18 21:00 | 3310 |  |  | 0
2019-05-18 22:00 | 3311 |  |  | 0
2019-05-18 23:00 | 3312 |  |  | 0
2019-05-19 | 3313 |  |  | 0
2019-05-19 01:00 | 3314 |  |  | 0
2019-05-19 02:00 | 3315 |  |  | 0
2019-05-19 03:00 | 3316 |  |  | 0
2019-05-19 04:00 | 3317 |  |  | 0
2019-05-19 05:00 | 3318 |  |  | 0.0025004
2019-05-19 06:00 | 3319 |  |  | 0.021337
2019-05-19 07:00 | 3320 |  |  | 0.055843
2019-05-19 08:00 | 3321 |  |  | 0.11327
2019-05-19 09:00 | 3322 |  |  | 0.13619
2019-05-19 10:00 | 3323 |  |  | 0.20928
2019-05-19 11:00 | 3324 |  |  | 0.33739
2019-05-19 12:00 | 3325 |  |  | 0.45758
2019-05-19 13:00 | 3326 |  |  | 0.17186
2019-05-19 14:00 | 3327 |  |  | 0.40057
2019-05-19 15:00 | 3328 |  |  | 0.16169
2019-05-19 16:00 | 3329 |  |  | 0.2878
2019-05-19 17:00 | 3330 |  |  | 0.12569
2019-05-19 18:00 | 3331 |  |  | 0.016503
2019-05-19 19:00 | 3332 |  |  | 0
2019-05-19 20:00 | 3333 |  |  | 0
2019-05-19 21:00 | 3334 |  |  | 0
2019-05-19 22:00 | 3335 |  |  | 0
2019-05-19 23:00 | 3336 |  |  | 0
2019-05-20 | 3337 |  |  | 0
2019-05-20 01:00 | 3338 |  |  | 0
2019-05-20 02:00 | 3339 |  |  | 0
2019-05-20 03:00 | 3340 |  |  | 0
2019-05-20 04:00 | 3341 |  |  | 0
2019-05-20 05:00 | 3342 |  |  | 0.012085
2019-05-20 06:00 | 3343 |  |  | 0.045091
2019-05-20 07:00 | 3344 |  |  | 0.046758
2019-05-20 08:00 | 3345 |  |  | 0.09785
2019-05-20 09:00 | 3346 |  |  | 0.17161
2019-05-20 10:00 | 3347 |  |  | 0.35314
2019-05-20 11:00 | 3348 |  |  | 0.50992
2019-05-20 12:00 | 3349 |  |  | 0.63486
2019-05-20 13:00 | 3350 |  |  | 0.72112
2019-05-20 14:00 | 3351 |  |  | 0.60452
2019-05-20 15:00 | 3352 |  |  | 0.2172
2019-05-20 16:00 | 3353 |  |  | 0.073179
2019-05-20 17:00 | 3354 |  |  | 0.079347
2019-05-20 18:00 | 3355 |  |  | 0.070762
2019-05-20 19:00 | 3356 |  |  | 0.016669
2019-05-20 20:00 | 3357 |  |  | 0
2019-05-20 21:00 | 3358 |  |  | 0
2019-05-20 22:00 | 3359 |  |  | 0
2019-05-20 23:00 | 3360 |  |  | 0
2019-05-21 | 3361 |  |  | 0
2019-05-21 01:00 | 3362 |  |  | 0
2019-05-21 02:00 | 3363 |  |  | 0
2019-05-21 03:00 | 3364 |  |  | 0
2019-05-21 04:00 | 3365 |  |  | 0
2019-05-21 05:00 | 3366 |  |  | 0.014836
2019-05-21 06:00 | 3367 |  |  | 0.034422
2019-05-21 07:00 | 3368 |  |  | 0.13077
2019-05-21 08:00 | 3369 |  |  | 0.34414
2019-05-21 09:00 | 3370 |  |  | 0.52017
2019-05-21 10:00 | 3371 |  |  | 0.67211
2019-05-21 11:00 | 3372 |  |  | 0.76071
2019-05-21 12:00 | 3373 |  |  | 0.78855
2019-05-21 13:00 | 3374 |  |  | 0.7988
2019-05-21 14:00 | 3375 |  |  | 0.76588
2019-05-21 15:00 | 3376 |  |  | 0.67278
2019-05-21 16:00 | 3377 |  |  | 0.46083
2019-05-21 17:00 | 3378 |  |  | 0.051009
2019-05-21 18:00 | 3379 |  |  | 0.023337
2019-05-21 19:00 | 3380 |  |  | 0.0096683
2019-05-21 20:00 | 3381 |  |  | 8.3347e-05
2019-05-21 21:00 | 3382 |  |  | 0
2019-05-21 22:00 | 3383 |  |  | 0
2019-05-21 23:00 | 3384 |  |  | 0
2019-05-22 | 3385 |  |  | 0
2019-05-22 01:00 | 3386 |  |  | 0
2019-05-22 02:00 | 3387 |  |  | 0
2019-05-22 03:00 | 3388 |  |  | 0
2019-05-22 04:00 | 3389 |  |  | 0
2019-05-22 05:00 | 3390 |  |  | 0.019337
2019-05-22 06:00 | 3391 |  |  | 0.049425
2019-05-22 07:00 | 3392 |  |  | 0.13177
2019-05-22 08:00 | 3393 |  |  | 0.32005
2019-05-22 09:00 | 3394 |  |  | 0.52009
2019-05-22 10:00 | 3395 |  |  | 0.65986
2019-05-22 11:00 | 3396 |  |  | 0.75288
2019-05-22 12:00 | 3397 |  |  | 0.7933
2019-05-22 13:00 | 3398 |  |  | 0.80297
2019-05-22 14:00 | 3399 |  |  | 0.78671
2019-05-22 15:00 | 3400 |  |  | 0.36856
2019-05-22 16:00 | 3401 |  |  | 0.21695
2019-05-22 17:00 | 3402 |  |  | 0.1091
2019-05-22 18:00 | 3403 |  |  | 0.047258
2019-05-22 19:00 | 3404 |  |  | 0.012252
2019-05-22 20:00 | 3405 |  |  | 0
2019-05-22 21:00 | 3406 |  |  | 0
2019-05-22 22:00 | 3407 |  |  | 0
2019-05-22 23:00 | 3408 |  |  | 0
2019-05-23 | 3409 |  |  | 0
2019-05-23 01:00 | 3410 |  |  | 0
2019-05-23 02:00 | 3411 |  |  | 0
2019-05-23 03:00 | 3412 |  |  | 0
2019-05-23 04:00 | 3413 |  |  | 0
2019-05-23 05:00 | 3414 |  |  | 0.027088
2019-05-23 06:00 | 3415 |  |  | 0.052175
2019-05-23 07:00 | 3416 |  |  | 0.13877
2019-05-23 08:00 | 3417 |  |  | 0.32655
2019-05-23 09:00 | 3418 |  |  | 0.504
2019-05-23 10:00 | 3419 |  |  | 0.60785
2019-05-23 11:00 | 3420 |  |  | 0.71054
2019-05-23 12:00 | 3421 |  |  | 0.78005
2019-05-23 13:00 | 3422 |  |  | 0.75938
2019-05-23 14:00 | 3423 |  |  | 0.76396
2019-05-23 15:00 | 3424 |  |  | 0.55534
2019-05-23 16:00 | 3425 |  |  | 0.46308
2019-05-23 17:00 | 3426 |  |  | 0.29563
2019-05-23 18:00 | 3427 |  |  | 0.14152
2019-05-23 19:00 | 3428 |  |  | 0.018086
2019-05-23 20:00 | 3429 |  |  | 0
2019-05-23 21:00 | 3430 |  |  | 0
2019-05-23 22:00 | 3431 |  |  | 0
2019-05-23 23:00 | 3432 |  |  | 0
2019-05-24 | 3433 |  |  | 0
2019-05-24 01:00 | 3434 |  |  | 0
2019-05-24 02:00 | 3435 |  |  | 0
2019-05-24 03:00 | 3436 |  |  | 0
2019-05-24 04:00 | 3437 |  |  | 8.3347e-05
2019-05-24 05:00 | 3438 |  |  | 0.025004
2019-05-24 06:00 | 3439 |  |  | 0.059427
2019-05-24 07:00 | 3440 |  |  | 0.16361
2019-05-24 08:00 | 3441 |  |  | 0.30363
2019-05-24 09:00 | 3442 |  |  | 0.38806
2019-05-24 10:00 | 3443 |  |  | 0.48708
2019-05-24 11:00 | 3444 |  |  | 0.62002
2019-05-24 12:00 | 3445 |  |  | 0.53776
2019-05-24 13:00 | 3446 |  |  | 0.20378
2019-05-24 14:00 | 3447 |  |  | 0.15678
2019-05-24 15:00 | 3448 |  |  | 0.029588
2019-05-24 16:00 | 3449 |  |  | 0.034339
2019-05-24 17:00 | 3450 |  |  | 0.036673
2019-05-24 18:00 | 3451 |  |  | 0.063427
2019-05-24 19:00 | 3452 |  |  | 0.01742
2019-05-24 20:00 | 3453 |  |  | 0
2019-05-24 21:00 | 3454 |  |  | 0
2019-05-24 22:00 | 3455 |  |  | 0
2019-05-24 23:00 | 3456 |  |  | 0
2019-05-25 | 3457 |  |  | 0
2019-05-25 01:00 | 3458 |  |  | 0
2019-05-25 02:00 | 3459 |  |  | 0
2019-05-25 03:00 | 3460 |  |  | 0
2019-05-25 04:00 | 3461 |  |  | 0
2019-05-25 05:00 | 3462 |  |  | 0.023837
2019-05-25 06:00 | 3463 |  |  | 0.081014
2019-05-25 07:00 | 3464 |  |  | 0.15678
2019-05-25 08:00 | 3465 |  |  | 0.30455
2019-05-25 09:00 | 3466 |  |  | 0.47675
2019-05-25 10:00 | 3467 |  |  | 0.60893
2019-05-25 11:00 | 3468 |  |  | 0.38098
2019-05-25 12:00 | 3469 |  |  | 0.42207
2019-05-25 13:00 | 3470 |  |  | 0.15119
2019-05-25 14:00 | 3471 |  |  | 0.10027
2019-05-25 15:00 | 3472 |  |  | 0.33031
2019-05-25 16:00 | 3473 |  |  | 0.35673
2019-05-25 17:00 | 3474 |  |  | 0.070428
2019-05-25 18:00 | 3475 |  |  | 0.0051675
2019-05-25 19:00 | 3476 |  |  | 0.0044174
2019-05-25 20:00 | 3477 |  |  | 0
2019-05-25 21:00 | 3478 |  |  | 0
2019-05-25 22:00 | 3479 |  |  | 0
2019-05-25 23:00 | 3480 |  |  | 0
2019-05-26 | 3481 |  |  | 0
2019-05-26 01:00 | 3482 |  |  | 0
2019-05-26 02:00 | 3483 |  |  | 0
2019-05-26 03:00 | 3484 |  |  | 0
2019-05-26 04:00 | 3485 |  |  | 0
2019-05-26 05:00 | 3486 |  |  | 0.00075013
2019-05-26 06:00 | 3487 |  |  | 0.02142
2019-05-26 07:00 | 3488 |  |  | 0.052509
2019-05-26 08:00 | 3489 |  |  | 0.13027
2019-05-26 09:00 | 3490 |  |  | 0.24404
2019-05-26 10:00 | 3491 |  |  | 0.43241
2019-05-26 11:00 | 3492 |  |  | 0.53442
2019-05-26 12:00 | 3493 |  |  | 0.50358
2019-05-26 13:00 | 3494 |  |  | 0.48008
2019-05-26 14:00 | 3495 |  |  | 0.15211
2019-05-26 15:00 | 3496 |  |  | 0.1772
2019-05-26 16:00 | 3497 |  |  | 0.53734
2019-05-26 17:00 | 3498 |  |  | 0.25471
2019-05-26 18:00 | 3499 |  |  | 0.17036
2019-05-26 19:00 | 3500 |  |  | 0.026671
2019-05-26 20:00 | 3501 |  |  | 0
2019-05-26 21:00 | 3502 |  |  | 0
2019-05-26 22:00 | 3503 |  |  | 0
2019-05-26 23:00 | 3504 |  |  | 0
2019-05-27 | 3505 |  |  | 0
2019-05-27 01:00 | 3506 |  |  | 0
2019-05-27 02:00 | 3507 |  |  | 0
2019-05-27 03:00 | 3508 |  |  | 0
2019-05-27 04:00 | 3509 |  |  | 0
2019-05-27 05:00 | 3510 |  |  | 0.0076679
2019-05-27 06:00 | 3511 |  |  | 0.041674
2019-05-27 07:00 | 3512 |  |  | 0.10252
2019-05-27 08:00 | 3513 |  |  | 0.11002
2019-05-27 09:00 | 3514 |  |  | 0.068928
2019-05-27 10:00 | 3515 |  |  | 0.16169
2019-05-27 11:00 | 3516 |  |  | 0.16269
2019-05-27 12:00 | 3517 |  |  | 0.1892
2019-05-27 13:00 | 3518 |  |  | 0.19012
2019-05-27 14:00 | 3519 |  |  | 0.16386
2019-05-27 15:00 | 3520 |  |  | 0.13494
2019-05-27 16:00 | 3521 |  |  | 0.12419
2019-05-27 17:00 | 3522 |  |  | 0.10077
2019-05-27 18:00 | 3523 |  |  | 0.067345
2019-05-27 19:00 | 3524 |  |  | 0.0095849
2019-05-27 20:00 | 3525 |  |  | 0
2019-05-27 21:00 | 3526 |  |  | 0
2019-05-27 22:00 | 3527 |  |  | 0
2019-05-27 23:00 | 3528 |  |  | 0
2019-05-28 | 3529 |  |  | 0
2019-05-28 01:00 | 3530 |  |  | 0
2019-05-28 02:00 | 3531 |  |  | 0
2019-05-28 03:00 | 3532 |  |  | 0
2019-05-28 04:00 | 3533 |  |  | 0
2019-05-28 05:00 | 3534 |  |  | 0.016586
2019-05-28 06:00 | 3535 |  |  | 0.052175
2019-05-28 07:00 | 3536 |  |  | 0.10202
2019-05-28 08:00 | 3537 |  |  | 0.31672
2019-05-28 09:00 | 3538 |  |  | 0.35889
2019-05-28 10:00 | 3539 |  |  | 0.50475
2019-05-28 11:00 | 3540 |  |  | 0.56084
2019-05-28 12:00 | 3541 |  |  | 0.49608
2019-05-28 13:00 | 3542 |  |  | 0.34722
2019-05-28 14:00 | 3543 |  |  | 0.29847
2019-05-28 15:00 | 3544 |  |  | 0.21787
2019-05-28 16:00 | 3545 |  |  | 0.2182
2019-05-28 17:00 | 3546 |  |  | 0.12644
2019-05-28 18:00 | 3547 |  |  | 0.11194
2019-05-28 19:00 | 3548 |  |  | 0.025921
2019-05-28 20:00 | 3549 |  |  | 0.00033339
2019-05-28 21:00 | 3550 |  |  | 0
2019-05-28 22:00 | 3551 |  |  | 0
2019-05-28 23:00 | 3552 |  |  | 0
2019-05-29 | 3553 |  |  | 0
2019-05-29 01:00 | 3554 |  |  | 0
2019-05-29 02:00 | 3555 |  |  | 0
2019-05-29 03:00 | 3556 |  |  | 0
2019-05-29 04:00 | 3557 |  |  | 0
2019-05-29 05:00 | 3558 |  |  | 0.009835
2019-05-29 06:00 | 3559 |  |  | 0.029505
2019-05-29 07:00 | 3560 |  |  | 0.13211
2019-05-29 08:00 | 3561 |  |  | 0.32555
2019-05-29 09:00 | 3562 |  |  | 0.509
2019-05-29 10:00 | 3563 |  |  | 0.66103
2019-05-29 11:00 | 3564 |  |  | 0.75838
2019-05-29 12:00 | 3565 |  |  | 0.81589
2019-05-29 13:00 | 3566 |  |  | 0.44957
2019-05-29 14:00 | 3567 |  |  | 0.2122
2019-05-29 15:00 | 3568 |  |  | 0.41174
2019-05-29 16:00 | 3569 |  |  | 0.12344
2019-05-29 17:00 | 3570 |  |  | 0.11294
2019-05-29 18:00 | 3571 |  |  | 0.08043
2019-05-29 19:00 | 3572 |  |  | 0.042924
2019-05-29 20:00 | 3573 |  |  | 0
2019-05-29 21:00 | 3574 |  |  | 0
2019-05-29 22:00 | 3575 |  |  | 0
2019-05-29 23:00 | 3576 |  |  | 0
2019-05-30 | 3577 |  |  | 0
2019-05-30 01:00 | 3578 |  |  | 0
2019-05-30 02:00 | 3579 |  |  | 0
2019-05-30 03:00 | 3580 |  |  | 0
2019-05-30 04:00 | 3581 |  |  | 8.3347e-05
2019-05-30 05:00 | 3582 |  |  | 0.015586
2019-05-30 06:00 | 3583 |  |  | 0.030088
2019-05-30 07:00 | 3584 |  |  | 0.1291
2019-05-30 08:00 | 3585 |  |  | 0.34081
2019-05-30 09:00 | 3586 |  |  | 0.51617
2019-05-30 10:00 | 3587 |  |  | 0.65828
2019-05-30 11:00 | 3588 |  |  | 0.68711
2019-05-30 12:00 | 3589 |  |  | 0.79647
2019-05-30 13:00 | 3590 |  |  | 0.8028
2019-05-30 14:00 | 3591 |  |  | 0.76496
2019-05-30 15:00 | 3592 |  |  | 0.68145
2019-05-30 16:00 | 3593 |  |  | 0.55676
2019-05-30 17:00 | 3594 |  |  | 0.36106
2019-05-30 18:00 | 3595 |  |  | 0.16119
2019-05-30 19:00 | 3596 |  |  | 0.023837
2019-05-30 20:00 | 3597 |  |  | 0
2019-05-30 21:00 | 3598 |  |  | 0
2019-05-30 22:00 | 3599 |  |  | 0
2019-05-30 23:00 | 3600 |  |  | 0
2019-05-31 | 3601 |  |  | 0
2019-05-31 01:00 | 3602 |  |  | 0
2019-05-31 02:00 | 3603 |  |  | 0
2019-05-31 03:00 | 3604 |  |  | 0
2019-05-31 04:00 | 3605 |  |  | 8.3347e-05
2019-05-31 05:00 | 3606 |  |  | 0.017586
2019-05-31 06:00 | 3607 |  |  | 0.047925
2019-05-31 07:00 | 3608 |  |  | 0.14252
2019-05-31 08:00 | 3609 |  |  | 0.32939
2019-05-31 09:00 | 3610 |  |  | 0.5155
2019-05-31 10:00 | 3611 |  |  | 0.66111
2019-05-31 11:00 | 3612 |  |  | 0.43441
2019-05-31 12:00 | 3613 |  |  | 0.46124
2019-05-31 13:00 | 3614 |  |  | 0.70395
2019-05-31 14:00 | 3615 |  |  | 0.69445
2019-05-31 15:00 | 3616 |  |  | 0.63327
2019-05-31 16:00 | 3617 |  |  | 0.52575
2019-05-31 17:00 | 3618 |  |  | 0.35164
2019-05-31 18:00 | 3619 |  |  | 0.15928
2019-05-31 19:00 | 3620 |  |  | 0.024504
2019-05-31 20:00 | 3621 |  |  | 0
2019-05-31 21:00 | 3622 |  |  | 0
2019-05-31 22:00 | 3623 |  |  | 0
2019-05-31 23:00 | 3624 |  |  | 0
2019-06-01 | 3625 |  |  | 0
2019-06-01 01:00 | 3626 |  |  | 0
2019-06-01 02:00 | 3627 |  |  | 0
2019-06-01 03:00 | 3628 |  |  | 0
2019-06-01 04:00 | 3629 |  |  | 8.3347e-05
2019-06-01 05:00 | 3630 |  |  | 0.019087
2019-06-01 06:00 | 3631 |  |  | 0.047091
2019-06-01 07:00 | 3632 |  |  | 0.13327
2019-06-01 08:00 | 3633 |  |  | 0.32297
2019-06-01 09:00 | 3634 |  |  | 0.5005
2019-06-01 10:00 | 3635 |  |  | 0.63361
2019-06-01 11:00 | 3636 |  |  | 0.71595
2019-06-01 12:00 | 3637 |  |  | 0.77488
2019-06-01 13:00 | 3638 |  |  | 0.7843
2019-06-01 14:00 | 3639 |  |  | 0.73321
2019-06-01 15:00 | 3640 |  |  | 0.64811
2019-06-01 16:00 | 3641 |  |  | 0.5235
2019-06-01 17:00 | 3642 |  |  | 0.34564
2019-06-01 18:00 | 3643 |  |  | 0.14927
2019-06-01 19:00 | 3644 |  |  | 0.023837
2019-06-01 20:00 | 3645 |  |  | 8.3347e-05
2019-06-01 21:00 | 3646 |  |  | 0
2019-06-01 22:00 | 3647 |  |  | 0
2019-06-01 23:00 | 3648 |  |  | 0
2019-06-02 | 3649 |  |  | 0
2019-06-02 01:00 | 3650 |  |  | 0
2019-06-02 02:00 | 3651 |  |  | 0
2019-06-02 03:00 | 3652 |  |  | 0
2019-06-02 04:00 | 3653 |  |  | 8.3347e-05
2019-06-02 05:00 | 3654 |  |  | 0.018586
2019-06-02 06:00 | 3655 |  |  | 0.044091
2019-06-02 07:00 | 3656 |  |  | 0.13161
2019-06-02 08:00 | 3657 |  |  | 0.32239
2019-06-02 09:00 | 3658 |  |  | 0.49983
2019-06-02 10:00 | 3659 |  |  | 0.6186
2019-06-02 11:00 | 3660 |  |  | 0.71404
2019-06-02 12:00 | 3661 |  |  | 0.71787
2019-06-02 13:00 | 3662 |  |  | 0.76146
2019-06-02 14:00 | 3663 |  |  | 0.7282
2019-06-02 15:00 | 3664 |  |  | 0.64494
2019-06-02 16:00 | 3665 |  |  | 0.51417
2019-06-02 17:00 | 3666 |  |  | 0.34172
2019-06-02 18:00 | 3667 |  |  | 0.15428
2019-06-02 19:00 | 3668 |  |  | 0.024504
2019-06-02 20:00 | 3669 |  |  | 8.3347e-05
2019-06-02 21:00 | 3670 |  |  | 0
2019-06-02 22:00 | 3671 |  |  | 0
2019-06-02 23:00 | 3672 |  |  | 0
2019-06-03 | 3673 |  |  | 0
2019-06-03 01:00 | 3674 |  |  | 0
2019-06-03 02:00 | 3675 |  |  | 0
2019-06-03 03:00 | 3676 |  |  | 0
2019-06-03 04:00 | 3677 |  |  | 8.3347e-05
2019-06-03 05:00 | 3678 |  |  | 0.020003
2019-06-03 06:00 | 3679 |  |  | 0.046758
2019-06-03 07:00 | 3680 |  |  | 0.13319
2019-06-03 08:00 | 3681 |  |  | 0.31555
2019-06-03 09:00 | 3682 |  |  | 0.48675
2019-06-03 10:00 | 3683 |  |  | 0.63027
2019-06-03 11:00 | 3684 |  |  | 0.71754
2019-06-03 12:00 | 3685 |  |  | 0.75279
2019-06-03 13:00 | 3686 |  |  | 0.74762
2019-06-03 14:00 | 3687 |  |  | 0.72804
2019-06-03 15:00 | 3688 |  |  | 0.62277
2019-06-03 16:00 | 3689 |  |  | 0.41482
2019-06-03 17:00 | 3690 |  |  | 0.038756
2019-06-03 18:00 | 3691 |  |  | 0.0020003
2019-06-03 19:00 | 3692 |  |  | 0
2019-06-03 20:00 | 3693 |  |  | 0
2019-06-03 21:00 | 3694 |  |  | 0
2019-06-03 22:00 | 3695 |  |  | 0
2019-06-03 23:00 | 3696 |  |  | 0
2019-06-04 | 3697 |  |  | 0
2019-06-04 01:00 | 3698 |  |  | 0
2019-06-04 02:00 | 3699 |  |  | 0
2019-06-04 03:00 | 3700 |  |  | 0
2019-06-04 04:00 | 3701 |  |  | 0
2019-06-04 05:00 | 3702 |  |  | 0.01867
2019-06-04 06:00 | 3703 |  |  | 0.049175
2019-06-04 07:00 | 3704 |  |  | 0.13677
2019-06-04 08:00 | 3705 |  |  | 0.31005
2019-06-04 09:00 | 3706 |  |  | 0.48766
2019-06-04 10:00 | 3707 |  |  | 0.61994
2019-06-04 11:00 | 3708 |  |  | 0.70562
2019-06-04 12:00 | 3709 |  |  | 0.73721
2019-06-04 13:00 | 3710 |  |  | 0.58718
2019-06-04 14:00 | 3711 |  |  | 0.49067
2019-06-04 15:00 | 3712 |  |  | 0.30563
2019-06-04 16:00 | 3713 |  |  | 0.22587
2019-06-04 17:00 | 3714 |  |  | 0.2137
2019-06-04 18:00 | 3715 |  |  | 0.062844
2019-06-04 19:00 | 3716 |  |  | 0.02217
2019-06-04 20:00 | 3717 |  |  | 0.00025004
2019-06-04 21:00 | 3718 |  |  | 0
2019-06-04 22:00 | 3719 |  |  | 0
2019-06-04 23:00 | 3720 |  |  | 0
2019-06-05 | 3721 |  |  | 0
2019-06-05 01:00 | 3722 |  |  | 0
2019-06-05 02:00 | 3723 |  |  | 0
2019-06-05 03:00 | 3724 |  |  | 0
2019-06-05 04:00 | 3725 |  |  | 8.3347e-05
2019-06-05 05:00 | 3726 |  |  | 0.028588
2019-06-05 06:00 | 3727 |  |  | 0.071179
2019-06-05 07:00 | 3728 |  |  | 0.1767
2019-06-05 08:00 | 3729 |  |  | 0.25021
2019-06-05 09:00 | 3730 |  |  | 0.48225
2019-06-05 10:00 | 3731 |  |  | 0.60743
2019-06-05 11:00 | 3732 |  |  | 0.6897
2019-06-05 12:00 | 3733 |  |  | 0.76371
2019-06-05 13:00 | 3734 |  |  | 0.37348
2019-06-05 14:00 | 3735 |  |  | 0.11385
2019-06-05 15:00 | 3736 |  |  | 0.071345
2019-06-05 16:00 | 3737 |  |  | 0.12477
2019-06-05 17:00 | 3738 |  |  | 0.17353
2019-06-05 18:00 | 3739 |  |  | 0.064511
2019-06-05 19:00 | 3740 |  |  | 0.010168
2019-06-05 20:00 | 3741 |  |  | 8.3347e-05
2019-06-05 21:00 | 3742 |  |  | 0
2019-06-05 22:00 | 3743 |  |  | 0
2019-06-05 23:00 | 3744 |  |  | 0
2019-06-06 | 3745 |  |  | 0
2019-06-06 01:00 | 3746 |  |  | 0
2019-06-06 02:00 | 3747 |  |  | 0
2019-06-06 03:00 | 3748 |  |  | 0
2019-06-06 04:00 | 3749 |  |  | 0.00058343
2019-06-06 05:00 | 3750 |  |  | 0.023921
2019-06-06 06:00 | 3751 |  |  | 0.041424
2019-06-06 07:00 | 3752 |  |  | 0.091432
2019-06-06 08:00 | 3753 |  |  | 0.088098
2019-06-06 09:00 | 3754 |  |  | 0.19037
2019-06-06 10:00 | 3755 |  |  | 0.27763
2019-06-06 11:00 | 3756 |  |  | 0.39965
2019-06-06 12:00 | 3757 |  |  | 0.69462
2019-06-06 13:00 | 3758 |  |  | 0.61777
2019-06-06 14:00 | 3759 |  |  | 0.65436
2019-06-06 15:00 | 3760 |  |  | 0.41074
2019-06-06 16:00 | 3761 |  |  | 0.1762
2019-06-06 17:00 | 3762 |  |  | 0.031422
2019-06-06 18:00 | 3763 |  |  | 0.08093
2019-06-06 19:00 | 3764 |  |  | 0.015003
2019-06-06 20:00 | 3765 |  |  | 0
2019-06-06 21:00 | 3766 |  |  | 0
2019-06-06 22:00 | 3767 |  |  | 0
2019-06-06 23:00 | 3768 |  |  | 0
2019-06-07 | 3769 |  |  | 0
2019-06-07 01:00 | 3770 |  |  | 0
2019-06-07 02:00 | 3771 |  |  | 0
2019-06-07 03:00 | 3772 |  |  | 0
2019-06-07 04:00 | 3773 |  |  | 0.00016669
2019-06-07 05:00 | 3774 |  |  | 0.02017
2019-06-07 06:00 | 3775 |  |  | 0.091515
2019-06-07 07:00 | 3776 |  |  | 0.14802
2019-06-07 08:00 | 3777 |  |  | 0.25713
2019-06-07 09:00 | 3778 |  |  | 0.34131
2019-06-07 10:00 | 3779 |  |  | 0.37648
2019-06-07 11:00 | 3780 |  |  | 0.40548
2019-06-07 12:00 | 3781 |  |  | 0.38948
2019-06-07 13:00 | 3782 |  |  | 0.21729
2019-06-07 14:00 | 3783 |  |  | 0.36231
2019-06-07 15:00 | 3784 |  |  | 0.16728
2019-06-07 16:00 | 3785 |  |  | 0.15628
2019-06-07 17:00 | 3786 |  |  | 0.032172
2019-06-07 18:00 | 3787 |  |  | 0.026004
2019-06-07 19:00 | 3788 |  |  | 0.0049175
2019-06-07 20:00 | 3789 |  |  | 0
2019-06-07 21:00 | 3790 |  |  | 0
2019-06-07 22:00 | 3791 |  |  | 0
2019-06-07 23:00 | 3792 |  |  | 0
2019-06-08 | 3793 |  |  | 0
2019-06-08 01:00 | 3794 |  |  | 0
2019-06-08 02:00 | 3795 |  |  | 0
2019-06-08 03:00 | 3796 |  |  | 0
2019-06-08 04:00 | 3797 |  |  | 0.00025004
2019-06-08 05:00 | 3798 |  |  | 0.020337
2019-06-08 06:00 | 3799 |  |  | 0.044924
2019-06-08 07:00 | 3800 |  |  | 0.13202
2019-06-08 08:00 | 3801 |  |  | 0.31972
2019-06-08 09:00 | 3802 |  |  | 0.48658
2019-06-08 10:00 | 3803 |  |  | 0.63194
2019-06-08 11:00 | 3804 |  |  | 0.70087
2019-06-08 12:00 | 3805 |  |  | 0.55193
2019-06-08 13:00 | 3806 |  |  | 0.37431
2019-06-08 14:00 | 3807 |  |  | 0.33814
2019-06-08 15:00 | 3808 |  |  | 0.23079
2019-06-08 16:00 | 3809 |  |  | 0.40007
2019-06-08 17:00 | 3810 |  |  | 0.34931
2019-06-08 18:00 | 3811 |  |  | 0.15644
2019-06-08 19:00 | 3812 |  |  | 0.028588
2019-06-08 20:00 | 3813 |  |  | 0.00016669
2019-06-08 21:00 | 3814 |  |  | 0
2019-06-08 22:00 | 3815 |  |  | 0
2019-06-08 23:00 | 3816 |  |  | 0
2019-06-09 | 3817 |  |  | 0
2019-06-09 01:00 | 3818 |  |  | 0
2019-06-09 02:00 | 3819 |  |  | 0
2019-06-09 03:00 | 3820 |  |  | 0
2019-06-09 04:00 | 3821 |  |  | 0
2019-06-09 05:00 | 3822 |  |  | 0.0073346
2019-06-09 06:00 | 3823 |  |  | 0.055343
2019-06-09 07:00 | 3824 |  |  | 0.11552
2019-06-09 08:00 | 3825 |  |  | 0.16778
2019-06-09 09:00 | 3826 |  |  | 0.25979
2019-06-09 10:00 | 3827 |  |  | 0.42115
2019-06-09 11:00 | 3828 |  |  | 0.33914
2019-06-09 12:00 | 3829 |  |  | 0.3253
2019-06-09 13:00 | 3830 |  |  | 0.27821
2019-06-09 14:00 | 3831 |  |  | 0.27963
2019-06-09 15:00 | 3832 |  |  | 0.24129
2019-06-09 16:00 | 3833 |  |  | 0.19503
2019-06-09 17:00 | 3834 |  |  | 0.26288
2019-06-09 18:00 | 3835 |  |  | 0.14386
2019-06-09 19:00 | 3836 |  |  | 0.032005
2019-06-09 20:00 | 3837 |  |  | 0
2019-06-09 21:00 | 3838 |  |  | 0
2019-06-09 22:00 | 3839 |  |  | 0
2019-06-09 23:00 | 3840 |  |  | 0
2019-06-10 | 3841 |  |  | 0
2019-06-10 01:00 | 3842 |  |  | 0
2019-06-10 02:00 | 3843 |  |  | 0
2019-06-10 03:00 | 3844 |  |  | 0
2019-06-10 04:00 | 3845 |  |  | 0
2019-06-10 05:00 | 3846 |  |  | 0.014669
2019-06-10 06:00 | 3847 |  |  | 0.05726
2019-06-10 07:00 | 3848 |  |  | 0.17853
2019-06-10 08:00 | 3849 |  |  | 0.22537
2019-06-10 09:00 | 3850 |  |  | 0.32297
2019-06-10 10:00 | 3851 |  |  | 0.497
2019-06-10 11:00 | 3852 |  |  | 0.13294
2019-06-10 12:00 | 3853 |  |  | 0.13244
2019-06-10 13:00 | 3854 |  |  | 0.34364
2019-06-10 14:00 | 3855 |  |  | 0.39115
2019-06-10 15:00 | 3856 |  |  | 0.33239
2019-06-10 16:00 | 3857 |  |  | 0.3058
2019-06-10 17:00 | 3858 |  |  | 0.08168
2019-06-10 18:00 | 3859 |  |  | 0.0052509
2019-06-10 19:00 | 3860 |  |  | 0.00083347
2019-06-10 20:00 | 3861 |  |  | 0
2019-06-10 21:00 | 3862 |  |  | 0
2019-06-10 22:00 | 3863 |  |  | 0
2019-06-10 23:00 | 3864 |  |  | 0
2019-06-11 | 3865 |  |  | 0
2019-06-11 01:00 | 3866 |  |  | 0
2019-06-11 02:00 | 3867 |  |  | 0
2019-06-11 03:00 | 3868 |  |  | 0
2019-06-11 04:00 | 3869 |  |  | 0.0023337
2019-06-11 05:00 | 3870 |  |  | 0.031922
2019-06-11 06:00 | 3871 |  |  | 0.082764
2019-06-11 07:00 | 3872 |  |  | 0.15336
2019-06-11 08:00 | 3873 |  |  | 0.22604
2019-06-11 09:00 | 3874 |  |  | 0.2938
2019-06-11 10:00 | 3875 |  |  | 0.35931
2019-06-11 11:00 | 3876 |  |  | 0.37231
2019-06-11 12:00 | 3877 |  |  | 0.43232
2019-06-11 13:00 | 3878 |  |  | 0.24354
2019-06-11 14:00 | 3879 |  |  | 0.35664
2019-06-11 15:00 | 3880 |  |  | 0.17911
2019-06-11 16:00 | 3881 |  |  | 0.19787
2019-06-11 17:00 | 3882 |  |  | 0.066678
2019-06-11 18:00 | 3883 |  |  | 0.051175
2019-06-11 19:00 | 3884 |  |  | 0.015253
2019-06-11 20:00 | 3885 |  |  | 0
2019-06-11 21:00 | 3886 |  |  | 0
2019-06-11 22:00 | 3887 |  |  | 0
2019-06-11 23:00 | 3888 |  |  | 0
2019-06-12 | 3889 |  |  | 0
2019-06-12 01:00 | 3890 |  |  | 0
2019-06-12 02:00 | 3891 |  |  | 0
2019-06-12 03:00 | 3892 |  |  | 0
2019-06-12 04:00 | 3893 |  |  | 0
2019-06-12 05:00 | 3894 |  |  | 0.02292
2019-06-12 06:00 | 3895 |  |  | 0.074346
2019-06-12 07:00 | 3896 |  |  | 0.14936
2019-06-12 08:00 | 3897 |  |  | 0.21879
2019-06-12 09:00 | 3898 |  |  | 0.4765
2019-06-12 10:00 | 3899 |  |  | 0.39498
2019-06-12 11:00 | 3900 |  |  | 0.59918
2019-06-12 12:00 | 3901 |  |  | 0.78071
2019-06-12 13:00 | 3902 |  |  | 0.69787
2019-06-12 14:00 | 3903 |  |  | 0.46691
2019-06-12 15:00 | 3904 |  |  | 0.08243
2019-06-12 16:00 | 3905 |  |  | 0.12094
2019-06-12 17:00 | 3906 |  |  | 0.096849
2019-06-12 18:00 | 3907 |  |  | 0.040257
2019-06-12 19:00 | 3908 |  |  | 0.03909
2019-06-12 20:00 | 3909 |  |  | 8.3347e-05
2019-06-12 21:00 | 3910 |  |  | 0
2019-06-12 22:00 | 3911 |  |  | 0
2019-06-12 23:00 | 3912 |  |  | 0
2019-06-13 | 3913 |  |  | 0
2019-06-13 01:00 | 3914 |  |  | 0
2019-06-13 02:00 | 3915 |  |  | 0
2019-06-13 03:00 | 3916 |  |  | 0
2019-06-13 04:00 | 3917 |  |  | 0.00033339
2019-06-13 05:00 | 3918 |  |  | 0.018253
2019-06-13 06:00 | 3919 |  |  | 0.034422
2019-06-13 07:00 | 3920 |  |  | 0.12827
2019-06-13 08:00 | 3921 |  |  | 0.33297
2019-06-13 09:00 | 3922 |  |  | 0.51392
2019-06-13 10:00 | 3923 |  |  | 0.65436
2019-06-13 11:00 | 3924 |  |  | 0.73729
2019-06-13 12:00 | 3925 |  |  | 0.68736
2019-06-13 13:00 | 3926 |  |  | 0.56309
2019-06-13 14:00 | 3927 |  |  | 0.55201
2019-06-13 15:00 | 3928 |  |  | 0.63686
2019-06-13 16:00 | 3929 |  |  | 0.30513
2019-06-13 17:00 | 3930 |  |  | 0.26338
2019-06-13 18:00 | 3931 |  |  | 0.11827
2019-06-13 19:00 | 3932 |  |  | 0.013419
2019-06-13 20:00 | 3933 |  |  | 0.00016669
2019-06-13 21:00 | 3934 |  |  | 0
2019-06-13 22:00 | 3935 |  |  | 0
2019-06-13 23:00 | 3936 |  |  | 0
2019-06-14 | 3937 |  |  | 0
2019-06-14 01:00 | 3938 |  |  | 0
2019-06-14 02:00 | 3939 |  |  | 0
2019-06-14 03:00 | 3940 |  |  | 0
2019-06-14 04:00 | 3941 |  |  | 8.3347e-05
2019-06-14 05:00 | 3942 |  |  | 0.02192
2019-06-14 06:00 | 3943 |  |  | 0.068845
2019-06-14 07:00 | 3944 |  |  | 0.12827
2019-06-14 08:00 | 3945 |  |  | 0.31564
2019-06-14 09:00 | 3946 |  |  | 0.36073
2019-06-14 10:00 | 3947 |  |  | 0.51359
2019-06-14 11:00 | 3948 |  |  | 0.70487
2019-06-14 12:00 | 3949 |  |  | 0.71945
2019-06-14 13:00 | 3950 |  |  | 0.70895
2019-06-14 14:00 | 3951 |  |  | 0.70553
2019-06-14 15:00 | 3952 |  |  | 0.56584
2019-06-14 16:00 | 3953 |  |  | 0.4114
2019-06-14 17:00 | 3954 |  |  | 0.21645
2019-06-14 18:00 | 3955 |  |  | 0.03909
2019-06-14 19:00 | 3956 |  |  | 0.019003
2019-06-14 20:00 | 3957 |  |  | 0.00033339
2019-06-14 21:00 | 3958 |  |  | 0
2019-06-14 22:00 | 3959 |  |  | 0
2019-06-14 23:00 | 3960 |  |  | 0
2019-06-15 | 3961 |  |  | 0
2019-06-15 01:00 | 3962 |  |  | 0
2019-06-15 02:00 | 3963 |  |  | 0
2019-06-15 03:00 | 3964 |  |  | 0
2019-06-15 04:00 | 3965 |  |  | 0.00066678
2019-06-15 05:00 | 3966 |  |  | 0.03884
2019-06-15 06:00 | 3967 |  |  | 0.099683
2019-06-15 07:00 | 3968 |  |  | 0.18945
2019-06-15 08:00 | 3969 |  |  | 0.23221
2019-06-15 09:00 | 3970 |  |  | 0.40357
2019-06-15 10:00 | 3971 |  |  | 0.57818
2019-06-15 11:00 | 3972 |  |  | 0.68011
2019-06-15 12:00 | 3973 |  |  | 0.33864
2019-06-15 13:00 | 3974 |  |  | 0.32105
2019-06-15 14:00 | 3975 |  |  | 0.26438
2019-06-15 15:00 | 3976 |  |  | 0.31914
2019-06-15 16:00 | 3977 |  |  | 0.36814
2019-06-15 17:00 | 3978 |  |  | 0.13336
2019-06-15 18:00 | 3979 |  |  | 0.019253
2019-06-15 19:00 | 3980 |  |  | 0.074096
2019-06-15 20:00 | 3981 |  |  | 0.0013336
2019-06-15 21:00 | 3982 |  |  | 0
2019-06-15 22:00 | 3983 |  |  | 0
2019-06-15 23:00 | 3984 |  |  | 0
2019-06-16 | 3985 |  |  | 0
2019-06-16 01:00 | 3986 |  |  | 0
2019-06-16 02:00 | 3987 |  |  | 0
2019-06-16 03:00 | 3988 |  |  | 0
2019-06-16 04:00 | 3989 |  |  | 0.00025004
2019-06-16 05:00 | 3990 |  |  | 0.017836
2019-06-16 06:00 | 3991 |  |  | 0.034422
2019-06-16 07:00 | 3992 |  |  | 0.12794
2019-06-16 08:00 | 3993 |  |  | 0.3208
2019-06-16 09:00 | 3994 |  |  | 0.50308
2019-06-16 10:00 | 3995 |  |  | 0.63411
2019-06-16 11:00 | 3996 |  |  | 0.72062
2019-06-16 12:00 | 3997 |  |  | 0.75788
2019-06-16 13:00 | 3998 |  |  | 0.76938
2019-06-16 14:00 | 3999 |  |  | 0.72795
2019-06-16 15:00 | 4000 |  |  | 0.64077
2019-06-16 16:00 | 4001 |  |  | 0.53367
2019-06-16 17:00 | 4002 |  |  | 0.37098
2019-06-16 18:00 | 4003 |  |  | 0.17995
2019-06-16 19:00 | 4004 |  |  | 0.029922
2019-06-16 20:00 | 4005 |  |  | 0.00041674
2019-06-16 21:00 | 4006 |  |  | 0
2019-06-16 22:00 | 4007 |  |  | 0
2019-06-16 23:00 | 4008 |  |  | 0
2019-06-17 | 4009 |  |  | 0
2019-06-17 01:00 | 4010 |  |  | 0
2019-06-17 02:00 | 4011 |  |  | 0
2019-06-17 03:00 | 4012 |  |  | 0
2019-06-17 04:00 | 4013 |  |  | 0.00025004
2019-06-17 05:00 | 4014 |  |  | 0.017003
2019-06-17 06:00 | 4015 |  |  | 0.032339
2019-06-17 07:00 | 4016 |  |  | 0.12344
2019-06-17 08:00 | 4017 |  |  | 0.31097
2019-06-17 09:00 | 4018 |  |  | 0.497
2019-06-17 10:00 | 4019 |  |  | 0.63627
2019-06-17 11:00 | 4020 |  |  | 0.71904
2019-06-17 12:00 | 4021 |  |  | 0.76688
2019-06-17 13:00 | 4022 |  |  | 0.76621
2019-06-17 14:00 | 4023 |  |  | 0.67378
2019-06-17 15:00 | 4024 |  |  | 0.6031
2019-06-17 16:00 | 4025 |  |  | 0.52425
2019-06-17 17:00 | 4026 |  |  | 0.3759
2019-06-17 18:00 | 4027 |  |  | 0.10502
2019-06-17 19:00 | 4028 |  |  | 0.01992
2019-06-17 20:00 | 4029 |  |  | 8.3347e-05
2019-06-17 21:00 | 4030 |  |  | 0
2019-06-17 22:00 | 4031 |  |  | 0
2019-06-17 23:00 | 4032 |  |  | 0
2019-06-18 | 4033 |  |  | 0
2019-06-18 01:00 | 4034 |  |  | 0
2019-06-18 02:00 | 4035 |  |  | 0
2019-06-18 03:00 | 4036 |  |  | 0
2019-06-18 04:00 | 4037 |  |  | 0
2019-06-18 05:00 | 4038 |  |  | 0.030588
2019-06-18 06:00 | 4039 |  |  | 0.082764
2019-06-18 07:00 | 4040 |  |  | 0.15211
2019-06-18 08:00 | 4041 |  |  | 0.31164
2019-06-18 09:00 | 4042 |  |  | 0.47783
2019-06-18 10:00 | 4043 |  |  | 0.60352
2019-06-18 11:00 | 4044 |  |  | 0.68628
2019-06-18 12:00 | 4045 |  |  | 0.512
2019-06-18 13:00 | 4046 |  |  | 0.22904
2019-06-18 14:00 | 4047 |  |  | 0.37465
2019-06-18 15:00 | 4048 |  |  | 0.24462
2019-06-18 16:00 | 4049 |  |  | 0.25804
2019-06-18 17:00 | 4050 |  |  | 0.15869
2019-06-18 18:00 | 4051 |  |  | 0.070512
2019-06-18 19:00 | 4052 |  |  | 0.022087
2019-06-18 20:00 | 4053 |  |  | 0.00025004
2019-06-18 21:00 | 4054 |  |  | 0
2019-06-18 22:00 | 4055 |  |  | 0
2019-06-18 23:00 | 4056 |  |  | 0
2019-06-19 | 4057 |  |  | 0
2019-06-19 01:00 | 4058 |  |  | 0
2019-06-19 02:00 | 4059 |  |  | 0
2019-06-19 03:00 | 4060 |  |  | 0
2019-06-19 04:00 | 4061 |  |  | 0.00025004
2019-06-19 05:00 | 4062 |  |  | 0.01967
2019-06-19 06:00 | 4063 |  |  | 0.05751
2019-06-19 07:00 | 4064 |  |  | 0.13411
2019-06-19 08:00 | 4065 |  |  | 0.26938
2019-06-19 09:00 | 4066 |  |  | 0.46974
2019-06-19 10:00 | 4067 |  |  | 0.58335
2019-06-19 11:00 | 4068 |  |  | 0.66844
2019-06-19 12:00 | 4069 |  |  | 0.71512
2019-06-19 13:00 | 4070 |  |  | 0.71087
2019-06-19 14:00 | 4071 |  |  | 0.69253
2019-06-19 15:00 | 4072 |  |  | 0.61169
2019-06-19 16:00 | 4073 |  |  | 0.3974
2019-06-19 17:00 | 4074 |  |  | 0.21079
2019-06-19 18:00 | 4075 |  |  | 0.058593
2019-06-19 19:00 | 4076 |  |  | 0.027338
2019-06-19 20:00 | 4077 |  |  | 0.00058343
2019-06-19 21:00 | 4078 |  |  | 0
2019-06-19 22:00 | 4079 |  |  | 0
2019-06-19 23:00 | 4080 |  |  | 0
2019-06-20 | 4081 |  |  | 0
2019-06-20 01:00 | 4082 |  |  | 0
2019-06-20 02:00 | 4083 |  |  | 0
2019-06-20 03:00 | 4084 |  |  | 0
2019-06-20 04:00 | 4085 |  |  | 0.00016669
2019-06-20 05:00 | 4086 |  |  | 0.026338
2019-06-20 06:00 | 4087 |  |  | 0.05701
2019-06-20 07:00 | 4088 |  |  | 0.13119
2019-06-20 08:00 | 4089 |  |  | 0.30205
2019-06-20 09:00 | 4090 |  |  | 0.44949
2019-06-20 10:00 | 4091 |  |  | 0.53401
2019-06-20 11:00 | 4092 |  |  | 0.45616
2019-06-20 12:00 | 4093 |  |  | 0.38123
2019-06-20 13:00 | 4094 |  |  | 0.31914
2019-06-20 14:00 | 4095 |  |  | 0.23254
2019-06-20 15:00 | 4096 |  |  | 0.2042
2019-06-20 16:00 | 4097 |  |  | 0.35214
2019-06-20 17:00 | 4098 |  |  | 0.06026
2019-06-20 18:00 | 4099 |  |  | 0.13736
2019-06-20 19:00 | 4100 |  |  | 0.0096683
2019-06-20 20:00 | 4101 |  |  | 0
2019-06-20 21:00 | 4102 |  |  | 0
2019-06-20 22:00 | 4103 |  |  | 0
2019-06-20 23:00 | 4104 |  |  | 0
2019-06-21 | 4105 |  |  | 0
2019-06-21 01:00 | 4106 |  |  | 0
2019-06-21 02:00 | 4107 |  |  | 0
2019-06-21 03:00 | 4108 |  |  | 0
2019-06-21 04:00 | 4109 |  |  | 0
2019-06-21 05:00 | 4110 |  |  | 0.0054176
2019-06-21 06:00 | 4111 |  |  | 0.053676
2019-06-21 07:00 | 4112 |  |  | 0.15011
2019-06-21 08:00 | 4113 |  |  | 0.26588
2019-06-21 09:00 | 4114 |  |  | 0.43557
2019-06-21 10:00 | 4115 |  |  | 0.5205
2019-06-21 11:00 | 4116 |  |  | 0.62544
2019-06-21 12:00 | 4117 |  |  | 0.46083
2019-06-21 13:00 | 4118 |  |  | 0.14052
2019-06-21 14:00 | 4119 |  |  | 0.016586
2019-06-21 15:00 | 4120 |  |  | 0.050508
2019-06-21 16:00 | 4121 |  |  | 0.032005
2019-06-21 17:00 | 4122 |  |  | 0.048425
2019-06-21 18:00 | 4123 |  |  | 0.0016669
2019-06-21 19:00 | 4124 |  |  | 0
2019-06-21 20:00 | 4125 |  |  | 0
2019-06-21 21:00 | 4126 |  |  | 0
2019-06-21 22:00 | 4127 |  |  | 0
2019-06-21 23:00 | 4128 |  |  | 0
2019-06-22 | 4129 |  |  | 0
2019-06-22 01:00 | 4130 |  |  | 0
2019-06-22 02:00 | 4131 |  |  | 0
2019-06-22 03:00 | 4132 |  |  | 0
2019-06-22 04:00 | 4133 |  |  | 0.00050008
2019-06-22 05:00 | 4134 |  |  | 0.025004
2019-06-22 06:00 | 4135 |  |  | 0.069762
2019-06-22 07:00 | 4136 |  |  | 0.15369
2019-06-22 08:00 | 4137 |  |  | 0.29697
2019-06-22 09:00 | 4138 |  |  | 0.47091
2019-06-22 10:00 | 4139 |  |  | 0.56843
2019-06-22 11:00 | 4140 |  |  | 0.71095
2019-06-22 12:00 | 4141 |  |  | 0.40915
2019-06-22 13:00 | 4142 |  |  | 0.052259
2019-06-22 14:00 | 4143 |  |  | 0.29605
2019-06-22 15:00 | 4144 |  |  | 0.14877
2019-06-22 16:00 | 4145 |  |  | 0.27388
2019-06-22 17:00 | 4146 |  |  | 0.35756
2019-06-22 18:00 | 4147 |  |  | 0.17495
2019-06-22 19:00 | 4148 |  |  | 0.027421
2019-06-22 20:00 | 4149 |  |  | 0.00050008
2019-06-22 21:00 | 4150 |  |  | 0
2019-06-22 22:00 | 4151 |  |  | 0
2019-06-22 23:00 | 4152 |  |  | 0
2019-06-23 | 4153 |  |  | 0
2019-06-23 01:00 | 4154 |  |  | 0
2019-06-23 02:00 | 4155 |  |  | 0
2019-06-23 03:00 | 4156 |  |  | 0
2019-06-23 04:00 | 4157 |  |  | 0.00016669
2019-06-23 05:00 | 4158 |  |  | 0.016503
2019-06-23 06:00 | 4159 |  |  | 0.030588
2019-06-23 07:00 | 4160 |  |  | 0.11694
2019-06-23 08:00 | 4161 |  |  | 0.30947
2019-06-23 09:00 | 4162 |  |  | 0.48333
2019-06-23 10:00 | 4163 |  |  | 0.59777
2019-06-23 11:00 | 4164 |  |  | 0.6947
2019-06-23 12:00 | 4165 |  |  | 0.74479
2019-06-23 13:00 | 4166 |  |  | 0.73804
2019-06-23 14:00 | 4167 |  |  | 0.70787
2019-06-23 15:00 | 4168 |  |  | 0.63069
2019-06-23 16:00 | 4169 |  |  | 0.50283
2019-06-23 17:00 | 4170 |  |  | 0.35581
2019-06-23 18:00 | 4171 |  |  | 0.16711
2019-06-23 19:00 | 4172 |  |  | 0.02092
2019-06-23 20:00 | 4173 |  |  | 0.00025004
2019-06-23 21:00 | 4174 |  |  | 0
2019-06-23 22:00 | 4175 |  |  | 0
2019-06-23 23:00 | 4176 |  |  | 0
2019-06-24 | 4177 |  |  | 0
2019-06-24 01:00 | 4178 |  |  | 0
2019-06-24 02:00 | 4179 |  |  | 0
2019-06-24 03:00 | 4180 |  |  | 0
2019-06-24 04:00 | 4181 |  |  | 0.00025004
2019-06-24 05:00 | 4182 |  |  | 0.017003
2019-06-24 06:00 | 4183 |  |  | 0.034339
2019-06-24 07:00 | 4184 |  |  | 0.1166
2019-06-24 08:00 | 4185 |  |  | 0.29988
2019-06-24 09:00 | 4186 |  |  | 0.46066
2019-06-24 10:00 | 4187 |  |  | 0.59035
2019-06-24 11:00 | 4188 |  |  | 0.64552
2019-06-24 12:00 | 4189 |  |  | 0.70812
2019-06-24 13:00 | 4190 |  |  | 0.6226
2019-06-24 14:00 | 4191 |  |  | 0.41932
2019-06-24 15:00 | 4192 |  |  | 0.41949
2019-06-24 16:00 | 4193 |  |  | 0.43316
2019-06-24 17:00 | 4194 |  |  | 0.36581
2019-06-24 18:00 | 4195 |  |  | 0.15544
2019-06-24 19:00 | 4196 |  |  | 0.025588
2019-06-24 20:00 | 4197 |  |  | 0.00016669
2019-06-24 21:00 | 4198 |  |  | 0
2019-06-24 22:00 | 4199 |  |  | 0
2019-06-24 23:00 | 4200 |  |  | 0
2019-06-25 | 4201 |  |  | 0
2019-06-25 01:00 | 4202 |  |  | 0
2019-06-25 02:00 | 4203 |  |  | 0
2019-06-25 03:00 | 4204 |  |  | 0
2019-06-25 04:00 | 4205 |  |  | 8.3347e-05
2019-06-25 05:00 | 4206 |  |  | 0.01792
2019-06-25 06:00 | 4207 |  |  | 0.065928
2019-06-25 07:00 | 4208 |  |  | 0.13986
2019-06-25 08:00 | 4209 |  |  | 0.27871
2019-06-25 09:00 | 4210 |  |  | 0.43832
2019-06-25 10:00 | 4211 |  |  | 0.55884
2019-06-25 11:00 | 4212 |  |  | 0.61344
2019-06-25 12:00 | 4213 |  |  | 0.38665
2019-06-25 13:00 | 4214 |  |  | 0.6777
2019-06-25 14:00 | 4215 |  |  | 0.63311
2019-06-25 15:00 | 4216 |  |  | 0.56084
2019-06-25 16:00 | 4217 |  |  | 0.43707
2019-06-25 17:00 | 4218 |  |  | 0.28638
2019-06-25 18:00 | 4219 |  |  | 0.12627
2019-06-25 19:00 | 4220 |  |  | 0.023504
2019-06-25 20:00 | 4221 |  |  | 0.00033339
2019-06-25 21:00 | 4222 |  |  | 0
2019-06-25 22:00 | 4223 |  |  | 0
2019-06-25 23:00 | 4224 |  |  | 0
2019-06-26 | 4225 |  |  | 0
2019-06-26 01:00 | 4226 |  |  | 0
2019-06-26 02:00 | 4227 |  |  | 0
2019-06-26 03:00 | 4228 |  |  | 0
2019-06-26 04:00 | 4229 |  |  | 0
2019-06-26 05:00 | 4230 |  |  | 0.010752
2019-06-26 06:00 | 4231 |  |  | 0.064011
2019-06-26 07:00 | 4232 |  |  | 0.13111
2019-06-26 08:00 | 4233 |  |  | 0.27796
2019-06-26 09:00 | 4234 |  |  | 0.43541
2019-06-26 10:00 | 4235 |  |  | 0.54384
2019-06-26 11:00 | 4236 |  |  | 0.6271
2019-06-26 12:00 | 4237 |  |  | 0.6777
2019-06-26 13:00 | 4238 |  |  | 0.68903
2019-06-26 14:00 | 4239 |  |  | 0.64469
2019-06-26 15:00 | 4240 |  |  | 0.57935
2019-06-26 16:00 | 4241 |  |  | 0.45924
2019-06-26 17:00 | 4242 |  |  | 0.3048
2019-06-26 18:00 | 4243 |  |  | 0.10293
2019-06-26 19:00 | 4244 |  |  | 0.0083347
2019-06-26 20:00 | 4245 |  |  | 0.00025004
2019-06-26 21:00 | 4246 |  |  | 0
2019-06-26 22:00 | 4247 |  |  | 0
2019-06-26 23:00 | 4248 |  |  | 0
2019-06-27 | 4249 |  |  | 0
2019-06-27 01:00 | 4250 |  |  | 0
2019-06-27 02:00 | 4251 |  |  | 0
2019-06-27 03:00 | 4252 |  |  | 0
2019-06-27 04:00 | 4253 |  |  | 8.3347e-05
2019-06-27 05:00 | 4254 |  |  | 0.018503
2019-06-27 06:00 | 4255 |  |  | 0.044674
2019-06-27 07:00 | 4256 |  |  | 0.11827
2019-06-27 08:00 | 4257 |  |  | 0.28038
2019-06-27 09:00 | 4258 |  |  | 0.43699
2019-06-27 10:00 | 4259 |  |  | 0.55734
2019-06-27 11:00 | 4260 |  |  | 0.64827
2019-06-27 12:00 | 4261 |  |  | 0.69228
2019-06-27 13:00 | 4262 |  |  | 0.68645
2019-06-27 14:00 | 4263 |  |  | 0.55059
2019-06-27 15:00 | 4264 |  |  | 0.60677
2019-06-27 16:00 | 4265 |  |  | 0.49017
2019-06-27 17:00 | 4266 |  |  | 0.32789
2019-06-27 18:00 | 4267 |  |  | 0.15903
2019-06-27 19:00 | 4268 |  |  | 0.035256
2019-06-27 20:00 | 4269 |  |  | 0.00083347
2019-06-27 21:00 | 4270 |  |  | 0
2019-06-27 22:00 | 4271 |  |  | 0
2019-06-27 23:00 | 4272 |  |  | 0
2019-06-28 | 4273 |  |  | 0
2019-06-28 01:00 | 4274 |  |  | 0
2019-06-28 02:00 | 4275 |  |  | 0
2019-06-28 03:00 | 4276 |  |  | 0
2019-06-28 04:00 | 4277 |  |  | 0.00016669
2019-06-28 05:00 | 4278 |  |  | 0.016419
2019-06-28 06:00 | 4279 |  |  | 0.033339
2019-06-28 07:00 | 4280 |  |  | 0.11185
2019-06-28 08:00 | 4281 |  |  | 0.28946
2019-06-28 09:00 | 4282 |  |  | 0.44682
2019-06-28 10:00 | 4283 |  |  | 0.5756
2019-06-28 11:00 | 4284 |  |  | 0.65844
2019-06-28 12:00 | 4285 |  |  | 0.69628
2019-06-28 13:00 | 4286 |  |  | 0.68778
2019-06-28 14:00 | 4287 |  |  | 0.66753
2019-06-28 15:00 | 4288 |  |  | 0.59918
2019-06-28 16:00 | 4289 |  |  | 0.48083
2019-06-28 17:00 | 4290 |  |  | 0.33622
2019-06-28 18:00 | 4291 |  |  | 0.15919
2019-06-28 19:00 | 4292 |  |  | 0.032422
2019-06-28 20:00 | 4293 |  |  | 0.00066678
2019-06-28 21:00 | 4294 |  |  | 0
2019-06-28 22:00 | 4295 |  |  | 0
2019-06-28 23:00 | 4296 |  |  | 0
2019-06-29 | 4297 |  |  | 0
2019-06-29 01:00 | 4298 |  |  | 0
2019-06-29 02:00 | 4299 |  |  | 0
2019-06-29 03:00 | 4300 |  |  | 0
2019-06-29 04:00 | 4301 |  |  | 0
2019-06-29 05:00 | 4302 |  |  | 0.019337
2019-06-29 06:00 | 4303 |  |  | 0.06151
2019-06-29 07:00 | 4304 |  |  | 0.10852
2019-06-29 08:00 | 4305 |  |  | 0.25954
2019-06-29 09:00 | 4306 |  |  | 0.43832
2019-06-29 10:00 | 4307 |  |  | 0.57293
2019-06-29 11:00 | 4308 |  |  | 0.67203
2019-06-29 12:00 | 4309 |  |  | 0.67728
2019-06-29 13:00 | 4310 |  |  | 0.7152
2019-06-29 14:00 | 4311 |  |  | 0.67903
2019-06-29 15:00 | 4312 |  |  | 0.59352
2019-06-29 16:00 | 4313 |  |  | 0.48016
2019-06-29 17:00 | 4314 |  |  | 0.32614
2019-06-29 18:00 | 4315 |  |  | 0.15411
2019-06-29 19:00 | 4316 |  |  | 0.035006
2019-06-29 20:00 | 4317 |  |  | 0.00083347
2019-06-29 21:00 | 4318 |  |  | 0
2019-06-29 22:00 | 4319 |  |  | 0
2019-06-29 23:00 | 4320 |  |  | 0
2019-06-30 | 4321 |  |  | 0
2019-06-30 01:00 | 4322 |  |  | 0
2019-06-30 02:00 | 4323 |  |  | 0
2019-06-30 03:00 | 4324 |  |  | 0
2019-06-30 04:00 | 4325 |  |  | 0
2019-06-30 05:00 | 4326 |  |  | 0.012419
2019-06-30 06:00 | 4327 |  |  | 0.06026
2019-06-30 07:00 | 4328 |  |  | 0.14469
2019-06-30 08:00 | 4329 |  |  | 0.26271
2019-06-30 09:00 | 4330 |  |  | 0.44049
2019-06-30 10:00 | 4331 |  |  | 0.56084
2019-06-30 11:00 | 4332 |  |  | 0.64436
2019-06-30 12:00 | 4333 |  |  | 0.71737
2019-06-30 13:00 | 4334 |  |  | 0.58126
2019-06-30 14:00 | 4335 |  |  | 0.5801
2019-06-30 15:00 | 4336 |  |  | 0.35739
2019-06-30 16:00 | 4337 |  |  | 0.22679
2019-06-30 17:00 | 4338 |  |  | 0.10193
2019-06-30 18:00 | 4339 |  |  | 0.045258
2019-06-30 19:00 | 4340 |  |  | 0.013252
2019-06-30 20:00 | 4341 |  |  | 0
2019-06-30 21:00 | 4342 |  |  | 0
2019-06-30 22:00 | 4343 |  |  | 0
2019-06-30 23:00 | 4344 |  |  | 0
2019-07-01 | 4345 |  |  | 0
2019-07-01 01:00 | 4346 |  |  | 0
2019-07-01 02:00 | 4347 |  |  | 0
2019-07-01 03:00 | 4348 |  |  | 0
2019-07-01 04:00 | 4349 |  |  | 0
2019-07-01 05:00 | 4350 |  |  | 0.015586
2019-07-01 06:00 | 4351 |  |  | 0.046341
2019-07-01 07:00 | 4352 |  |  | 0.1176
2019-07-01 08:00 | 4353 |  |  | 0.27113
2019-07-01 09:00 | 4354 |  |  | 0.4249
2019-07-01 10:00 | 4355 |  |  | 0.54026
2019-07-01 11:00 | 4356 |  |  | 0.63552
2019-07-01 12:00 | 4357 |  |  | 0.69395
2019-07-01 13:00 | 4358 |  |  | 0.7067
2019-07-01 14:00 | 4359 |  |  | 0.66036
2019-07-01 15:00 | 4360 |  |  | 0.46583
2019-07-01 16:00 | 4361 |  |  | 0.045424
2019-07-01 17:00 | 4362 |  |  | 0.069845
2019-07-01 18:00 | 4363 |  |  | 0.0056676
2019-07-01 19:00 | 4364 |  |  | 0
2019-07-01 20:00 | 4365 |  |  | 0
2019-07-01 21:00 | 4366 |  |  | 0
2019-07-01 22:00 | 4367 |  |  | 0
2019-07-01 23:00 | 4368 |  |  | 0
2019-07-02 | 4369 |  |  | 0
2019-07-02 01:00 | 4370 |  |  | 0
2019-07-02 02:00 | 4371 |  |  | 0
2019-07-02 03:00 | 4372 |  |  | 0
2019-07-02 04:00 | 4373 |  |  | 0
2019-07-02 05:00 | 4374 |  |  | 0.015253
2019-07-02 06:00 | 4375 |  |  | 0.033589
2019-07-02 07:00 | 4376 |  |  | 0.11294
2019-07-02 08:00 | 4377 |  |  | 0.28905
2019-07-02 09:00 | 4378 |  |  | 0.45916
2019-07-02 10:00 | 4379 |  |  | 0.58218
2019-07-02 11:00 | 4380 |  |  | 0.67411
2019-07-02 12:00 | 4381 |  |  | 0.71629
2019-07-02 13:00 | 4382 |  |  | 0.7227
2019-07-02 14:00 | 4383 |  |  | 0.54509
2019-07-02 15:00 | 4384 |  |  | 0.14036
2019-07-02 16:00 | 4385 |  |  | 0.050425
2019-07-02 17:00 | 4386 |  |  | 0.03934
2019-07-02 18:00 | 4387 |  |  | 0.02167
2019-07-02 19:00 | 4388 |  |  | 0.0040007
2019-07-02 20:00 | 4389 |  |  | 0
2019-07-02 21:00 | 4390 |  |  | 0
2019-07-02 22:00 | 4391 |  |  | 0
2019-07-02 23:00 | 4392 |  |  | 0
2019-07-03 | 4393 |  |  | 0
2019-07-03 01:00 | 4394 |  |  | 0
2019-07-03 02:00 | 4395 |  |  | 0
2019-07-03 03:00 | 4396 |  |  | 0
2019-07-03 04:00 | 4397 |  |  | 0
2019-07-03 05:00 | 4398 |  |  | 0.015836
2019-07-03 06:00 | 4399 |  |  | 0.040173
2019-07-03 07:00 | 4400 |  |  | 0.091765
2019-07-03 08:00 | 4401 |  |  | 0.29072
2019-07-03 09:00 | 4402 |  |  | 0.42974
2019-07-03 10:00 | 4403 |  |  | 0.55934
2019-07-03 11:00 | 4404 |  |  | 0.61019
2019-07-03 12:00 | 4405 |  |  | 0.59785
2019-07-03 13:00 | 4406 |  |  | 0.71912
2019-07-03 14:00 | 4407 |  |  | 0.61319
2019-07-03 15:00 | 4408 |  |  | 0.067261
2019-07-03 16:00 | 4409 |  |  | 0.053509
2019-07-03 17:00 | 4410 |  |  | 0.011002
2019-07-03 18:00 | 4411 |  |  | 0.018836
2019-07-03 19:00 | 4412 |  |  | 0.001917
2019-07-03 20:00 | 4413 |  |  | 0
2019-07-03 21:00 | 4414 |  |  | 0
2019-07-03 22:00 | 4415 |  |  | 0
2019-07-03 23:00 | 4416 |  |  | 0
2019-07-04 | 4417 |  |  | 0
2019-07-04 01:00 | 4418 |  |  | 0
2019-07-04 02:00 | 4419 |  |  | 0
2019-07-04 03:00 | 4420 |  |  | 0
2019-07-04 04:00 | 4421 |  |  | 0
2019-07-04 05:00 | 4422 |  |  | 0.016003
2019-07-04 06:00 | 4423 |  |  | 0.037423
2019-07-04 07:00 | 4424 |  |  | 0.11152
2019-07-04 08:00 | 4425 |  |  | 0.28421
2019-07-04 09:00 | 4426 |  |  | 0.45758
2019-07-04 10:00 | 4427 |  |  | 0.58901
2019-07-04 11:00 | 4428 |  |  | 0.6737
2019-07-04 12:00 | 4429 |  |  | 0.71162
2019-07-04 13:00 | 4430 |  |  | 0.69278
2019-07-04 14:00 | 4431 |  |  | 0.59718
2019-07-04 15:00 | 4432 |  |  | 0.58876
2019-07-04 16:00 | 4433 |  |  | 0.44949
2019-07-04 17:00 | 4434 |  |  | 0.20545
2019-07-04 18:00 | 4435 |  |  | 0.15544
2019-07-04 19:00 | 4436 |  |  | 0.031422
2019-07-04 20:00 | 4437 |  |  | 0.00083347
2019-07-04 21:00 | 4438 |  |  | 0
2019-07-04 22:00 | 4439 |  |  | 0
2019-07-04 23:00 | 4440 |  |  | 0
2019-07-05 | 4441 |  |  | 0
2019-07-05 01:00 | 4442 |  |  | 0
2019-07-05 02:00 | 4443 |  |  | 0
2019-07-05 03:00 | 4444 |  |  | 0
2019-07-05 04:00 | 4445 |  |  | 0
2019-07-05 05:00 | 4446 |  |  | 0.015836
2019-07-05 06:00 | 4447 |  |  | 0.03984
2019-07-05 07:00 | 4448 |  |  | 0.11435
2019-07-05 08:00 | 4449 |  |  | 0.28271
2019-07-05 09:00 | 4450 |  |  | 0.44907
2019-07-05 10:00 | 4451 |  |  | 0.58018
2019-07-05 11:00 | 4452 |  |  | 0.66578
2019-07-05 12:00 | 4453 |  |  | 0.70703
2019-07-05 13:00 | 4454 |  |  | 0.71545
2019-07-05 14:00 | 4455 |  |  | 0.67511
2019-07-05 15:00 | 4456 |  |  | 0.60485
2019-07-05 16:00 | 4457 |  |  | 0.49725
2019-07-05 17:00 | 4458 |  |  | 0.34872
2019-07-05 18:00 | 4459 |  |  | 0.17095
2019-07-05 19:00 | 4460 |  |  | 0.036089
2019-07-05 20:00 | 4461 |  |  | 0.00050008
2019-07-05 21:00 | 4462 |  |  | 0
2019-07-05 22:00 | 4463 |  |  | 0
2019-07-05 23:00 | 4464 |  |  | 0
2019-07-06 | 4465 |  |  | 0
2019-07-06 01:00 | 4466 |  |  | 0
2019-07-06 02:00 | 4467 |  |  | 0
2019-07-06 03:00 | 4468 |  |  | 0
2019-07-06 04:00 | 4469 |  |  | 0
2019-07-06 05:00 | 4470 |  |  | 0.014836
2019-07-06 06:00 | 4471 |  |  | 0.041757
2019-07-06 07:00 | 4472 |  |  | 0.11335
2019-07-06 08:00 | 4473 |  |  | 0.27755
2019-07-06 09:00 | 4474 |  |  | 0.43316
2019-07-06 10:00 | 4475 |  |  | 0.55201
2019-07-06 11:00 | 4476 |  |  | 0.63569
2019-07-06 12:00 | 4477 |  |  | 0.66953
2019-07-06 13:00 | 4478 |  |  | 0.50458
2019-07-06 14:00 | 4479 |  |  | 0.51717
2019-07-06 15:00 | 4480 |  |  | 0.33089
2019-07-06 16:00 | 4481 |  |  | 0.24437
2019-07-06 17:00 | 4482 |  |  | 0.081097
2019-07-06 18:00 | 4483 |  |  | 0.054926
2019-07-06 19:00 | 4484 |  |  | 0.014252
2019-07-06 20:00 | 4485 |  |  | 0.00025004
2019-07-06 21:00 | 4486 |  |  | 0
2019-07-06 22:00 | 4487 |  |  | 0
2019-07-06 23:00 | 4488 |  |  | 0
2019-07-07 | 4489 |  |  | 0
2019-07-07 01:00 | 4490 |  |  | 0
2019-07-07 02:00 | 4491 |  |  | 0
2019-07-07 03:00 | 4492 |  |  | 0
2019-07-07 04:00 | 4493 |  |  | 0.00025004
2019-07-07 05:00 | 4494 |  |  | 0.030672
2019-07-07 06:00 | 4495 |  |  | 0.072845
2019-07-07 07:00 | 4496 |  |  | 0.13111
2019-07-07 08:00 | 4497 |  |  | 0.28546
2019-07-07 09:00 | 4498 |  |  | 0.3934
2019-07-07 10:00 | 4499 |  |  | 0.58268
2019-07-07 11:00 | 4500 |  |  | 0.67211
2019-07-07 12:00 | 4501 |  |  | 0.69428
2019-07-07 13:00 | 4502 |  |  | 0.68028
2019-07-07 14:00 | 4503 |  |  | 0.54159
2019-07-07 15:00 | 4504 |  |  | 0.41924
2019-07-07 16:00 | 4505 |  |  | 0.39298
2019-07-07 17:00 | 4506 |  |  | 0.27205
2019-07-07 18:00 | 4507 |  |  | 0.16944
2019-07-07 19:00 | 4508 |  |  | 0.043424
2019-07-07 20:00 | 4509 |  |  | 0.00025004
2019-07-07 21:00 | 4510 |  |  | 0
2019-07-07 22:00 | 4511 |  |  | 0
2019-07-07 23:00 | 4512 |  |  | 0
2019-07-08 | 4513 |  |  | 0
2019-07-08 01:00 | 4514 |  |  | 0
2019-07-08 02:00 | 4515 |  |  | 0
2019-07-08 03:00 | 4516 |  |  | 0
2019-07-08 04:00 | 4517 |  |  | 8.3347e-05
2019-07-08 05:00 | 4518 |  |  | 0.018753
2019-07-08 06:00 | 4519 |  |  | 0.064427
2019-07-08 07:00 | 4520 |  |  | 0.12585
2019-07-08 08:00 | 4521 |  |  | 0.28771
2019-07-08 09:00 | 4522 |  |  | 0.40473
2019-07-08 10:00 | 4523 |  |  | 0.503
2019-07-08 11:00 | 4524 |  |  | 0.65161
2019-07-08 12:00 | 4525 |  |  | 0.71404
2019-07-08 13:00 | 4526 |  |  | 0.72445
2019-07-08 14:00 | 4527 |  |  | 0.68136
2019-07-08 15:00 | 4528 |  |  | 0.59302
2019-07-08 16:00 | 4529 |  |  | 0.49358
2019-07-08 17:00 | 4530 |  |  | 0.35814
2019-07-08 18:00 | 4531 |  |  | 0.14877
2019-07-08 19:00 | 4532 |  |  | 0.024921
2019-07-08 20:00 | 4533 |  |  | 0.00033339
2019-07-08 21:00 | 4534 |  |  | 0
2019-07-08 22:00 | 4535 |  |  | 0
2019-07-08 23:00 | 4536 |  |  | 0
2019-07-09 | 4537 |  |  | 0
2019-07-09 01:00 | 4538 |  |  | 0
2019-07-09 02:00 | 4539 |  |  | 0
2019-07-09 03:00 | 4540 |  |  | 0
2019-07-09 04:00 | 4541 |  |  | 0
2019-07-09 05:00 | 4542 |  |  | 0.013252
2019-07-09 06:00 | 4543 |  |  | 0.052009
2019-07-09 07:00 | 4544 |  |  | 0.048425
2019-07-09 08:00 | 4545 |  |  | 0.14244
2019-07-09 09:00 | 4546 |  |  | 0.33156
2019-07-09 10:00 | 4547 |  |  | 0.44299
2019-07-09 11:00 | 4548 |  |  | 0.52859
2019-07-09 12:00 | 4549 |  |  | 0.29497
2019-07-09 13:00 | 4550 |  |  | 0.14911
2019-07-09 14:00 | 4551 |  |  | 0.11119
2019-07-09 15:00 | 4552 |  |  | 0.45116
2019-07-09 16:00 | 4553 |  |  | 0.43774
2019-07-09 17:00 | 4554 |  |  | 0.33539
2019-07-09 18:00 | 4555 |  |  | 0.1161
2019-07-09 19:00 | 4556 |  |  | 0.010502
2019-07-09 20:00 | 4557 |  |  | 0.00016669
2019-07-09 21:00 | 4558 |  |  | 0
2019-07-09 22:00 | 4559 |  |  | 0
2019-07-09 23:00 | 4560 |  |  | 0
2019-07-10 | 4561 |  |  | 0
2019-07-10 01:00 | 4562 |  |  | 0
2019-07-10 02:00 | 4563 |  |  | 0
2019-07-10 03:00 | 4564 |  |  | 0
2019-07-10 04:00 | 4565 |  |  | 0
2019-07-10 05:00 | 4566 |  |  | 0.0076679
2019-07-10 06:00 | 4567 |  |  | 0.02267
2019-07-10 07:00 | 4568 |  |  | 0.050092
2019-07-10 08:00 | 4569 |  |  | 0.13444
2019-07-10 09:00 | 4570 |  |  | 0.20003
2019-07-10 10:00 | 4571 |  |  | 0.3233
2019-07-10 11:00 | 4572 |  |  | 0.45991
2019-07-10 12:00 | 4573 |  |  | 0.45191
2019-07-10 13:00 | 4574 |  |  | 0.49225
2019-07-10 14:00 | 4575 |  |  | 0.25879
2019-07-10 15:00 | 4576 |  |  | 0.26746
2019-07-10 16:00 | 4577 |  |  | 0.15378
2019-07-10 17:00 | 4578 |  |  | 0.1136
2019-07-10 18:00 | 4579 |  |  | 0.041507
2019-07-10 19:00 | 4580 |  |  | 0.010418
2019-07-10 20:00 | 4581 |  |  | 0
2019-07-10 21:00 | 4582 |  |  | 0
2019-07-10 22:00 | 4583 |  |  | 0
2019-07-10 23:00 | 4584 |  |  | 0
2019-07-11 | 4585 |  |  | 0
2019-07-11 01:00 | 4586 |  |  | 0
2019-07-11 02:00 | 4587 |  |  | 0
2019-07-11 03:00 | 4588 |  |  | 0
2019-07-11 04:00 | 4589 |  |  | 0
2019-07-11 05:00 | 4590 |  |  | 0.0051675
2019-07-11 06:00 | 4591 |  |  | 0.042174
2019-07-11 07:00 | 4592 |  |  | 0.11927
2019-07-11 08:00 | 4593 |  |  | 0.1827
2019-07-11 09:00 | 4594 |  |  | 0.34281
2019-07-11 10:00 | 4595 |  |  | 0.37315
2019-07-11 11:00 | 4596 |  |  | 0.47416
2019-07-11 12:00 | 4597 |  |  | 0.34822
2019-07-11 13:00 | 4598 |  |  | 0.45316
2019-07-11 14:00 | 4599 |  |  | 0.44466
2019-07-11 15:00 | 4600 |  |  | 0.2908
2019-07-11 16:00 | 4601 |  |  | 0.20928
2019-07-11 17:00 | 4602 |  |  | 0.11252
2019-07-11 18:00 | 4603 |  |  | 0.067761
2019-07-11 19:00 | 4604 |  |  | 0.026004
2019-07-11 20:00 | 4605 |  |  | 0.00016669
2019-07-11 21:00 | 4606 |  |  | 0
2019-07-11 22:00 | 4607 |  |  | 0
2019-07-11 23:00 | 4608 |  |  | 0
2019-07-12 | 4609 |  |  | 0
2019-07-12 01:00 | 4610 |  |  | 0
2019-07-12 02:00 | 4611 |  |  | 0
2019-07-12 03:00 | 4612 |  |  | 0
2019-07-12 04:00 | 4613 |  |  | 0
2019-07-12 05:00 | 4614 |  |  | 0.011835
2019-07-12 06:00 | 4615 |  |  | 0.053926
2019-07-12 07:00 | 4616 |  |  | 0.11952
2019-07-12 08:00 | 4617 |  |  | 0.27471
2019-07-12 09:00 | 4618 |  |  | 0.43716
2019-07-12 10:00 | 4619 |  |  | 0.53376
2019-07-12 11:00 | 4620 |  |  | 0.6762
2019-07-12 12:00 | 4621 |  |  | 0.70587
2019-07-12 13:00 | 4622 |  |  | 0.72254
2019-07-12 14:00 | 4623 |  |  | 0.6912
2019-07-12 15:00 | 4624 |  |  | 0.61877
2019-07-12 16:00 | 4625 |  |  | 0.49975
2019-07-12 17:00 | 4626 |  |  | 0.35639
2019-07-12 18:00 | 4627 |  |  | 0.17753
2019-07-12 19:00 | 4628 |  |  | 0.024171
2019-07-12 20:00 | 4629 |  |  | 0.00016669
2019-07-12 21:00 | 4630 |  |  | 0
2019-07-12 22:00 | 4631 |  |  | 0
2019-07-12 23:00 | 4632 |  |  | 0
2019-07-13 | 4633 |  |  | 0
2019-07-13 01:00 | 4634 |  |  | 0
2019-07-13 02:00 | 4635 |  |  | 0
2019-07-13 03:00 | 4636 |  |  | 0
2019-07-13 04:00 | 4637 |  |  | 0
2019-07-13 05:00 | 4638 |  |  | 0.012502
2019-07-13 06:00 | 4639 |  |  | 0.037006
2019-07-13 07:00 | 4640 |  |  | 0.10618
2019-07-13 08:00 | 4641 |  |  | 0.27813
2019-07-13 09:00 | 4642 |  |  | 0.45033
2019-07-13 10:00 | 4643 |  |  | 0.57901
2019-07-13 11:00 | 4644 |  |  | 0.59635
2019-07-13 12:00 | 4645 |  |  | 0.6827
2019-07-13 13:00 | 4646 |  |  | 0.65803
2019-07-13 14:00 | 4647 |  |  | 0.48991
2019-07-13 15:00 | 4648 |  |  | 0.5866
2019-07-13 16:00 | 4649 |  |  | 0.50467
2019-07-13 17:00 | 4650 |  |  | 0.34939
2019-07-13 18:00 | 4651 |  |  | 0.16553
2019-07-13 19:00 | 4652 |  |  | 0.032422
2019-07-13 20:00 | 4653 |  |  | 0.00041674
2019-07-13 21:00 | 4654 |  |  | 0
2019-07-13 22:00 | 4655 |  |  | 0
2019-07-13 23:00 | 4656 |  |  | 0
2019-07-14 | 4657 |  |  | 0
2019-07-14 01:00 | 4658 |  |  | 0
2019-07-14 02:00 | 4659 |  |  | 0
2019-07-14 03:00 | 4660 |  |  | 0
2019-07-14 04:00 | 4661 |  |  | 0
2019-07-14 05:00 | 4662 |  |  | 0.012419
2019-07-14 06:00 | 4663 |  |  | 0.03984
2019-07-14 07:00 | 4664 |  |  | 0.11527
2019-07-14 08:00 | 4665 |  |  | 0.29147
2019-07-14 09:00 | 4666 |  |  | 0.42507
2019-07-14 10:00 | 4667 |  |  | 0.58185
2019-07-14 11:00 | 4668 |  |  | 0.67111
2019-07-14 12:00 | 4669 |  |  | 0.73346
2019-07-14 13:00 | 4670 |  |  | 0.75071
2019-07-14 14:00 | 4671 |  |  | 0.67603
2019-07-14 15:00 | 4672 |  |  | 0.36539
2019-07-14 16:00 | 4673 |  |  | 0.085931
2019-07-14 17:00 | 4674 |  |  | 0.069428
2019-07-14 18:00 | 4675 |  |  | 0.043174
2019-07-14 19:00 | 4676 |  |  | 0.0026671
2019-07-14 20:00 | 4677 |  |  | 0
2019-07-14 21:00 | 4678 |  |  | 0
2019-07-14 22:00 | 4679 |  |  | 0
2019-07-14 23:00 | 4680 |  |  | 0
2019-07-15 | 4681 |  |  | 0
2019-07-15 01:00 | 4682 |  |  | 0
2019-07-15 02:00 | 4683 |  |  | 0
2019-07-15 03:00 | 4684 |  |  | 0
2019-07-15 04:00 | 4685 |  |  | 0
2019-07-15 05:00 | 4686 |  |  | 0
2019-07-15 06:00 | 4687 |  |  | 0.00041674
2019-07-15 07:00 | 4688 |  |  | 0.0045008
2019-07-15 08:00 | 4689 |  |  | 0.032505
2019-07-15 09:00 | 4690 |  |  | 0.032589
2019-07-15 10:00 | 4691 |  |  | 0.039673
2019-07-15 11:00 | 4692 |  |  | 0.040923
2019-07-15 12:00 | 4693 |  |  | 0.054092
2019-07-15 13:00 | 4694 |  |  | 0.085014
2019-07-15 14:00 | 4695 |  |  | 0.1076
2019-07-15 15:00 | 4696 |  |  | 0.11835
2019-07-15 16:00 | 4697 |  |  | 0.18145
2019-07-15 17:00 | 4698 |  |  | 0.22054
2019-07-15 18:00 | 4699 |  |  | 0.19028
2019-07-15 19:00 | 4700 |  |  | 0.038006
2019-07-15 20:00 | 4701 |  |  | 0.00058343
2019-07-15 21:00 | 4702 |  |  | 0
2019-07-15 22:00 | 4703 |  |  | 0
2019-07-15 23:00 | 4704 |  |  | 0
2019-07-16 | 4705 |  |  | 0
2019-07-16 01:00 | 4706 |  |  | 0
2019-07-16 02:00 | 4707 |  |  | 0
2019-07-16 03:00 | 4708 |  |  | 0
2019-07-16 04:00 | 4709 |  |  | 0
2019-07-16 05:00 | 4710 |  |  | 0.011419
2019-07-16 06:00 | 4711 |  |  | 0.028421
2019-07-16 07:00 | 4712 |  |  | 0.097516
2019-07-16 08:00 | 4713 |  |  | 0.2908
2019-07-16 09:00 | 4714 |  |  | 0.46858
2019-07-16 10:00 | 4715 |  |  | 0.59827
2019-07-16 11:00 | 4716 |  |  | 0.70312
2019-07-16 12:00 | 4717 |  |  | 0.75329
2019-07-16 13:00 | 4718 |  |  | 0.75279
2019-07-16 14:00 | 4719 |  |  | 0.72795
2019-07-16 15:00 | 4720 |  |  | 0.65153
2019-07-16 16:00 | 4721 |  |  | 0.52759
2019-07-16 17:00 | 4722 |  |  | 0.36214
2019-07-16 18:00 | 4723 |  |  | 0.14136
2019-07-16 19:00 | 4724 |  |  | 0.031172
2019-07-16 20:00 | 4725 |  |  | 0.00050008
2019-07-16 21:00 | 4726 |  |  | 0
2019-07-16 22:00 | 4727 |  |  | 0
2019-07-16 23:00 | 4728 |  |  | 0
2019-07-17 | 4729 |  |  | 0
2019-07-17 01:00 | 4730 |  |  | 0
2019-07-17 02:00 | 4731 |  |  | 0
2019-07-17 03:00 | 4732 |  |  | 0
2019-07-17 04:00 | 4733 |  |  | 0
2019-07-17 05:00 | 4734 |  |  | 0.0082514
2019-07-17 06:00 | 4735 |  |  | 0.031755
2019-07-17 07:00 | 4736 |  |  | 0.10118
2019-07-17 08:00 | 4737 |  |  | 0.2823
2019-07-17 09:00 | 4738 |  |  | 0.44932
2019-07-17 10:00 | 4739 |  |  | 0.5911
2019-07-17 11:00 | 4740 |  |  | 0.42932
2019-07-17 12:00 | 4741 |  |  | 0.67736
2019-07-17 13:00 | 4742 |  |  | 0.52217
2019-07-17 14:00 | 4743 |  |  | 0.66553
2019-07-17 15:00 | 4744 |  |  | 0.59477
2019-07-17 16:00 | 4745 |  |  | 0.41274
2019-07-17 17:00 | 4746 |  |  | 0.19112
2019-07-17 18:00 | 4747 |  |  | 0.15194
2019-07-17 19:00 | 4748 |  |  | 0.035839
2019-07-17 20:00 | 4749 |  |  | 0
2019-07-17 21:00 | 4750 |  |  | 0
2019-07-17 22:00 | 4751 |  |  | 0
2019-07-17 23:00 | 4752 |  |  | 0
2019-07-18 | 4753 |  |  | 0
2019-07-18 01:00 | 4754 |  |  | 0
2019-07-18 02:00 | 4755 |  |  | 0
2019-07-18 03:00 | 4756 |  |  | 0
2019-07-18 04:00 | 4757 |  |  | 0
2019-07-18 05:00 | 4758 |  |  | 0.0052509
2019-07-18 06:00 | 4759 |  |  | 0.055259
2019-07-18 07:00 | 4760 |  |  | 0.11977
2019-07-18 08:00 | 4761 |  |  | 0.26429
2019-07-18 09:00 | 4762 |  |  | 0.44441
2019-07-18 10:00 | 4763 |  |  | 0.5841
2019-07-18 11:00 | 4764 |  |  | 0.62344
2019-07-18 12:00 | 4765 |  |  | 0.58485
2019-07-18 13:00 | 4766 |  |  | 0.35548
2019-07-18 14:00 | 4767 |  |  | 0.44207
2019-07-18 15:00 | 4768 |  |  | 0.29963
2019-07-18 16:00 | 4769 |  |  | 0.14911
2019-07-18 17:00 | 4770 |  |  | 0.10702
2019-07-18 18:00 | 4771 |  |  | 0.062427
2019-07-18 19:00 | 4772 |  |  | 0.022754
2019-07-18 20:00 | 4773 |  |  | 0
2019-07-18 21:00 | 4774 |  |  | 0
2019-07-18 22:00 | 4775 |  |  | 0
2019-07-18 23:00 | 4776 |  |  | 0
2019-07-19 | 4777 |  |  | 0
2019-07-19 01:00 | 4778 |  |  | 0
2019-07-19 02:00 | 4779 |  |  | 0
2019-07-19 03:00 | 4780 |  |  | 0
2019-07-19 04:00 | 4781 |  |  | 0
2019-07-19 05:00 | 4782 |  |  | 0.010002
2019-07-19 06:00 | 4783 |  |  | 0.05801
2019-07-19 07:00 | 4784 |  |  | 0.14277
2019-07-19 08:00 | 4785 |  |  | 0.26371
2019-07-19 09:00 | 4786 |  |  | 0.42115
2019-07-19 10:00 | 4787 |  |  | 0.56326
2019-07-19 11:00 | 4788 |  |  | 0.61469
2019-07-19 12:00 | 4789 |  |  | 0.43582
2019-07-19 13:00 | 4790 |  |  | 0.2728
2019-07-19 14:00 | 4791 |  |  | 0.19903
2019-07-19 15:00 | 4792 |  |  | 0.31289
2019-07-19 16:00 | 4793 |  |  | 0.23104
2019-07-19 17:00 | 4794 |  |  | 0.23962
2019-07-19 18:00 | 4795 |  |  | 0.11227
2019-07-19 19:00 | 4796 |  |  | 0.024171
2019-07-19 20:00 | 4797 |  |  | 8.3347e-05
2019-07-19 21:00 | 4798 |  |  | 0
2019-07-19 22:00 | 4799 |  |  | 0
2019-07-19 23:00 | 4800 |  |  | 0
2019-07-20 | 4801 |  |  | 0
2019-07-20 01:00 | 4802 |  |  | 0
2019-07-20 02:00 | 4803 |  |  | 0
2019-07-20 03:00 | 4804 |  |  | 0
2019-07-20 04:00 | 4805 |  |  | 0
2019-07-20 05:00 | 4806 |  |  | 0.012919
2019-07-20 06:00 | 4807 |  |  | 0.05976
2019-07-20 07:00 | 4808 |  |  | 0.11769
2019-07-20 08:00 | 4809 |  |  | 0.22812
2019-07-20 09:00 | 4810 |  |  | 0.42757
2019-07-20 10:00 | 4811 |  |  | 0.53959
2019-07-20 11:00 | 4812 |  |  | 0.64419
2019-07-20 12:00 | 4813 |  |  | 0.59285
2019-07-20 13:00 | 4814 |  |  | 0.60235
2019-07-20 14:00 | 4815 |  |  | 0.48341
2019-07-20 15:00 | 4816 |  |  | 0.35381
2019-07-20 16:00 | 4817 |  |  | 0.16594
2019-07-20 17:00 | 4818 |  |  | 0.24971
2019-07-20 18:00 | 4819 |  |  | 0.10727
2019-07-20 19:00 | 4820 |  |  | 0.023837
2019-07-20 20:00 | 4821 |  |  | 8.3347e-05
2019-07-20 21:00 | 4822 |  |  | 0
2019-07-20 22:00 | 4823 |  |  | 0
2019-07-20 23:00 | 4824 |  |  | 0
2019-07-21 | 4825 |  |  | 0
2019-07-21 01:00 | 4826 |  |  | 0
2019-07-21 02:00 | 4827 |  |  | 0
2019-07-21 03:00 | 4828 |  |  | 0
2019-07-21 04:00 | 4829 |  |  | 0
2019-07-21 05:00 | 4830 |  |  | 0.0090848
2019-07-21 06:00 | 4831 |  |  | 0.057676
2019-07-21 07:00 | 4832 |  |  | 0.12694
2019-07-21 08:00 | 4833 |  |  | 0.2738
2019-07-21 09:00 | 4834 |  |  | 0.41849
2019-07-21 10:00 | 4835 |  |  | 0.53042
2019-07-21 11:00 | 4836 |  |  | 0.25929
2019-07-21 12:00 | 4837 |  |  | 0.62252
2019-07-21 13:00 | 4838 |  |  | 0.47316
2019-07-21 14:00 | 4839 |  |  | 0.64869
2019-07-21 15:00 | 4840 |  |  | 0.56776
2019-07-21 16:00 | 4841 |  |  | 0.45658
2019-07-21 17:00 | 4842 |  |  | 0.31397
2019-07-21 18:00 | 4843 |  |  | 0.13994
2019-07-21 19:00 | 4844 |  |  | 0.023254
2019-07-21 20:00 | 4845 |  |  | 0
2019-07-21 21:00 | 4846 |  |  | 0
2019-07-21 22:00 | 4847 |  |  | 0
2019-07-21 23:00 | 4848 |  |  | 0
2019-07-22 | 4849 |  |  | 0
2019-07-22 01:00 | 4850 |  |  | 0
2019-07-22 02:00 | 4851 |  |  | 0
2019-07-22 03:00 | 4852 |  |  | 0
2019-07-22 04:00 | 4853 |  |  | 0
2019-07-22 05:00 | 4854 |  |  | 0.012002
2019-07-22 06:00 | 4855 |  |  | 0.046674
2019-07-22 07:00 | 4856 |  |  | 0.13136
2019-07-22 08:00 | 4857 |  |  | 0.24262
2019-07-22 09:00 | 4858 |  |  | 0.40432
2019-07-22 10:00 | 4859 |  |  | 0.45833
2019-07-22 11:00 | 4860 |  |  | 0.526
2019-07-22 12:00 | 4861 |  |  | 0.50208
2019-07-22 13:00 | 4862 |  |  | 0.67495
2019-07-22 14:00 | 4863 |  |  | 0.66178
2019-07-22 15:00 | 4864 |  |  | 0.56951
2019-07-22 16:00 | 4865 |  |  | 0.45141
2019-07-22 17:00 | 4866 |  |  | 0.28563
2019-07-22 18:00 | 4867 |  |  | 0.12685
2019-07-22 19:00 | 4868 |  |  | 0.025088
2019-07-22 20:00 | 4869 |  |  | 0
2019-07-22 21:00 | 4870 |  |  | 0
2019-07-22 22:00 | 4871 |  |  | 0
2019-07-22 23:00 | 4872 |  |  | 0
2019-07-23 | 4873 |  |  | 0
2019-07-23 01:00 | 4874 |  |  | 0
2019-07-23 02:00 | 4875 |  |  | 0
2019-07-23 03:00 | 4876 |  |  | 0
2019-07-23 04:00 | 4877 |  |  | 0
2019-07-23 05:00 | 4878 |  |  | 0.014586
2019-07-23 06:00 | 4879 |  |  | 0.052425
2019-07-23 07:00 | 4880 |  |  | 0.11685
2019-07-23 08:00 | 4881 |  |  | 0.25763
2019-07-23 09:00 | 4882 |  |  | 0.41057
2019-07-23 10:00 | 4883 |  |  | 0.54751
2019-07-23 11:00 | 4884 |  |  | 0.63877
2019-07-23 12:00 | 4885 |  |  | 0.57185
2019-07-23 13:00 | 4886 |  |  | 0.66528
2019-07-23 14:00 | 4887 |  |  | 0.65861
2019-07-23 15:00 | 4888 |  |  | 0.57293
2019-07-23 16:00 | 4889 |  |  | 0.46383
2019-07-23 17:00 | 4890 |  |  | 0.30922
2019-07-23 18:00 | 4891 |  |  | 0.0996
2019-07-23 19:00 | 4892 |  |  | 0.0048341
2019-07-23 20:00 | 4893 |  |  | 0
2019-07-23 21:00 | 4894 |  |  | 0
2019-07-23 22:00 | 4895 |  |  | 0
2019-07-23 23:00 | 4896 |  |  | 0
2019-07-24 | 4897 |  |  | 0
2019-07-24 01:00 | 4898 |  |  | 0
2019-07-24 02:00 | 4899 |  |  | 0
2019-07-24 03:00 | 4900 |  |  | 0
2019-07-24 04:00 | 4901 |  |  | 0
2019-07-24 05:00 | 4902 |  |  | 0.010668
2019-07-24 06:00 | 4903 |  |  | 0.04259
2019-07-24 07:00 | 4904 |  |  | 0.10285
2019-07-24 08:00 | 4905 |  |  | 0.25296
2019-07-24 09:00 | 4906 |  |  | 0.41449
2019-07-24 10:00 | 4907 |  |  | 0.54551
2019-07-24 11:00 | 4908 |  |  | 0.63811
2019-07-24 12:00 | 4909 |  |  | 0.6862
2019-07-24 13:00 | 4910 |  |  | 0.69212
2019-07-24 14:00 | 4911 |  |  | 0.65486
2019-07-24 15:00 | 4912 |  |  | 0.5035
2019-07-24 16:00 | 4913 |  |  | 0.15569
2019-07-24 17:00 | 4914 |  |  | 0.10685
2019-07-24 18:00 | 4915 |  |  | 0.054259
2019-07-24 19:00 | 4916 |  |  | 0.013419
2019-07-24 20:00 | 4917 |  |  | 0
2019-07-24 21:00 | 4918 |  |  | 0
2019-07-24 22:00 | 4919 |  |  | 0
2019-07-24 23:00 | 4920 |  |  | 0
2019-07-25 | 4921 |  |  | 0
2019-07-25 01:00 | 4922 |  |  | 0
2019-07-25 02:00 | 4923 |  |  | 0
2019-07-25 03:00 | 4924 |  |  | 0
2019-07-25 04:00 | 4925 |  |  | 0
2019-07-25 05:00 | 4926 |  |  | 0.0097516
2019-07-25 06:00 | 4927 |  |  | 0.040923
2019-07-25 07:00 | 4928 |  |  | 0.1006
2019-07-25 08:00 | 4929 |  |  | 0.25113
2019-07-25 09:00 | 4930 |  |  | 0.40715
2019-07-25 10:00 | 4931 |  |  | 0.52625
2019-07-25 11:00 | 4932 |  |  | 0.5926
2019-07-25 12:00 | 4933 |  |  | 0.68036
2019-07-25 13:00 | 4934 |  |  | 0.68386
2019-07-25 14:00 | 4935 |  |  | 0.65736
2019-07-25 15:00 | 4936 |  |  | 0.59168
2019-07-25 16:00 | 4937 |  |  | 0.41557
2019-07-25 17:00 | 4938 |  |  | 0.11269
2019-07-25 18:00 | 4939 |  |  | 0.030672
2019-07-25 19:00 | 4940 |  |  | 0.0086681
2019-07-25 20:00 | 4941 |  |  | 0
2019-07-25 21:00 | 4942 |  |  | 0
2019-07-25 22:00 | 4943 |  |  | 0
2019-07-25 23:00 | 4944 |  |  | 0
2019-07-26 | 4945 |  |  | 0
2019-07-26 01:00 | 4946 |  |  | 0
2019-07-26 02:00 | 4947 |  |  | 0
2019-07-26 03:00 | 4948 |  |  | 0
2019-07-26 04:00 | 4949 |  |  | 0
2019-07-26 05:00 | 4950 |  |  | 0.026754
2019-07-26 06:00 | 4951 |  |  | 0.067011
2019-07-26 07:00 | 4952 |  |  | 0.13144
2019-07-26 08:00 | 4953 |  |  | 0.25596
2019-07-26 09:00 | 4954 |  |  | 0.41257
2019-07-26 10:00 | 4955 |  |  | 0.43057
2019-07-26 11:00 | 4956 |  |  | 0.29447
2019-07-26 12:00 | 4957 |  |  | 0.55443
2019-07-26 13:00 | 4958 |  |  | 0.6892
2019-07-26 14:00 | 4959 |  |  | 0.53834
2019-07-26 15:00 | 4960 |  |  | 0.59735
2019-07-26 16:00 | 4961 |  |  | 0.46449
2019-07-26 17:00 | 4962 |  |  | 0.24246
2019-07-26 18:00 | 4963 |  |  | 0.1016
2019-07-26 19:00 | 4964 |  |  | 0.017586
2019-07-26 20:00 | 4965 |  |  | 0
2019-07-26 21:00 | 4966 |  |  | 0
2019-07-26 22:00 | 4967 |  |  | 0
2019-07-26 23:00 | 4968 |  |  | 0
2019-07-27 | 4969 |  |  | 0
2019-07-27 01:00 | 4970 |  |  | 0
2019-07-27 02:00 | 4971 |  |  | 0
2019-07-27 03:00 | 4972 |  |  | 0
2019-07-27 04:00 | 4973 |  |  | 0
2019-07-27 05:00 | 4974 |  |  | 0.0073346
2019-07-27 06:00 | 4975 |  |  | 0.044591
2019-07-27 07:00 | 4976 |  |  | 0.086431
2019-07-27 08:00 | 4977 |  |  | 0.27821
2019-07-27 09:00 | 4978 |  |  | 0.19078
2019-07-27 10:00 | 4979 |  |  | 0.38623
2019-07-27 11:00 | 4980 |  |  | 0.59602
2019-07-27 12:00 | 4981 |  |  | 0.23721
2019-07-27 13:00 | 4982 |  |  | 0.012919
2019-07-27 14:00 | 4983 |  |  | 0.012169
2019-07-27 15:00 | 4984 |  |  | 0.22287
2019-07-27 16:00 | 4985 |  |  | 0.32589
2019-07-27 17:00 | 4986 |  |  | 0.1927
2019-07-27 18:00 | 4987 |  |  | 0.090015
2019-07-27 19:00 | 4988 |  |  | 0.02292
2019-07-27 20:00 | 4989 |  |  | 0
2019-07-27 21:00 | 4990 |  |  | 0
2019-07-27 22:00 | 4991 |  |  | 0
2019-07-27 23:00 | 4992 |  |  | 0
2019-07-28 | 4993 |  |  | 0
2019-07-28 01:00 | 4994 |  |  | 0
2019-07-28 02:00 | 4995 |  |  | 0
2019-07-28 03:00 | 4996 |  |  | 0
2019-07-28 04:00 | 4997 |  |  | 0
2019-07-28 05:00 | 4998 |  |  | 0.00050008
2019-07-28 06:00 | 4999 |  |  | 0.034006
2019-07-28 07:00 | 5000 |  |  | 0.066094
2019-07-28 08:00 | 5001 |  |  | 0.22504
2019-07-28 09:00 | 5002 |  |  | 0.44282
2019-07-28 10:00 | 5003 |  |  | 0.42732
2019-07-28 11:00 | 5004 |  |  | 0.60752
2019-07-28 12:00 | 5005 |  |  | 0.74829
2019-07-28 13:00 | 5006 |  |  | 0.70862
2019-07-28 14:00 | 5007 |  |  | 0.69353
2019-07-28 15:00 | 5008 |  |  | 0.64102
2019-07-28 16:00 | 5009 |  |  | 0.52309
2019-07-28 17:00 | 5010 |  |  | 0.35089
2019-07-28 18:00 | 5011 |  |  | 0.15928
2019-07-28 19:00 | 5012 |  |  | 0.025171
2019-07-28 20:00 | 5013 |  |  | 0
2019-07-28 21:00 | 5014 |  |  | 0
2019-07-28 22:00 | 5015 |  |  | 0
2019-07-28 23:00 | 5016 |  |  | 0
2019-07-29 | 5017 |  |  | 0
2019-07-29 01:00 | 5018 |  |  | 0
2019-07-29 02:00 | 5019 |  |  | 0
2019-07-29 03:00 | 5020 |  |  | 0
2019-07-29 04:00 | 5021 |  |  | 0
2019-07-29 05:00 | 5022 |  |  | 0.0070845
2019-07-29 06:00 | 5023 |  |  | 0.026504
2019-07-29 07:00 | 5024 |  |  | 0.087598
2019-07-29 08:00 | 5025 |  |  | 0.27213
2019-07-29 09:00 | 5026 |  |  | 0.44857
2019-07-29 10:00 | 5027 |  |  | 0.57985
2019-07-29 11:00 | 5028 |  |  | 0.68286
2019-07-29 12:00 | 5029 |  |  | 0.73504
2019-07-29 13:00 | 5030 |  |  | 0.74012
2019-07-29 14:00 | 5031 |  |  | 0.7112
2019-07-29 15:00 | 5032 |  |  | 0.63111
2019-07-29 16:00 | 5033 |  |  | 0.47816
2019-07-29 17:00 | 5034 |  |  | 0.36289
2019-07-29 18:00 | 5035 |  |  | 0.15919
2019-07-29 19:00 | 5036 |  |  | 0.021254
2019-07-29 20:00 | 5037 |  |  | 0
2019-07-29 21:00 | 5038 |  |  | 0
2019-07-29 22:00 | 5039 |  |  | 0
2019-07-29 23:00 | 5040 |  |  | 0
2019-07-30 | 5041 |  |  | 0
2019-07-30 01:00 | 5042 |  |  | 0
2019-07-30 02:00 | 5043 |  |  | 0
2019-07-30 03:00 | 5044 |  |  | 0
2019-07-30 04:00 | 5045 |  |  | 0
2019-07-30 05:00 | 5046 |  |  | 0.0064177
2019-07-30 06:00 | 5047 |  |  | 0.025921
2019-07-30 07:00 | 5048 |  |  | 0.085014
2019-07-30 08:00 | 5049 |  |  | 0.26663
2019-07-30 09:00 | 5050 |  |  | 0.44049
2019-07-30 10:00 | 5051 |  |  | 0.57801
2019-07-30 11:00 | 5052 |  |  | 0.66828
2019-07-30 12:00 | 5053 |  |  | 0.71512
2019-07-30 13:00 | 5054 |  |  | 0.73712
2019-07-30 14:00 | 5055 |  |  | 0.69378
2019-07-30 15:00 | 5056 |  |  | 0.62469
2019-07-30 16:00 | 5057 |  |  | 0.50542
2019-07-30 17:00 | 5058 |  |  | 0.2813
2019-07-30 18:00 | 5059 |  |  | 0.15078
2019-07-30 19:00 | 5060 |  |  | 0.015586
2019-07-30 20:00 | 5061 |  |  | 0
2019-07-30 21:00 | 5062 |  |  | 0
2019-07-30 22:00 | 5063 |  |  | 0
2019-07-30 23:00 | 5064 |  |  | 0
2019-07-31 | 5065 |  |  | 0
2019-07-31 01:00 | 5066 |  |  | 0
2019-07-31 02:00 | 5067 |  |  | 0
2019-07-31 03:00 | 5068 |  |  | 0
2019-07-31 04:00 | 5069 |  |  | 0
2019-07-31 05:00 | 5070 |  |  | 0.0075013
2019-07-31 06:00 | 5071 |  |  | 0.037673
2019-07-31 07:00 | 5072 |  |  | 0.095099
2019-07-31 08:00 | 5073 |  |  | 0.25938
2019-07-31 09:00 | 5074 |  |  | 0.43841
2019-07-31 10:00 | 5075 |  |  | 0.5766
2019-07-31 11:00 | 5076 |  |  | 0.63827
2019-07-31 12:00 | 5077 |  |  | 0.61644
2019-07-31 13:00 | 5078 |  |  | 0.5751
2019-07-31 14:00 | 5079 |  |  | 0.1947
2019-07-31 15:00 | 5080 |  |  | 0.30897
2019-07-31 16:00 | 5081 |  |  | 0.26929
2019-07-31 17:00 | 5082 |  |  | 0.093432
2019-07-31 18:00 | 5083 |  |  | 0.02217
2019-07-31 19:00 | 5084 |  |  | 0.0080013
2019-07-31 20:00 | 5085 |  |  | 0
2019-07-31 21:00 | 5086 |  |  | 0
2019-07-31 22:00 | 5087 |  |  | 0
2019-07-31 23:00 | 5088 |  |  | 0
2019-08-01 | 5089 |  |  | 0
2019-08-01 01:00 | 5090 |  |  | 0
2019-08-01 02:00 | 5091 |  |  | 0
2019-08-01 03:00 | 5092 |  |  | 0
2019-08-01 04:00 | 5093 |  |  | 0
2019-08-01 05:00 | 5094 |  |  | 0.0067511
2019-08-01 06:00 | 5095 |  |  | 0.038673
2019-08-01 07:00 | 5096 |  |  | 0.092015
2019-08-01 08:00 | 5097 |  |  | 0.22854
2019-08-01 09:00 | 5098 |  |  | 0.38715
2019-08-01 10:00 | 5099 |  |  | 0.49592
2019-08-01 11:00 | 5100 |  |  | 0.49583
2019-08-01 12:00 | 5101 |  |  | 0.40923
2019-08-01 13:00 | 5102 |  |  | 0.12569
2019-08-01 14:00 | 5103 |  |  | 0.26279
2019-08-01 15:00 | 5104 |  |  | 0.1917
2019-08-01 16:00 | 5105 |  |  | 0.16569
2019-08-01 17:00 | 5106 |  |  | 0.14044
2019-08-01 18:00 | 5107 |  |  | 0.11085
2019-08-01 19:00 | 5108 |  |  | 0.019003
2019-08-01 20:00 | 5109 |  |  | 0
2019-08-01 21:00 | 5110 |  |  | 0
2019-08-01 22:00 | 5111 |  |  | 0
2019-08-01 23:00 | 5112 |  |  | 0
2019-08-02 | 5113 |  |  | 0
2019-08-02 01:00 | 5114 |  |  | 0
2019-08-02 02:00 | 5115 |  |  | 0
2019-08-02 03:00 | 5116 |  |  | 0
2019-08-02 04:00 | 5117 |  |  | 0
2019-08-02 05:00 | 5118 |  |  | 0.0064177
2019-08-02 06:00 | 5119 |  |  | 0.035339
2019-08-02 07:00 | 5120 |  |  | 0.092765
2019-08-02 08:00 | 5121 |  |  | 0.25921
2019-08-02 09:00 | 5122 |  |  | 0.44857
2019-08-02 10:00 | 5123 |  |  | 0.34022
2019-08-02 11:00 | 5124 |  |  | 0.64511
2019-08-02 12:00 | 5125 |  |  | 0.7232
2019-08-02 13:00 | 5126 |  |  | 0.70803
2019-08-02 14:00 | 5127 |  |  | 0.69045
2019-08-02 15:00 | 5128 |  |  | 0.24579
2019-08-02 16:00 | 5129 |  |  | 0.30638
2019-08-02 17:00 | 5130 |  |  | 0.34156
2019-08-02 18:00 | 5131 |  |  | 0.14527
2019-08-02 19:00 | 5132 |  |  | 0.017503
2019-08-02 20:00 | 5133 |  |  | 0
2019-08-02 21:00 | 5134 |  |  | 0
2019-08-02 22:00 | 5135 |  |  | 0
2019-08-02 23:00 | 5136 |  |  | 0
2019-08-03 | 5137 |  |  | 0
2019-08-03 01:00 | 5138 |  |  | 0
2019-08-03 02:00 | 5139 |  |  | 0
2019-08-03 03:00 | 5140 |  |  | 0
2019-08-03 04:00 | 5141 |  |  | 0
2019-08-03 05:00 | 5142 |  |  | 0.0069178
2019-08-03 06:00 | 5143 |  |  | 0.030338
2019-08-03 07:00 | 5144 |  |  | 0.088515
2019-08-03 08:00 | 5145 |  |  | 0.26529
2019-08-03 09:00 | 5146 |  |  | 0.44807
2019-08-03 10:00 | 5147 |  |  | 0.57401
2019-08-03 11:00 | 5148 |  |  | 0.6767
2019-08-03 12:00 | 5149 |  |  | 0.72912
2019-08-03 13:00 | 5150 |  |  | 0.73121
2019-08-03 14:00 | 5151 |  |  | 0.72937
2019-08-03 15:00 | 5152 |  |  | 0.24746
2019-08-03 16:00 | 5153 |  |  | 0.13111
2019-08-03 17:00 | 5154 |  |  | 0.29697
2019-08-03 18:00 | 5155 |  |  | 0.10143
2019-08-03 19:00 | 5156 |  |  | 0.011919
2019-08-03 20:00 | 5157 |  |  | 0
2019-08-03 21:00 | 5158 |  |  | 0
2019-08-03 22:00 | 5159 |  |  | 0
2019-08-03 23:00 | 5160 |  |  | 0
2019-08-04 | 5161 |  |  | 0
2019-08-04 01:00 | 5162 |  |  | 0
2019-08-04 02:00 | 5163 |  |  | 0
2019-08-04 03:00 | 5164 |  |  | 0
2019-08-04 04:00 | 5165 |  |  | 0
2019-08-04 05:00 | 5166 |  |  | 0.0044174
2019-08-04 06:00 | 5167 |  |  | 0.030338
2019-08-04 07:00 | 5168 |  |  | 0.093932
2019-08-04 08:00 | 5169 |  |  | 0.24954
2019-08-04 09:00 | 5170 |  |  | 0.42007
2019-08-04 10:00 | 5171 |  |  | 0.57301
2019-08-04 11:00 | 5172 |  |  | 0.66636
2019-08-04 12:00 | 5173 |  |  | 0.7072
2019-08-04 13:00 | 5174 |  |  | 0.6006
2019-08-04 14:00 | 5175 |  |  | 0.46449
2019-08-04 15:00 | 5176 |  |  | 0.56609
2019-08-04 16:00 | 5177 |  |  | 0.13869
2019-08-04 17:00 | 5178 |  |  | 0.10227
2019-08-04 18:00 | 5179 |  |  | 0.046924
2019-08-04 19:00 | 5180 |  |  | 0.008168
2019-08-04 20:00 | 5181 |  |  | 0
2019-08-04 21:00 | 5182 |  |  | 0
2019-08-04 22:00 | 5183 |  |  | 0
2019-08-04 23:00 | 5184 |  |  | 0
2019-08-05 | 5185 |  |  | 0
2019-08-05 01:00 | 5186 |  |  | 0
2019-08-05 02:00 | 5187 |  |  | 0
2019-08-05 03:00 | 5188 |  |  | 0
2019-08-05 04:00 | 5189 |  |  | 0
2019-08-05 05:00 | 5190 |  |  | 0.0061677
2019-08-05 06:00 | 5191 |  |  | 0.044841
2019-08-05 07:00 | 5192 |  |  | 0.10527
2019-08-05 08:00 | 5193 |  |  | 0.25163
2019-08-05 09:00 | 5194 |  |  | 0.41949
2019-08-05 10:00 | 5195 |  |  | 0.55418
2019-08-05 11:00 | 5196 |  |  | 0.65986
2019-08-05 12:00 | 5197 |  |  | 0.48641
2019-08-05 13:00 | 5198 |  |  | 0.41824
2019-08-05 14:00 | 5199 |  |  | 0.33347
2019-08-05 15:00 | 5200 |  |  | 0.30963
2019-08-05 16:00 | 5201 |  |  | 0.23079
2019-08-05 17:00 | 5202 |  |  | 0.13544
2019-08-05 18:00 | 5203 |  |  | 0.039173
2019-08-05 19:00 | 5204 |  |  | 0.0051675
2019-08-05 20:00 | 5205 |  |  | 0
2019-08-05 21:00 | 5206 |  |  | 0
2019-08-05 22:00 | 5207 |  |  | 0
2019-08-05 23:00 | 5208 |  |  | 0
2019-08-06 | 5209 |  |  | 0
2019-08-06 01:00 | 5210 |  |  | 0
2019-08-06 02:00 | 5211 |  |  | 0
2019-08-06 03:00 | 5212 |  |  | 0
2019-08-06 04:00 | 5213 |  |  | 0
2019-08-06 05:00 | 5214 |  |  | 0.0047508
2019-08-06 06:00 | 5215 |  |  | 0.047008
2019-08-06 07:00 | 5216 |  |  | 0.12127
2019-08-06 08:00 | 5217 |  |  | 0.21512
2019-08-06 09:00 | 5218 |  |  | 0.40398
2019-08-06 10:00 | 5219 |  |  | 0.54684
2019-08-06 11:00 | 5220 |  |  | 0.64644
2019-08-06 12:00 | 5221 |  |  | 0.50033
2019-08-06 13:00 | 5222 |  |  | 0.48425
2019-08-06 14:00 | 5223 |  |  | 0.45466
2019-08-06 15:00 | 5224 |  |  | 0.23162
2019-08-06 16:00 | 5225 |  |  | 0.14002
2019-08-06 17:00 | 5226 |  |  | 0.063344
2019-08-06 18:00 | 5227 |  |  | 0.030088
2019-08-06 19:00 | 5228 |  |  | 0.0036673
2019-08-06 20:00 | 5229 |  |  | 0
2019-08-06 21:00 | 5230 |  |  | 0
2019-08-06 22:00 | 5231 |  |  | 0
2019-08-06 23:00 | 5232 |  |  | 0
2019-08-07 | 5233 |  |  | 0
2019-08-07 01:00 | 5234 |  |  | 0
2019-08-07 02:00 | 5235 |  |  | 0
2019-08-07 03:00 | 5236 |  |  | 0
2019-08-07 04:00 | 5237 |  |  | 0
2019-08-07 05:00 | 5238 |  |  | 0
2019-08-07 06:00 | 5239 |  |  | 0.0088348
2019-08-07 07:00 | 5240 |  |  | 0.033172
2019-08-07 08:00 | 5241 |  |  | 0.054426
2019-08-07 09:00 | 5242 |  |  | 0.035506
2019-08-07 10:00 | 5243 |  |  | 0.086514
2019-08-07 11:00 | 5244 |  |  | 0.14502
2019-08-07 12:00 | 5245 |  |  | 0.13886
2019-08-07 13:00 | 5246 |  |  | 0.20545
2019-08-07 14:00 | 5247 |  |  | 0.51384
2019-08-07 15:00 | 5248 |  |  | 0.37031
2019-08-07 16:00 | 5249 |  |  | 0.1897
2019-08-07 17:00 | 5250 |  |  | 0.062094
2019-08-07 18:00 | 5251 |  |  | 0.030755
2019-08-07 19:00 | 5252 |  |  | 0.0029172
2019-08-07 20:00 | 5253 |  |  | 0
2019-08-07 21:00 | 5254 |  |  | 0
2019-08-07 22:00 | 5255 |  |  | 0
2019-08-07 23:00 | 5256 |  |  | 0
2019-08-08 | 5257 |  |  | 0
2019-08-08 01:00 | 5258 |  |  | 0
2019-08-08 02:00 | 5259 |  |  | 0
2019-08-08 03:00 | 5260 |  |  | 0
2019-08-08 04:00 | 5261 |  |  | 0
2019-08-08 05:00 | 5262 |  |  | 0.0070012
2019-08-08 06:00 | 5263 |  |  | 0.046674
2019-08-08 07:00 | 5264 |  |  | 0.12152
2019-08-08 08:00 | 5265 |  |  | 0.25404
2019-08-08 09:00 | 5266 |  |  | 0.44257
2019-08-08 10:00 | 5267 |  |  | 0.56001
2019-08-08 11:00 | 5268 |  |  | 0.65036
2019-08-08 12:00 | 5269 |  |  | 0.64544
2019-08-08 13:00 | 5270 |  |  | 0.69603
2019-08-08 14:00 | 5271 |  |  | 0.67236
2019-08-08 15:00 | 5272 |  |  | 0.61844
2019-08-08 16:00 | 5273 |  |  | 0.45024
2019-08-08 17:00 | 5274 |  |  | 0.31614
2019-08-08 18:00 | 5275 |  |  | 0.11952
2019-08-08 19:00 | 5276 |  |  | 0.010418
2019-08-08 20:00 | 5277 |  |  | 0
2019-08-08 21:00 | 5278 |  |  | 0
2019-08-08 22:00 | 5279 |  |  | 0
2019-08-08 23:00 | 5280 |  |  | 0
2019-08-09 | 5281 |  |  | 0
2019-08-09 01:00 | 5282 |  |  | 0
2019-08-09 02:00 | 5283 |  |  | 0
2019-08-09 03:00 | 5284 |  |  | 0
2019-08-09 04:00 | 5285 |  |  | 0
2019-08-09 05:00 | 5286 |  |  | 0.0046674
2019-08-09 06:00 | 5287 |  |  | 0.057843
2019-08-09 07:00 | 5288 |  |  | 0.096516
2019-08-09 08:00 | 5289 |  |  | 0.11519
2019-08-09 09:00 | 5290 |  |  | 0.29947
2019-08-09 10:00 | 5291 |  |  | 0.54442
2019-08-09 11:00 | 5292 |  |  | 0.64069
2019-08-09 12:00 | 5293 |  |  | 0.71137
2019-08-09 13:00 | 5294 |  |  | 0.25096
2019-08-09 14:00 | 5295 |  |  | 0.20528
2019-08-09 15:00 | 5296 |  |  | 0.18145
2019-08-09 16:00 | 5297 |  |  | 0.11619
2019-08-09 17:00 | 5298 |  |  | 0.067428
2019-08-09 18:00 | 5299 |  |  | 0.025254
2019-08-09 19:00 | 5300 |  |  | 0.0015836
2019-08-09 20:00 | 5301 |  |  | 0
2019-08-09 21:00 | 5302 |  |  | 0
2019-08-09 22:00 | 5303 |  |  | 0
2019-08-09 23:00 | 5304 |  |  | 0
2019-08-10 | 5305 |  |  | 0
2019-08-10 01:00 | 5306 |  |  | 0
2019-08-10 02:00 | 5307 |  |  | 0
2019-08-10 03:00 | 5308 |  |  | 0
2019-08-10 04:00 | 5309 |  |  | 0
2019-08-10 05:00 | 5310 |  |  | 0.0030838
2019-08-10 06:00 | 5311 |  |  | 0.024671
2019-08-10 07:00 | 5312 |  |  | 0.094932
2019-08-10 08:00 | 5313 |  |  | 0.23896
2019-08-10 09:00 | 5314 |  |  | 0.40957
2019-08-10 10:00 | 5315 |  |  | 0.44149
2019-08-10 11:00 | 5316 |  |  | 0.57518
2019-08-10 12:00 | 5317 |  |  | 0.30113
2019-08-10 13:00 | 5318 |  |  | 0.26163
2019-08-10 14:00 | 5319 |  |  | 0.40082
2019-08-10 15:00 | 5320 |  |  | 0.18228
2019-08-10 16:00 | 5321 |  |  | 0.14811
2019-08-10 17:00 | 5322 |  |  | 0.13919
2019-08-10 18:00 | 5323 |  |  | 0.023254
2019-08-10 19:00 | 5324 |  |  | 0.0020837
2019-08-10 20:00 | 5325 |  |  | 0
2019-08-10 21:00 | 5326 |  |  | 0
2019-08-10 22:00 | 5327 |  |  | 0
2019-08-10 23:00 | 5328 |  |  | 0
2019-08-11 | 5329 |  |  | 0
2019-08-11 01:00 | 5330 |  |  | 0
2019-08-11 02:00 | 5331 |  |  | 0
2019-08-11 03:00 | 5332 |  |  | 0
2019-08-11 04:00 | 5333 |  |  | 0
2019-08-11 05:00 | 5334 |  |  | 0.0035839
2019-08-11 06:00 | 5335 |  |  | 0.035089
2019-08-11 07:00 | 5336 |  |  | 0.10535
2019-08-11 08:00 | 5337 |  |  | 0.23054
2019-08-11 09:00 | 5338 |  |  | 0.37356
2019-08-11 10:00 | 5339 |  |  | 0.53892
2019-08-11 11:00 | 5340 |  |  | 0.53692
2019-08-11 12:00 | 5341 |  |  | 0.4204
2019-08-11 13:00 | 5342 |  |  | 0.47683
2019-08-11 14:00 | 5343 |  |  | 0.13336
2019-08-11 15:00 | 5344 |  |  | 0.12985
2019-08-11 16:00 | 5345 |  |  | 0.35756
2019-08-11 17:00 | 5346 |  |  | 0.051175
2019-08-11 18:00 | 5347 |  |  | 0.02267
2019-08-11 19:00 | 5348 |  |  | 0.0080013
2019-08-11 20:00 | 5349 |  |  | 0
2019-08-11 21:00 | 5350 |  |  | 0
2019-08-11 22:00 | 5351 |  |  | 0
2019-08-11 23:00 | 5352 |  |  | 0
2019-08-12 | 5353 |  |  | 0
2019-08-12 01:00 | 5354 |  |  | 0
2019-08-12 02:00 | 5355 |  |  | 0
2019-08-12 03:00 | 5356 |  |  | 0
2019-08-12 04:00 | 5357 |  |  | 0
2019-08-12 05:00 | 5358 |  |  | 0.0030838
2019-08-12 06:00 | 5359 |  |  | 0.025004
2019-08-12 07:00 | 5360 |  |  | 0.11369
2019-08-12 08:00 | 5361 |  |  | 0.14344
2019-08-12 09:00 | 5362 |  |  | 0.22587
2019-08-12 10:00 | 5363 |  |  | 0.55584
2019-08-12 11:00 | 5364 |  |  | 0.44432
2019-08-12 12:00 | 5365 |  |  | 0.55418
2019-08-12 13:00 | 5366 |  |  | 0.25254
2019-08-12 14:00 | 5367 |  |  | 0.028255
2019-08-12 15:00 | 5368 |  |  | 0.28296
2019-08-12 16:00 | 5369 |  |  | 0.028505
2019-08-12 17:00 | 5370 |  |  | 0.23862
2019-08-12 18:00 | 5371 |  |  | 0.079097
2019-08-12 19:00 | 5372 |  |  | 0.0040007
2019-08-12 20:00 | 5373 |  |  | 0
2019-08-12 21:00 | 5374 |  |  | 0
2019-08-12 22:00 | 5375 |  |  | 0
2019-08-12 23:00 | 5376 |  |  | 0
2019-08-13 | 5377 |  |  | 0
2019-08-13 01:00 | 5378 |  |  | 0
2019-08-13 02:00 | 5379 |  |  | 0
2019-08-13 03:00 | 5380 |  |  | 0
2019-08-13 04:00 | 5381 |  |  | 0
2019-08-13 05:00 | 5382 |  |  | 0.0028338
2019-08-13 06:00 | 5383 |  |  | 0.024504
2019-08-13 07:00 | 5384 |  |  | 0.080513
2019-08-13 08:00 | 5385 |  |  | 0.26713
2019-08-13 09:00 | 5386 |  |  | 0.43699
2019-08-13 10:00 | 5387 |  |  | 0.4264
2019-08-13 11:00 | 5388 |  |  | 0.58335
2019-08-13 12:00 | 5389 |  |  | 0.53576
2019-08-13 13:00 | 5390 |  |  | 0.52342
2019-08-13 14:00 | 5391 |  |  | 0.52709
2019-08-13 15:00 | 5392 |  |  | 0.26654
2019-08-13 16:00 | 5393 |  |  | 0.49358
2019-08-13 17:00 | 5394 |  |  | 0.34539
2019-08-13 18:00 | 5395 |  |  | 0.12285
2019-08-13 19:00 | 5396 |  |  | 0.0076679
2019-08-13 20:00 | 5397 |  |  | 0
2019-08-13 21:00 | 5398 |  |  | 0
2019-08-13 22:00 | 5399 |  |  | 0
2019-08-13 23:00 | 5400 |  |  | 0
2019-08-14 | 5401 |  |  | 0
2019-08-14 01:00 | 5402 |  |  | 0
2019-08-14 02:00 | 5403 |  |  | 0
2019-08-14 03:00 | 5404 |  |  | 0
2019-08-14 04:00 | 5405 |  |  | 0
2019-08-14 05:00 | 5406 |  |  | 0.0033339
2019-08-14 06:00 | 5407 |  |  | 0.046258
2019-08-14 07:00 | 5408 |  |  | 0.13269
2019-08-14 08:00 | 5409 |  |  | 0.24396
2019-08-14 09:00 | 5410 |  |  | 0.27388
2019-08-14 10:00 | 5411 |  |  | 0.54734
2019-08-14 11:00 | 5412 |  |  | 0.64794
2019-08-14 12:00 | 5413 |  |  | 0.75271
2019-08-14 13:00 | 5414 |  |  | 0.76429
2019-08-14 14:00 | 5415 |  |  | 0.72645
2019-08-14 15:00 | 5416 |  |  | 0.56151
2019-08-14 16:00 | 5417 |  |  | 0.508
2019-08-14 17:00 | 5418 |  |  | 0.32714
2019-08-14 18:00 | 5419 |  |  | 0.1261
2019-08-14 19:00 | 5420 |  |  | 0.0075846
2019-08-14 20:00 | 5421 |  |  | 0
2019-08-14 21:00 | 5422 |  |  | 0
2019-08-14 22:00 | 5423 |  |  | 0
2019-08-14 23:00 | 5424 |  |  | 0
2019-08-15 | 5425 |  |  | 0
2019-08-15 01:00 | 5426 |  |  | 0
2019-08-15 02:00 | 5427 |  |  | 0
2019-08-15 03:00 | 5428 |  |  | 0
2019-08-15 04:00 | 5429 |  |  | 0
2019-08-15 05:00 | 5430 |  |  | 0.0046674
2019-08-15 06:00 | 5431 |  |  | 0.048758
2019-08-15 07:00 | 5432 |  |  | 0.10385
2019-08-15 08:00 | 5433 |  |  | 0.21312
2019-08-15 09:00 | 5434 |  |  | 0.39965
2019-08-15 10:00 | 5435 |  |  | 0.51634
2019-08-15 11:00 | 5436 |  |  | 0.46116
2019-08-15 12:00 | 5437 |  |  | 0.65419
2019-08-15 13:00 | 5438 |  |  | 0.59468
2019-08-15 14:00 | 5439 |  |  | 0.43024
2019-08-15 15:00 | 5440 |  |  | 0.34947
2019-08-15 16:00 | 5441 |  |  | 0.23237
2019-08-15 17:00 | 5442 |  |  | 0.086848
2019-08-15 18:00 | 5443 |  |  | 0.11369
2019-08-15 19:00 | 5444 |  |  | 0.0061677
2019-08-15 20:00 | 5445 |  |  | 0
2019-08-15 21:00 | 5446 |  |  | 0
2019-08-15 22:00 | 5447 |  |  | 0
2019-08-15 23:00 | 5448 |  |  | 0
2019-08-16 | 5449 |  |  | 0
2019-08-16 01:00 | 5450 |  |  | 0
2019-08-16 02:00 | 5451 |  |  | 0
2019-08-16 03:00 | 5452 |  |  | 0
2019-08-16 04:00 | 5453 |  |  | 0
2019-08-16 05:00 | 5454 |  |  | 0.001917
2019-08-16 06:00 | 5455 |  |  | 0.034922
2019-08-16 07:00 | 5456 |  |  | 0.10202
2019-08-16 08:00 | 5457 |  |  | 0.25588
2019-08-16 09:00 | 5458 |  |  | 0.43382
2019-08-16 10:00 | 5459 |  |  | 0.56518
2019-08-16 11:00 | 5460 |  |  | 0.63352
2019-08-16 12:00 | 5461 |  |  | 0.64977
2019-08-16 13:00 | 5462 |  |  | 0.472
2019-08-16 14:00 | 5463 |  |  | 0.25346
2019-08-16 15:00 | 5464 |  |  | 0.23404
2019-08-16 16:00 | 5465 |  |  | 0.23279
2019-08-16 17:00 | 5466 |  |  | 0.21945
2019-08-16 18:00 | 5467 |  |  | 0.09985
2019-08-16 19:00 | 5468 |  |  | 0.0036673
2019-08-16 20:00 | 5469 |  |  | 0
2019-08-16 21:00 | 5470 |  |  | 0
2019-08-16 22:00 | 5471 |  |  | 0
2019-08-16 23:00 | 5472 |  |  | 0
2019-08-17 | 5473 |  |  | 0
2019-08-17 01:00 | 5474 |  |  | 0
2019-08-17 02:00 | 5475 |  |  | 0
2019-08-17 03:00 | 5476 |  |  | 0
2019-08-17 04:00 | 5477 |  |  | 0
2019-08-17 05:00 | 5478 |  |  | 0.0015003
2019-08-17 06:00 | 5479 |  |  | 0.028505
2019-08-17 07:00 | 5480 |  |  | 0.10135
2019-08-17 08:00 | 5481 |  |  | 0.2147
2019-08-17 09:00 | 5482 |  |  | 0.43924
2019-08-17 10:00 | 5483 |  |  | 0.57601
2019-08-17 11:00 | 5484 |  |  | 0.50742
2019-08-17 12:00 | 5485 |  |  | 0.20912
2019-08-17 13:00 | 5486 |  |  | 0.15969
2019-08-17 14:00 | 5487 |  |  | 0.54667
2019-08-17 15:00 | 5488 |  |  | 0.38831
2019-08-17 16:00 | 5489 |  |  | 0.42665
2019-08-17 17:00 | 5490 |  |  | 0.23854
2019-08-17 18:00 | 5491 |  |  | 0.051425
2019-08-17 19:00 | 5492 |  |  | 0.0030838
2019-08-17 20:00 | 5493 |  |  | 0
2019-08-17 21:00 | 5494 |  |  | 0
2019-08-17 22:00 | 5495 |  |  | 0
2019-08-17 23:00 | 5496 |  |  | 0
2019-08-18 | 5497 |  |  | 0
2019-08-18 01:00 | 5498 |  |  | 0
2019-08-18 02:00 | 5499 |  |  | 0
2019-08-18 03:00 | 5500 |  |  | 0
2019-08-18 04:00 | 5501 |  |  | 0
2019-08-18 05:00 | 5502 |  |  | 0.0010002
2019-08-18 06:00 | 5503 |  |  | 0.036256
2019-08-18 07:00 | 5504 |  |  | 0.075179
2019-08-18 08:00 | 5505 |  |  | 0.18936
2019-08-18 09:00 | 5506 |  |  | 0.43941
2019-08-18 10:00 | 5507 |  |  | 0.59127
2019-08-18 11:00 | 5508 |  |  | 0.43966
2019-08-18 12:00 | 5509 |  |  | 0.43357
2019-08-18 13:00 | 5510 |  |  | 0.35281
2019-08-18 14:00 | 5511 |  |  | 0.27713
2019-08-18 15:00 | 5512 |  |  | 0.16178
2019-08-18 16:00 | 5513 |  |  | 0.094432
2019-08-18 17:00 | 5514 |  |  | 0.047841
2019-08-18 18:00 | 5515 |  |  | 0.02142
2019-08-18 19:00 | 5516 |  |  | 0.0010835
2019-08-18 20:00 | 5517 |  |  | 0
2019-08-18 21:00 | 5518 |  |  | 0
2019-08-18 22:00 | 5519 |  |  | 0
2019-08-18 23:00 | 5520 |  |  | 0
2019-08-19 | 5521 |  |  | 0
2019-08-19 01:00 | 5522 |  |  | 0
2019-08-19 02:00 | 5523 |  |  | 0
2019-08-19 03:00 | 5524 |  |  | 0
2019-08-19 04:00 | 5525 |  |  | 0
2019-08-19 05:00 | 5526 |  |  | 0.0025004
2019-08-19 06:00 | 5527 |  |  | 0.03984
2019-08-19 07:00 | 5528 |  |  | 0.070678
2019-08-19 08:00 | 5529 |  |  | 0.2152
2019-08-19 09:00 | 5530 |  |  | 0.38648
2019-08-19 10:00 | 5531 |  |  | 0.55318
2019-08-19 11:00 | 5532 |  |  | 0.58293
2019-08-19 12:00 | 5533 |  |  | 0.56301
2019-08-19 13:00 | 5534 |  |  | 0.49917
2019-08-19 14:00 | 5535 |  |  | 0.31472
2019-08-19 15:00 | 5536 |  |  | 0.14952
2019-08-19 16:00 | 5537 |  |  | 0.067011
2019-08-19 17:00 | 5538 |  |  | 0.092599
2019-08-19 18:00 | 5539 |  |  | 0.032172
2019-08-19 19:00 | 5540 |  |  | 0.0017503
2019-08-19 20:00 | 5541 |  |  | 0
2019-08-19 21:00 | 5542 |  |  | 0
2019-08-19 22:00 | 5543 |  |  | 0
2019-08-19 23:00 | 5544 |  |  | 0
2019-08-20 | 5545 |  |  | 0
2019-08-20 01:00 | 5546 |  |  | 0
2019-08-20 02:00 | 5547 |  |  | 0
2019-08-20 03:00 | 5548 |  |  | 0
2019-08-20 04:00 | 5549 |  |  | 0
2019-08-20 05:00 | 5550 |  |  | 0
2019-08-20 06:00 | 5551 |  |  | 0.0063344
2019-08-20 07:00 | 5552 |  |  | 0.052592
2019-08-20 08:00 | 5553 |  |  | 0.096599
2019-08-20 09:00 | 5554 |  |  | 0.22937
2019-08-20 10:00 | 5555 |  |  | 0.33856
2019-08-20 11:00 | 5556 |  |  | 0.29047
2019-08-20 12:00 | 5557 |  |  | 0.32355
2019-08-20 13:00 | 5558 |  |  | 0.47558
2019-08-20 14:00 | 5559 |  |  | 0.3233
2019-08-20 15:00 | 5560 |  |  | 0.25621
2019-08-20 16:00 | 5561 |  |  | 0.089348
2019-08-20 17:00 | 5562 |  |  | 0.067261
2019-08-20 18:00 | 5563 |  |  | 0.038173
2019-08-20 19:00 | 5564 |  |  | 0.001917
2019-08-20 20:00 | 5565 |  |  | 0
2019-08-20 21:00 | 5566 |  |  | 0
2019-08-20 22:00 | 5567 |  |  | 0
2019-08-20 23:00 | 5568 |  |  | 0
2019-08-21 | 5569 |  |  | 0
2019-08-21 01:00 | 5570 |  |  | 0
2019-08-21 02:00 | 5571 |  |  | 0
2019-08-21 03:00 | 5572 |  |  | 0
2019-08-21 04:00 | 5573 |  |  | 0
2019-08-21 05:00 | 5574 |  |  | 0
2019-08-21 06:00 | 5575 |  |  | 0.02217
2019-08-21 07:00 | 5576 |  |  | 0.076513
2019-08-21 08:00 | 5577 |  |  | 0.27405
2019-08-21 09:00 | 5578 |  |  | 0.45083
2019-08-21 10:00 | 5579 |  |  | 0.55734
2019-08-21 11:00 | 5580 |  |  | 0.65653
2019-08-21 12:00 | 5581 |  |  | 0.67395
2019-08-21 13:00 | 5582 |  |  | 0.58526
2019-08-21 14:00 | 5583 |  |  | 0.34581
2019-08-21 15:00 | 5584 |  |  | 0.44032
2019-08-21 16:00 | 5585 |  |  | 0.22287
2019-08-21 17:00 | 5586 |  |  | 0.085848
2019-08-21 18:00 | 5587 |  |  | 0.030422
2019-08-21 19:00 | 5588 |  |  | 0.0015836
2019-08-21 20:00 | 5589 |  |  | 0
2019-08-21 21:00 | 5590 |  |  | 0
2019-08-21 22:00 | 5591 |  |  | 0
2019-08-21 23:00 | 5592 |  |  | 0
2019-08-22 | 5593 |  |  | 0
2019-08-22 01:00 | 5594 |  |  | 0
2019-08-22 02:00 | 5595 |  |  | 0
2019-08-22 03:00 | 5596 |  |  | 0
2019-08-22 04:00 | 5597 |  |  | 0
2019-08-22 05:00 | 5598 |  |  | 0
2019-08-22 06:00 | 5599 |  |  | 8.3347e-05
2019-08-22 07:00 | 5600 |  |  | 0.00066678
2019-08-22 08:00 | 5601 |  |  | 0.0032505
2019-08-22 09:00 | 5602 |  |  | 0.011169
2019-08-22 10:00 | 5603 |  |  | 0.041924
2019-08-22 11:00 | 5604 |  |  | 0.13152
2019-08-22 12:00 | 5605 |  |  | 0.18503
2019-08-22 13:00 | 5606 |  |  | 0.38206
2019-08-22 14:00 | 5607 |  |  | 0.59452
2019-08-22 15:00 | 5608 |  |  | 0.62794
2019-08-22 16:00 | 5609 |  |  | 0.34956
2019-08-22 17:00 | 5610 |  |  | 0.20428
2019-08-22 18:00 | 5611 |  |  | 0.047925
2019-08-22 19:00 | 5612 |  |  | 0.0032505
2019-08-22 20:00 | 5613 |  |  | 0
2019-08-22 21:00 | 5614 |  |  | 0
2019-08-22 22:00 | 5615 |  |  | 0
2019-08-22 23:00 | 5616 |  |  | 0
2019-08-23 | 5617 |  |  | 0
2019-08-23 01:00 | 5618 |  |  | 0
2019-08-23 02:00 | 5619 |  |  | 0
2019-08-23 03:00 | 5620 |  |  | 0
2019-08-23 04:00 | 5621 |  |  | 0
2019-08-23 05:00 | 5622 |  |  | 0.00050008
2019-08-23 06:00 | 5623 |  |  | 0.026171
2019-08-23 07:00 | 5624 |  |  | 0.085348
2019-08-23 08:00 | 5625 |  |  | 0.20645
2019-08-23 09:00 | 5626 |  |  | 0.27046
2019-08-23 10:00 | 5627 |  |  | 0.38765
2019-08-23 11:00 | 5628 |  |  | 0.41057
2019-08-23 12:00 | 5629 |  |  | 0.2142
2019-08-23 13:00 | 5630 |  |  | 0.23937
2019-08-23 14:00 | 5631 |  |  | 0.64902
2019-08-23 15:00 | 5632 |  |  | 0.44349
2019-08-23 16:00 | 5633 |  |  | 0.4064
2019-08-23 17:00 | 5634 |  |  | 0.1832
2019-08-23 18:00 | 5635 |  |  | 0.030088
2019-08-23 19:00 | 5636 |  |  | 0.0017503
2019-08-23 20:00 | 5637 |  |  | 0
2019-08-23 21:00 | 5638 |  |  | 0
2019-08-23 22:00 | 5639 |  |  | 0
2019-08-23 23:00 | 5640 |  |  | 0
2019-08-24 | 5641 |  |  | 0
2019-08-24 01:00 | 5642 |  |  | 0
2019-08-24 02:00 | 5643 |  |  | 0
2019-08-24 03:00 | 5644 |  |  | 0
2019-08-24 04:00 | 5645 |  |  | 0
2019-08-24 05:00 | 5646 |  |  | 0.00041674
2019-08-24 06:00 | 5647 |  |  | 0.027588
2019-08-24 07:00 | 5648 |  |  | 0.088265
2019-08-24 08:00 | 5649 |  |  | 0.23104
2019-08-24 09:00 | 5650 |  |  | 0.40148
2019-08-24 10:00 | 5651 |  |  | 0.50225
2019-08-24 11:00 | 5652 |  |  | 0.57285
2019-08-24 12:00 | 5653 |  |  | 0.71054
2019-08-24 13:00 | 5654 |  |  | 0.56568
2019-08-24 14:00 | 5655 |  |  | 0.54134
2019-08-24 15:00 | 5656 |  |  | 0.3253
2019-08-24 16:00 | 5657 |  |  | 0.35039
2019-08-24 17:00 | 5658 |  |  | 0.1952
2019-08-24 18:00 | 5659 |  |  | 0.043091
2019-08-24 19:00 | 5660 |  |  | 0.0015003
2019-08-24 20:00 | 5661 |  |  | 0
2019-08-24 21:00 | 5662 |  |  | 0
2019-08-24 22:00 | 5663 |  |  | 0
2019-08-24 23:00 | 5664 |  |  | 0
2019-08-25 | 5665 |  |  | 0
2019-08-25 01:00 | 5666 |  |  | 0
2019-08-25 02:00 | 5667 |  |  | 0
2019-08-25 03:00 | 5668 |  |  | 0
2019-08-25 04:00 | 5669 |  |  | 0
2019-08-25 05:00 | 5670 |  |  | 0.00041674
2019-08-25 06:00 | 5671 |  |  | 0.033589
2019-08-25 07:00 | 5672 |  |  | 0.091349
2019-08-25 08:00 | 5673 |  |  | 0.22954
2019-08-25 09:00 | 5674 |  |  | 0.40515
2019-08-25 10:00 | 5675 |  |  | 0.53951
2019-08-25 11:00 | 5676 |  |  | 0.59727
2019-08-25 12:00 | 5677 |  |  | 0.54317
2019-08-25 13:00 | 5678 |  |  | 0.43757
2019-08-25 14:00 | 5679 |  |  | 0.59402
2019-08-25 15:00 | 5680 |  |  | 0.37648
2019-08-25 16:00 | 5681 |  |  | 0.46558
2019-08-25 17:00 | 5682 |  |  | 0.25588
2019-08-25 18:00 | 5683 |  |  | 0.067428
2019-08-25 19:00 | 5684 |  |  | 0.0014169
2019-08-25 20:00 | 5685 |  |  | 0
2019-08-25 21:00 | 5686 |  |  | 0
2019-08-25 22:00 | 5687 |  |  | 0
2019-08-25 23:00 | 5688 |  |  | 0
2019-08-26 | 5689 |  |  | 0
2019-08-26 01:00 | 5690 |  |  | 0
2019-08-26 02:00 | 5691 |  |  | 0
2019-08-26 03:00 | 5692 |  |  | 0
2019-08-26 04:00 | 5693 |  |  | 0
2019-08-26 05:00 | 5694 |  |  | 0.00033339
2019-08-26 06:00 | 5695 |  |  | 0.026921
2019-08-26 07:00 | 5696 |  |  | 0.092515
2019-08-26 08:00 | 5697 |  |  | 0.23279
2019-08-26 09:00 | 5698 |  |  | 0.39382
2019-08-26 10:00 | 5699 |  |  | 0.10543
2019-08-26 11:00 | 5700 |  |  | 0
2019-08-26 12:00 | 5701 |  |  | 0
2019-08-26 13:00 | 5702 |  |  | 0.26929
2019-08-26 14:00 | 5703 |  |  | 0.58126
2019-08-26 15:00 | 5704 |  |  | 0.51625
2019-08-26 16:00 | 5705 |  |  | 0.36889
2019-08-26 17:00 | 5706 |  |  | 0.23079
2019-08-26 18:00 | 5707 |  |  | 0.052592
2019-08-26 19:00 | 5708 |  |  | 0.00066678
2019-08-26 20:00 | 5709 |  |  | 0
2019-08-26 21:00 | 5710 |  |  | 0
2019-08-26 22:00 | 5711 |  |  | 0
2019-08-26 23:00 | 5712 |  |  | 0
2019-08-27 | 5713 |  |  | 0
2019-08-27 01:00 | 5714 |  |  | 0
2019-08-27 02:00 | 5715 |  |  | 0
2019-08-27 03:00 | 5716 |  |  | 0
2019-08-27 04:00 | 5717 |  |  | 0
2019-08-27 05:00 | 5718 |  |  | 0.00050008
2019-08-27 06:00 | 5719 |  |  | 0.030255
2019-08-27 07:00 | 5720 |  |  | 0.10002
2019-08-27 08:00 | 5721 |  |  | 0.2187
2019-08-27 09:00 | 5722 |  |  | 0.36514
2019-08-27 10:00 | 5723 |  |  | 0.50492
2019-08-27 11:00 | 5724 |  |  | 0.49333
2019-08-27 12:00 | 5725 |  |  | 0.44557
2019-08-27 13:00 | 5726 |  |  | 0.477
2019-08-27 14:00 | 5727 |  |  | 0.32497
2019-08-27 15:00 | 5728 |  |  | 0.23137
2019-08-27 16:00 | 5729 |  |  | 0.12444
2019-08-27 17:00 | 5730 |  |  | 0.079847
2019-08-27 18:00 | 5731 |  |  | 0.020003
2019-08-27 19:00 | 5732 |  |  | 0
2019-08-27 20:00 | 5733 |  |  | 0
2019-08-27 21:00 | 5734 |  |  | 0
2019-08-27 22:00 | 5735 |  |  | 0
2019-08-27 23:00 | 5736 |  |  | 0
2019-08-28 | 5737 |  |  | 0
2019-08-28 01:00 | 5738 |  |  | 0
2019-08-28 02:00 | 5739 |  |  | 0
2019-08-28 03:00 | 5740 |  |  | 0
2019-08-28 04:00 | 5741 |  |  | 0
2019-08-28 05:00 | 5742 |  |  | 0
2019-08-28 06:00 | 5743 |  |  | 0
2019-08-28 07:00 | 5744 |  |  | 0.015003
2019-08-28 08:00 | 5745 |  |  | 0.067261
2019-08-28 09:00 | 5746 |  |  | 0.13161
2019-08-28 10:00 | 5747 |  |  | 0.19403
2019-08-28 11:00 | 5748 |  |  | 0.16919
2019-08-28 12:00 | 5749 |  |  | 0.081264
2019-08-28 13:00 | 5750 |  |  | 0.12319
2019-08-28 14:00 | 5751 |  |  | 0.24471
2019-08-28 15:00 | 5752 |  |  | 0.23554
2019-08-28 16:00 | 5753 |  |  | 0.39382
2019-08-28 17:00 | 5754 |  |  | 0.27213
2019-08-28 18:00 | 5755 |  |  | 0.033756
2019-08-28 19:00 | 5756 |  |  | 0.00066678
2019-08-28 20:00 | 5757 |  |  | 0
2019-08-28 21:00 | 5758 |  |  | 0
2019-08-28 22:00 | 5759 |  |  | 0
2019-08-28 23:00 | 5760 |  |  | 0
2019-08-29 | 5761 |  |  | 0
2019-08-29 01:00 | 5762 |  |  | 0
2019-08-29 02:00 | 5763 |  |  | 0
2019-08-29 03:00 | 5764 |  |  | 0
2019-08-29 04:00 | 5765 |  |  | 0
2019-08-29 05:00 | 5766 |  |  | 8.3347e-05
2019-08-29 06:00 | 5767 |  |  | 0.037506
2019-08-29 07:00 | 5768 |  |  | 0.066928
2019-08-29 08:00 | 5769 |  |  | 0.24679
2019-08-29 09:00 | 5770 |  |  | 0.44241
2019-08-29 10:00 | 5771 |  |  | 0.58043
2019-08-29 11:00 | 5772 |  |  | 0.68345
2019-08-29 12:00 | 5773 |  |  | 0.73046
2019-08-29 13:00 | 5774 |  |  | 0.73279
2019-08-29 14:00 | 5775 |  |  | 0.67986
2019-08-29 15:00 | 5776 |  |  | 0.59035
2019-08-29 16:00 | 5777 |  |  | 0.44641
2019-08-29 17:00 | 5778 |  |  | 0.24212
2019-08-29 18:00 | 5779 |  |  | 0.043007
2019-08-29 19:00 | 5780 |  |  | 0.00041674
2019-08-29 20:00 | 5781 |  |  | 0
2019-08-29 21:00 | 5782 |  |  | 0
2019-08-29 22:00 | 5783 |  |  | 0
2019-08-29 23:00 | 5784 |  |  | 0
2019-08-30 | 5785 |  |  | 0
2019-08-30 01:00 | 5786 |  |  | 0
2019-08-30 02:00 | 5787 |  |  | 0
2019-08-30 03:00 | 5788 |  |  | 0
2019-08-30 04:00 | 5789 |  |  | 0
2019-08-30 05:00 | 5790 |  |  | 0.00025004
2019-08-30 06:00 | 5791 |  |  | 0.022004
2019-08-30 07:00 | 5792 |  |  | 0.073429
2019-08-30 08:00 | 5793 |  |  | 0.24571
2019-08-30 09:00 | 5794 |  |  | 0.4279
2019-08-30 10:00 | 5795 |  |  | 0.56218
2019-08-30 11:00 | 5796 |  |  | 0.66019
2019-08-30 12:00 | 5797 |  |  | 0.65369
2019-08-30 13:00 | 5798 |  |  | 0.67211
2019-08-30 14:00 | 5799 |  |  | 0.60068
2019-08-30 15:00 | 5800 |  |  | 0.5951
2019-08-30 16:00 | 5801 |  |  | 0.23229
2019-08-30 17:00 | 5802 |  |  | 0.089598
2019-08-30 18:00 | 5803 |  |  | 0.026504
2019-08-30 19:00 | 5804 |  |  | 0
2019-08-30 20:00 | 5805 |  |  | 0
2019-08-30 21:00 | 5806 |  |  | 0
2019-08-30 22:00 | 5807 |  |  | 0
2019-08-30 23:00 | 5808 |  |  | 0
2019-08-31 | 5809 |  |  | 0
2019-08-31 01:00 | 5810 |  |  | 0
2019-08-31 02:00 | 5811 |  |  | 0
2019-08-31 03:00 | 5812 |  |  | 0
2019-08-31 04:00 | 5813 |  |  | 0
2019-08-31 05:00 | 5814 |  |  | 8.3347e-05
2019-08-31 06:00 | 5815 |  |  | 0.023754
2019-08-31 07:00 | 5816 |  |  | 0.088348
2019-08-31 08:00 | 5817 |  |  | 0.23121
2019-08-31 09:00 | 5818 |  |  | 0.39065
2019-08-31 10:00 | 5819 |  |  | 0.54367
2019-08-31 11:00 | 5820 |  |  | 0.65494
2019-08-31 12:00 | 5821 |  |  | 0.69545
2019-08-31 13:00 | 5822 |  |  | 0.4715
2019-08-31 14:00 | 5823 |  |  | 0.17478
2019-08-31 15:00 | 5824 |  |  | 0.14477
2019-08-31 16:00 | 5825 |  |  | 0.42874
2019-08-31 17:00 | 5826 |  |  | 0.10902
2019-08-31 18:00 | 5827 |  |  | 0.025338
2019-08-31 19:00 | 5828 |  |  | 0
2019-08-31 20:00 | 5829 |  |  | 0
2019-08-31 21:00 | 5830 |  |  | 0
2019-08-31 22:00 | 5831 |  |  | 0
2019-08-31 23:00 | 5832 |  |  | 0
2019-09-01 | 5833 |  |  | 0
2019-09-01 01:00 | 5834 |  |  | 0
2019-09-01 02:00 | 5835 |  |  | 0
2019-09-01 03:00 | 5836 |  |  | 0
2019-09-01 04:00 | 5837 |  |  | 0
2019-09-01 05:00 | 5838 |  |  | 0
2019-09-01 06:00 | 5839 |  |  | 0.01717
2019-09-01 07:00 | 5840 |  |  | 0.086931
2019-09-01 08:00 | 5841 |  |  | 0.23354
2019-09-01 09:00 | 5842 |  |  | 0.41474
2019-09-01 10:00 | 5843 |  |  | 0.56376
2019-09-01 11:00 | 5844 |  |  | 0.66361
2019-09-01 12:00 | 5845 |  |  | 0.71345
2019-09-01 13:00 | 5846 |  |  | 0.68661
2019-09-01 14:00 | 5847 |  |  | 0.69012
2019-09-01 15:00 | 5848 |  |  | 0.58401
2019-09-01 16:00 | 5849 |  |  | 0.19387
2019-09-01 17:00 | 5850 |  |  | 0.029422
2019-09-01 18:00 | 5851 |  |  | 0.0074179
2019-09-01 19:00 | 5852 |  |  | 8.3347e-05
2019-09-01 20:00 | 5853 |  |  | 0
2019-09-01 21:00 | 5854 |  |  | 0
2019-09-01 22:00 | 5855 |  |  | 0
2019-09-01 23:00 | 5856 |  |  | 0
2019-09-02 | 5857 |  |  | 0
2019-09-02 01:00 | 5858 |  |  | 0
2019-09-02 02:00 | 5859 |  |  | 0
2019-09-02 03:00 | 5860 |  |  | 0
2019-09-02 04:00 | 5861 |  |  | 0
2019-09-02 05:00 | 5862 |  |  | 0
2019-09-02 06:00 | 5863 |  |  | 0.0072512
2019-09-02 07:00 | 5864 |  |  | 0.016586
2019-09-02 08:00 | 5865 |  |  | 0.056759
2019-09-02 09:00 | 5866 |  |  | 0.20512
2019-09-02 10:00 | 5867 |  |  | 0.54767
2019-09-02 11:00 | 5868 |  |  | 0.67345
2019-09-02 12:00 | 5869 |  |  | 0.72679
2019-09-02 13:00 | 5870 |  |  | 0.73096
2019-09-02 14:00 | 5871 |  |  | 0.57251
2019-09-02 15:00 | 5872 |  |  | 0.51134
2019-09-02 16:00 | 5873 |  |  | 0.4224
2019-09-02 17:00 | 5874 |  |  | 0.22929
2019-09-02 18:00 | 5875 |  |  | 0.042424
2019-09-02 19:00 | 5876 |  |  | 8.3347e-05
2019-09-02 20:00 | 5877 |  |  | 0
2019-09-02 21:00 | 5878 |  |  | 0
2019-09-02 22:00 | 5879 |  |  | 0
2019-09-02 23:00 | 5880 |  |  | 0
2019-09-03 | 5881 |  |  | 0
2019-09-03 01:00 | 5882 |  |  | 0
2019-09-03 02:00 | 5883 |  |  | 0
2019-09-03 03:00 | 5884 |  |  | 0
2019-09-03 04:00 | 5885 |  |  | 0
2019-09-03 05:00 | 5886 |  |  | 0
2019-09-03 06:00 | 5887 |  |  | 0.030672
2019-09-03 07:00 | 5888 |  |  | 0.1166
2019-09-03 08:00 | 5889 |  |  | 0.20603
2019-09-03 09:00 | 5890 |  |  | 0.34231
2019-09-03 10:00 | 5891 |  |  | 0.58985
2019-09-03 11:00 | 5892 |  |  | 0.70853
2019-09-03 12:00 | 5893 |  |  | 0.66003
2019-09-03 13:00 | 5894 |  |  | 0.72987
2019-09-03 14:00 | 5895 |  |  | 0.70062
2019-09-03 15:00 | 5896 |  |  | 0.60727
2019-09-03 16:00 | 5897 |  |  | 0.45733
2019-09-03 17:00 | 5898 |  |  | 0.24412
2019-09-03 18:00 | 5899 |  |  | 0.042007
2019-09-03 19:00 | 5900 |  |  | 0
2019-09-03 20:00 | 5901 |  |  | 0
2019-09-03 21:00 | 5902 |  |  | 0
2019-09-03 22:00 | 5903 |  |  | 0
2019-09-03 23:00 | 5904 |  |  | 0
2019-09-04 | 5905 |  |  | 0
2019-09-04 01:00 | 5906 |  |  | 0
2019-09-04 02:00 | 5907 |  |  | 0
2019-09-04 03:00 | 5908 |  |  | 0
2019-09-04 04:00 | 5909 |  |  | 0
2019-09-04 05:00 | 5910 |  |  | 0
2019-09-04 06:00 | 5911 |  |  | 0.023754
2019-09-04 07:00 | 5912 |  |  | 0.11294
2019-09-04 08:00 | 5913 |  |  | 0.098266
2019-09-04 09:00 | 5914 |  |  | 0.23562
2019-09-04 10:00 | 5915 |  |  | 0.30572
2019-09-04 11:00 | 5916 |  |  | 0.47366
2019-09-04 12:00 | 5917 |  |  | 0.53751
2019-09-04 13:00 | 5918 |  |  | 0.46958
2019-09-04 14:00 | 5919 |  |  | 0.30522
2019-09-04 15:00 | 5920 |  |  | 0.20153
2019-09-04 16:00 | 5921 |  |  | 0.29972
2019-09-04 17:00 | 5922 |  |  | 0.084431
2019-09-04 18:00 | 5923 |  |  | 0.018336
2019-09-04 19:00 | 5924 |  |  | 0
2019-09-04 20:00 | 5925 |  |  | 0
2019-09-04 21:00 | 5926 |  |  | 0
2019-09-04 22:00 | 5927 |  |  | 0
2019-09-04 23:00 | 5928 |  |  | 0
2019-09-05 | 5929 |  |  | 0
2019-09-05 01:00 | 5930 |  |  | 0
2019-09-05 02:00 | 5931 |  |  | 0
2019-09-05 03:00 | 5932 |  |  | 0
2019-09-05 04:00 | 5933 |  |  | 0
2019-09-05 05:00 | 5934 |  |  | 0
2019-09-05 06:00 | 5935 |  |  | 0.016086
2019-09-05 07:00 | 5936 |  |  | 0.069428
2019-09-05 08:00 | 5937 |  |  | 0.18745
2019-09-05 09:00 | 5938 |  |  | 0.35206
2019-09-05 10:00 | 5939 |  |  | 0.56943
2019-09-05 11:00 | 5940 |  |  | 0.51775
2019-09-05 12:00 | 5941 |  |  | 0.69562
2019-09-05 13:00 | 5942 |  |  | 0.43641
2019-09-05 14:00 | 5943 |  |  | 0.064011
2019-09-05 15:00 | 5944 |  |  | 0.031672
2019-09-05 16:00 | 5945 |  |  | 0.11852
2019-09-05 17:00 | 5946 |  |  | 0.034756
2019-09-05 18:00 | 5947 |  |  | 0.0012502
2019-09-05 19:00 | 5948 |  |  | 0
2019-09-05 20:00 | 5949 |  |  | 0
2019-09-05 21:00 | 5950 |  |  | 0
2019-09-05 22:00 | 5951 |  |  | 0
2019-09-05 23:00 | 5952 |  |  | 0
2019-09-06 | 5953 |  |  | 0
2019-09-06 01:00 | 5954 |  |  | 0
2019-09-06 02:00 | 5955 |  |  | 0
2019-09-06 03:00 | 5956 |  |  | 0
2019-09-06 04:00 | 5957 |  |  | 0
2019-09-06 05:00 | 5958 |  |  | 0
2019-09-06 06:00 | 5959 |  |  | 0.00016669
2019-09-06 07:00 | 5960 |  |  | 0.014752
2019-09-06 08:00 | 5961 |  |  | 0.044174
2019-09-06 09:00 | 5962 |  |  | 0.064927
2019-09-06 10:00 | 5963 |  |  | 0.072762
2019-09-06 11:00 | 5964 |  |  | 0.11435
2019-09-06 12:00 | 5965 |  |  | 0.068928
2019-09-06 13:00 | 5966 |  |  | 0.080347
2019-09-06 14:00 | 5967 |  |  | 0.11469
2019-09-06 15:00 | 5968 |  |  | 0.14494
2019-09-06 16:00 | 5969 |  |  | 0.19845
2019-09-06 17:00 | 5970 |  |  | 0.083347
2019-09-06 18:00 | 5971 |  |  | 0.015169
2019-09-06 19:00 | 5972 |  |  | 0
2019-09-06 20:00 | 5973 |  |  | 0
2019-09-06 21:00 | 5974 |  |  | 0
2019-09-06 22:00 | 5975 |  |  | 0
2019-09-06 23:00 | 5976 |  |  | 0
2019-09-07 | 5977 |  |  | 0
2019-09-07 01:00 | 5978 |  |  | 0
2019-09-07 02:00 | 5979 |  |  | 0
2019-09-07 03:00 | 5980 |  |  | 0
2019-09-07 04:00 | 5981 |  |  | 0
2019-09-07 05:00 | 5982 |  |  | 0
2019-09-07 06:00 | 5983 |  |  | 0.031839
2019-09-07 07:00 | 5984 |  |  | 0.07968
2019-09-07 08:00 | 5985 |  |  | 0.25763
2019-09-07 09:00 | 5986 |  |  | 0.23871
2019-09-07 10:00 | 5987 |  |  | 0.55384
2019-09-07 11:00 | 5988 |  |  | 0.62669
2019-09-07 12:00 | 5989 |  |  | 0.56726
2019-09-07 13:00 | 5990 |  |  | 0.73937
2019-09-07 14:00 | 5991 |  |  | 0.67203
2019-09-07 15:00 | 5992 |  |  | 0.6246
2019-09-07 16:00 | 5993 |  |  | 0.44241
2019-09-07 17:00 | 5994 |  |  | 0.073262
2019-09-07 18:00 | 5995 |  |  | 0.005751
2019-09-07 19:00 | 5996 |  |  | 0
2019-09-07 20:00 | 5997 |  |  | 0
2019-09-07 21:00 | 5998 |  |  | 0
2019-09-07 22:00 | 5999 |  |  | 0
2019-09-07 23:00 | 6000 |  |  | 0
2019-09-08 | 6001 |  |  | 0
2019-09-08 01:00 | 6002 |  |  | 0
2019-09-08 02:00 | 6003 |  |  | 0
2019-09-08 03:00 | 6004 |  |  | 0
2019-09-08 04:00 | 6005 |  |  | 0
2019-09-08 05:00 | 6006 |  |  | 0
2019-09-08 06:00 | 6007 |  |  | 0.015503
2019-09-08 07:00 | 6008 |  |  | 0.045758
2019-09-08 08:00 | 6009 |  |  | 0.10077
2019-09-08 09:00 | 6010 |  |  | 0.31189
2019-09-08 10:00 | 6011 |  |  | 0.35773
2019-09-08 11:00 | 6012 |  |  | 0.54184
2019-09-08 12:00 | 6013 |  |  | 0.6707
2019-09-08 13:00 | 6014 |  |  | 0.77821
2019-09-08 14:00 | 6015 |  |  | 0.53159
2019-09-08 15:00 | 6016 |  |  | 0.25279
2019-09-08 16:00 | 6017 |  |  | 0.045258
2019-09-08 17:00 | 6018 |  |  | 0.013002
2019-09-08 18:00 | 6019 |  |  | 0.032839
2019-09-08 19:00 | 6020 |  |  | 0
2019-09-08 20:00 | 6021 |  |  | 0
2019-09-08 21:00 | 6022 |  |  | 0
2019-09-08 22:00 | 6023 |  |  | 0
2019-09-08 23:00 | 6024 |  |  | 0
2019-09-09 | 6025 |  |  | 0
2019-09-09 01:00 | 6026 |  |  | 0
2019-09-09 02:00 | 6027 |  |  | 0
2019-09-09 03:00 | 6028 |  |  | 0
2019-09-09 04:00 | 6029 |  |  | 0
2019-09-09 05:00 | 6030 |  |  | 0
2019-09-09 06:00 | 6031 |  |  | 0.012419
2019-09-09 07:00 | 6032 |  |  | 0.066011
2019-09-09 08:00 | 6033 |  |  | 0.26721
2019-09-09 09:00 | 6034 |  |  | 0.47641
2019-09-09 10:00 | 6035 |  |  | 0.63877
2019-09-09 11:00 | 6036 |  |  | 0.74079
2019-09-09 12:00 | 6037 |  |  | 0.77188
2019-09-09 13:00 | 6038 |  |  | 0.74071
2019-09-09 14:00 | 6039 |  |  | 0.64136
2019-09-09 15:00 | 6040 |  |  | 0.43082
2019-09-09 16:00 | 6041 |  |  | 0.4164
2019-09-09 17:00 | 6042 |  |  | 0.15361
2019-09-09 18:00 | 6043 |  |  | 0.01767
2019-09-09 19:00 | 6044 |  |  | 0
2019-09-09 20:00 | 6045 |  |  | 0
2019-09-09 21:00 | 6046 |  |  | 0
2019-09-09 22:00 | 6047 |  |  | 0
2019-09-09 23:00 | 6048 |  |  | 0
2019-09-10 | 6049 |  |  | 0
2019-09-10 01:00 | 6050 |  |  | 0
2019-09-10 02:00 | 6051 |  |  | 0
2019-09-10 03:00 | 6052 |  |  | 0
2019-09-10 04:00 | 6053 |  |  | 0
2019-09-10 05:00 | 6054 |  |  | 0
2019-09-10 06:00 | 6055 |  |  | 0.0030838
2019-09-10 07:00 | 6056 |  |  | 0.048091
2019-09-10 08:00 | 6057 |  |  | 0.10077
2019-09-10 09:00 | 6058 |  |  | 0.12935
2019-09-10 10:00 | 6059 |  |  | 0.19328
2019-09-10 11:00 | 6060 |  |  | 0.15594
2019-09-10 12:00 | 6061 |  |  | 0.17536
2019-09-10 13:00 | 6062 |  |  | 0.21662
2019-09-10 14:00 | 6063 |  |  | 0.10527
2019-09-10 15:00 | 6064 |  |  | 0.18161
2019-09-10 16:00 | 6065 |  |  | 0.092015
2019-09-10 17:00 | 6066 |  |  | 0.034339
2019-09-10 18:00 | 6067 |  |  | 0.0011669
2019-09-10 19:00 | 6068 |  |  | 0
2019-09-10 20:00 | 6069 |  |  | 0
2019-09-10 21:00 | 6070 |  |  | 0
2019-09-10 22:00 | 6071 |  |  | 0
2019-09-10 23:00 | 6072 |  |  | 0
2019-09-11 | 6073 |  |  | 0
2019-09-11 01:00 | 6074 |  |  | 0
2019-09-11 02:00 | 6075 |  |  | 0
2019-09-11 03:00 | 6076 |  |  | 0
2019-09-11 04:00 | 6077 |  |  | 0
2019-09-11 05:00 | 6078 |  |  | 0
2019-09-11 06:00 | 6079 |  |  | 0.014169
2019-09-11 07:00 | 6080 |  |  | 0.068928
2019-09-11 08:00 | 6081 |  |  | 0.24446
2019-09-11 09:00 | 6082 |  |  | 0.44107
2019-09-11 10:00 | 6083 |  |  | 0.59385
2019-09-11 11:00 | 6084 |  |  | 0.69228
2019-09-11 12:00 | 6085 |  |  | 0.75946
2019-09-11 13:00 | 6086 |  |  | 0.75196
2019-09-11 14:00 | 6087 |  |  | 0.69878
2019-09-11 15:00 | 6088 |  |  | 0.48408
2019-09-11 16:00 | 6089 |  |  | 0.25579
2019-09-11 17:00 | 6090 |  |  | 0.1912
2019-09-11 18:00 | 6091 |  |  | 0.020753
2019-09-11 19:00 | 6092 |  |  | 0
2019-09-11 20:00 | 6093 |  |  | 0
2019-09-11 21:00 | 6094 |  |  | 0
2019-09-11 22:00 | 6095 |  |  | 0
2019-09-11 23:00 | 6096 |  |  | 0
2019-09-12 | 6097 |  |  | 0
2019-09-12 01:00 | 6098 |  |  | 0
2019-09-12 02:00 | 6099 |  |  | 0
2019-09-12 03:00 | 6100 |  |  | 0
2019-09-12 04:00 | 6101 |  |  | 0
2019-09-12 05:00 | 6102 |  |  | 0
2019-09-12 06:00 | 6103 |  |  | 0.010835
2019-09-12 07:00 | 6104 |  |  | 0.06026
2019-09-12 08:00 | 6105 |  |  | 0.24312
2019-09-12 09:00 | 6106 |  |  | 0.44291
2019-09-12 10:00 | 6107 |  |  | 0.5911
2019-09-12 11:00 | 6108 |  |  | 0.69537
2019-09-12 12:00 | 6109 |  |  | 0.74046
2019-09-12 13:00 | 6110 |  |  | 0.73279
2019-09-12 14:00 | 6111 |  |  | 0.69178
2019-09-12 15:00 | 6112 |  |  | 0.59893
2019-09-12 16:00 | 6113 |  |  | 0.44491
2019-09-12 17:00 | 6114 |  |  | 0.20203
2019-09-12 18:00 | 6115 |  |  | 0.018003
2019-09-12 19:00 | 6116 |  |  | 0
2019-09-12 20:00 | 6117 |  |  | 0
2019-09-12 21:00 | 6118 |  |  | 0
2019-09-12 22:00 | 6119 |  |  | 0
2019-09-12 23:00 | 6120 |  |  | 0
2019-09-13 | 6121 |  |  | 0
2019-09-13 01:00 | 6122 |  |  | 0
2019-09-13 02:00 | 6123 |  |  | 0
2019-09-13 03:00 | 6124 |  |  | 0
2019-09-13 04:00 | 6125 |  |  | 0
2019-09-13 05:00 | 6126 |  |  | 0
2019-09-13 06:00 | 6127 |  |  | 0.012002
2019-09-13 07:00 | 6128 |  |  | 0.063511
2019-09-13 08:00 | 6129 |  |  | 0.23279
2019-09-13 09:00 | 6130 |  |  | 0.4194
2019-09-13 10:00 | 6131 |  |  | 0.56818
2019-09-13 11:00 | 6132 |  |  | 0.66361
2019-09-13 12:00 | 6133 |  |  | 0.69537
2019-09-13 13:00 | 6134 |  |  | 0.69528
2019-09-13 14:00 | 6135 |  |  | 0.63702
2019-09-13 15:00 | 6136 |  |  | 0.52234
2019-09-13 16:00 | 6137 |  |  | 0.36114
2019-09-13 17:00 | 6138 |  |  | 0.15619
2019-09-13 18:00 | 6139 |  |  | 0.012835
2019-09-13 19:00 | 6140 |  |  | 0
2019-09-13 20:00 | 6141 |  |  | 0
2019-09-13 21:00 | 6142 |  |  | 0
2019-09-13 22:00 | 6143 |  |  | 0
2019-09-13 23:00 | 6144 |  |  | 0
2019-09-14 | 6145 |  |  | 0
2019-09-14 01:00 | 6146 |  |  | 0
2019-09-14 02:00 | 6147 |  |  | 0
2019-09-14 03:00 | 6148 |  |  | 0
2019-09-14 04:00 | 6149 |  |  | 0
2019-09-14 05:00 | 6150 |  |  | 0
2019-09-14 06:00 | 6151 |  |  | 0.013752
2019-09-14 07:00 | 6152 |  |  | 0.072429
2019-09-14 08:00 | 6153 |  |  | 0.22329
2019-09-14 09:00 | 6154 |  |  | 0.38848
2019-09-14 10:00 | 6155 |  |  | 0.53501
2019-09-14 11:00 | 6156 |  |  | 0.64152
2019-09-14 12:00 | 6157 |  |  | 0.68553
2019-09-14 13:00 | 6158 |  |  | 0.37106
2019-09-14 14:00 | 6159 |  |  | 0.57726
2019-09-14 15:00 | 6160 |  |  | 0.29663
2019-09-14 16:00 | 6161 |  |  | 0.24121
2019-09-14 17:00 | 6162 |  |  | 0.083681
2019-09-14 18:00 | 6163 |  |  | 0.013169
2019-09-14 19:00 | 6164 |  |  | 0
2019-09-14 20:00 | 6165 |  |  | 0
2019-09-14 21:00 | 6166 |  |  | 0
2019-09-14 22:00 | 6167 |  |  | 0
2019-09-14 23:00 | 6168 |  |  | 0
2019-09-15 | 6169 |  |  | 0
2019-09-15 01:00 | 6170 |  |  | 0
2019-09-15 02:00 | 6171 |  |  | 0
2019-09-15 03:00 | 6172 |  |  | 0
2019-09-15 04:00 | 6173 |  |  | 0
2019-09-15 05:00 | 6174 |  |  | 0
2019-09-15 06:00 | 6175 |  |  | 0.012252
2019-09-15 07:00 | 6176 |  |  | 0.08268
2019-09-15 08:00 | 6177 |  |  | 0.2152
2019-09-15 09:00 | 6178 |  |  | 0.38798
2019-09-15 10:00 | 6179 |  |  | 0.52642
2019-09-15 11:00 | 6180 |  |  | 0.58301
2019-09-15 12:00 | 6181 |  |  | 0.6807
2019-09-15 13:00 | 6182 |  |  | 0.6942
2019-09-15 14:00 | 6183 |  |  | 0.63086
2019-09-15 15:00 | 6184 |  |  | 0.51959
2019-09-15 16:00 | 6185 |  |  | 0.34739
2019-09-15 17:00 | 6186 |  |  | 0.11652
2019-09-15 18:00 | 6187 |  |  | 0.0090848
2019-09-15 19:00 | 6188 |  |  | 0
2019-09-15 20:00 | 6189 |  |  | 0
2019-09-15 21:00 | 6190 |  |  | 0
2019-09-15 22:00 | 6191 |  |  | 0
2019-09-15 23:00 | 6192 |  |  | 0
2019-09-16 | 6193 |  |  | 0
2019-09-16 01:00 | 6194 |  |  | 0
2019-09-16 02:00 | 6195 |  |  | 0
2019-09-16 03:00 | 6196 |  |  | 0
2019-09-16 04:00 | 6197 |  |  | 0
2019-09-16 05:00 | 6198 |  |  | 0
2019-09-16 06:00 | 6199 |  |  | 0.013336
2019-09-16 07:00 | 6200 |  |  | 0.073179
2019-09-16 08:00 | 6201 |  |  | 0.21254
2019-09-16 09:00 | 6202 |  |  | 0.38723
2019-09-16 10:00 | 6203 |  |  | 0.52709
2019-09-16 11:00 | 6204 |  |  | 0.63452
2019-09-16 12:00 | 6205 |  |  | 0.68628
2019-09-16 13:00 | 6206 |  |  | 0.6792
2019-09-16 14:00 | 6207 |  |  | 0.60843
2019-09-16 15:00 | 6208 |  |  | 0.49517
2019-09-16 16:00 | 6209 |  |  | 0.3248
2019-09-16 17:00 | 6210 |  |  | 0.1206
2019-09-16 18:00 | 6211 |  |  | 0.009835
2019-09-16 19:00 | 6212 |  |  | 0
2019-09-16 20:00 | 6213 |  |  | 0
2019-09-16 21:00 | 6214 |  |  | 0
2019-09-16 22:00 | 6215 |  |  | 0
2019-09-16 23:00 | 6216 |  |  | 0
2019-09-17 | 6217 |  |  | 0
2019-09-17 01:00 | 6218 |  |  | 0
2019-09-17 02:00 | 6219 |  |  | 0
2019-09-17 03:00 | 6220 |  |  | 0
2019-09-17 04:00 | 6221 |  |  | 0
2019-09-17 05:00 | 6222 |  |  | 0
2019-09-17 06:00 | 6223 |  |  | 0.010835
2019-09-17 07:00 | 6224 |  |  | 0.067595
2019-09-17 08:00 | 6225 |  |  | 0.21395
2019-09-17 09:00 | 6226 |  |  | 0.39507
2019-09-17 10:00 | 6227 |  |  | 0.53876
2019-09-17 11:00 | 6228 |  |  | 0.64136
2019-09-17 12:00 | 6229 |  |  | 0.70012
2019-09-17 13:00 | 6230 |  |  | 0.68586
2019-09-17 14:00 | 6231 |  |  | 0.63194
2019-09-17 15:00 | 6232 |  |  | 0.51942
2019-09-17 16:00 | 6233 |  |  | 0.33714
2019-09-17 17:00 | 6234 |  |  | 0.12852
2019-09-17 18:00 | 6235 |  |  | 0.0085014
2019-09-17 19:00 | 6236 |  |  | 0
2019-09-17 20:00 | 6237 |  |  | 0
2019-09-17 21:00 | 6238 |  |  | 0
2019-09-17 22:00 | 6239 |  |  | 0
2019-09-17 23:00 | 6240 |  |  | 0
2019-09-18 | 6241 |  |  | 0
2019-09-18 01:00 | 6242 |  |  | 0
2019-09-18 02:00 | 6243 |  |  | 0
2019-09-18 03:00 | 6244 |  |  | 0
2019-09-18 04:00 | 6245 |  |  | 0
2019-09-18 05:00 | 6246 |  |  | 0
2019-09-18 06:00 | 6247 |  |  | 0.015003
2019-09-18 07:00 | 6248 |  |  | 0.092099
2019-09-18 08:00 | 6249 |  |  | 0.22087
2019-09-18 09:00 | 6250 |  |  | 0.44832
2019-09-18 10:00 | 6251 |  |  | 0.50833
2019-09-18 11:00 | 6252 |  |  | 0.4995
2019-09-18 12:00 | 6253 |  |  | 0.47683
2019-09-18 13:00 | 6254 |  |  | 0.38565
2019-09-18 14:00 | 6255 |  |  | 0.2262
2019-09-18 15:00 | 6256 |  |  | 0.12802
2019-09-18 16:00 | 6257 |  |  | 0.051425
2019-09-18 17:00 | 6258 |  |  | 0.016919
2019-09-18 18:00 | 6259 |  |  | 0.0010835
2019-09-18 19:00 | 6260 |  |  | 0
2019-09-18 20:00 | 6261 |  |  | 0
2019-09-18 21:00 | 6262 |  |  | 0
2019-09-18 22:00 | 6263 |  |  | 0
2019-09-18 23:00 | 6264 |  |  | 0
2019-09-19 | 6265 |  |  | 0
2019-09-19 01:00 | 6266 |  |  | 0
2019-09-19 02:00 | 6267 |  |  | 0
2019-09-19 03:00 | 6268 |  |  | 0
2019-09-19 04:00 | 6269 |  |  | 0
2019-09-19 05:00 | 6270 |  |  | 0
2019-09-19 06:00 | 6271 |  |  | 0
2019-09-19 07:00 | 6272 |  |  | 0.0067511
2019-09-19 08:00 | 6273 |  |  | 0.030588
2019-09-19 09:00 | 6274 |  |  | 0.04034
2019-09-19 10:00 | 6275 |  |  | 0.090765
2019-09-19 11:00 | 6276 |  |  | 0.0986
2019-09-19 12:00 | 6277 |  |  | 0.10502
2019-09-19 13:00 | 6278 |  |  | 0.12102
2019-09-19 14:00 | 6279 |  |  | 0.19028
2019-09-19 15:00 | 6280 |  |  | 0.13294
2019-09-19 16:00 | 6281 |  |  | 0.091932
2019-09-19 17:00 | 6282 |  |  | 0.025254
2019-09-19 18:00 | 6283 |  |  | 0.0013336
2019-09-19 19:00 | 6284 |  |  | 0
2019-09-19 20:00 | 6285 |  |  | 0
2019-09-19 21:00 | 6286 |  |  | 0
2019-09-19 22:00 | 6287 |  |  | 0
2019-09-19 23:00 | 6288 |  |  | 0
2019-09-20 | 6289 |  |  | 0
2019-09-20 01:00 | 6290 |  |  | 0
2019-09-20 02:00 | 6291 |  |  | 0
2019-09-20 03:00 | 6292 |  |  | 0
2019-09-20 04:00 | 6293 |  |  | 0
2019-09-20 05:00 | 6294 |  |  | 0
2019-09-20 06:00 | 6295 |  |  | 0.0032505
2019-09-20 07:00 | 6296 |  |  | 0.051009
2019-09-20 08:00 | 6297 |  |  | 0.17503
2019-09-20 09:00 | 6298 |  |  | 0.33789
2019-09-20 10:00 | 6299 |  |  | 0.57643
2019-09-20 11:00 | 6300 |  |  | 0.68086
2019-09-20 12:00 | 6301 |  |  | 0.6006
2019-09-20 13:00 | 6302 |  |  | 0.42799
2019-09-20 14:00 | 6303 |  |  | 0.18153
2019-09-20 15:00 | 6304 |  |  | 0.10727
2019-09-20 16:00 | 6305 |  |  | 0.047175
2019-09-20 17:00 | 6306 |  |  | 0.017503
2019-09-20 18:00 | 6307 |  |  | 0.00033339
2019-09-20 19:00 | 6308 |  |  | 0
2019-09-20 20:00 | 6309 |  |  | 0
2019-09-20 21:00 | 6310 |  |  | 0
2019-09-20 22:00 | 6311 |  |  | 0
2019-09-20 23:00 | 6312 |  |  | 0
2019-09-21 | 6313 |  |  | 0
2019-09-21 01:00 | 6314 |  |  | 0
2019-09-21 02:00 | 6315 |  |  | 0
2019-09-21 03:00 | 6316 |  |  | 0
2019-09-21 04:00 | 6317 |  |  | 0
2019-09-21 05:00 | 6318 |  |  | 0
2019-09-21 06:00 | 6319 |  |  | 0.00041674
2019-09-21 07:00 | 6320 |  |  | 0.015336
2019-09-21 08:00 | 6321 |  |  | 0.043924
2019-09-21 09:00 | 6322 |  |  | 0.13402
2019-09-21 10:00 | 6323 |  |  | 0.46049
2019-09-21 11:00 | 6324 |  |  | 0.66753
2019-09-21 12:00 | 6325 |  |  | 0.69428
2019-09-21 13:00 | 6326 |  |  | 0.43524
2019-09-21 14:00 | 6327 |  |  | 0.40432
2019-09-21 15:00 | 6328 |  |  | 0.34197
2019-09-21 16:00 | 6329 |  |  | 0.10168
2019-09-21 17:00 | 6330 |  |  | 0.036756
2019-09-21 18:00 | 6331 |  |  | 8.3347e-05
2019-09-21 19:00 | 6332 |  |  | 0
2019-09-21 20:00 | 6333 |  |  | 0
2019-09-21 21:00 | 6334 |  |  | 0
2019-09-21 22:00 | 6335 |  |  | 0
2019-09-21 23:00 | 6336 |  |  | 0
2019-09-22 | 6337 |  |  | 0
2019-09-22 01:00 | 6338 |  |  | 0
2019-09-22 02:00 | 6339 |  |  | 0
2019-09-22 03:00 | 6340 |  |  | 0
2019-09-22 04:00 | 6341 |  |  | 0
2019-09-22 05:00 | 6342 |  |  | 0
2019-09-22 06:00 | 6343 |  |  | 0.00016669
2019-09-22 07:00 | 6344 |  |  | 0.02042
2019-09-22 08:00 | 6345 |  |  | 0.059927
2019-09-22 09:00 | 6346 |  |  | 0.1747
2019-09-22 10:00 | 6347 |  |  | 0.1867
2019-09-22 11:00 | 6348 |  |  | 0.25113
2019-09-22 12:00 | 6349 |  |  | 0.19078
2019-09-22 13:00 | 6350 |  |  | 0.20312
2019-09-22 14:00 | 6351 |  |  | 0.1096
2019-09-22 15:00 | 6352 |  |  | 0.064761
2019-09-22 16:00 | 6353 |  |  | 0.040507
2019-09-22 17:00 | 6354 |  |  | 0.0055009
2019-09-22 18:00 | 6355 |  |  | 8.3347e-05
2019-09-22 19:00 | 6356 |  |  | 0
2019-09-22 20:00 | 6357 |  |  | 0
2019-09-22 21:00 | 6358 |  |  | 0
2019-09-22 22:00 | 6359 |  |  | 0
2019-09-22 23:00 | 6360 |  |  | 0
2019-09-23 | 6361 |  |  | 0
2019-09-23 01:00 | 6362 |  |  | 0
2019-09-23 02:00 | 6363 |  |  | 0
2019-09-23 03:00 | 6364 |  |  | 0
2019-09-23 04:00 | 6365 |  |  | 0
2019-09-23 05:00 | 6366 |  |  | 0
2019-09-23 06:00 | 6367 |  |  | 0.0078346
2019-09-23 07:00 | 6368 |  |  | 0.057343
2019-09-23 08:00 | 6369 |  |  | 0.21962
2019-09-23 09:00 | 6370 |  |  | 0.41565
2019-09-23 10:00 | 6371 |  |  | 0.58293
2019-09-23 11:00 | 6372 |  |  | 0.48325
2019-09-23 12:00 | 6373 |  |  | 0.65961
2019-09-23 13:00 | 6374 |  |  | 0.73362
2019-09-23 14:00 | 6375 |  |  | 0.65253
2019-09-23 15:00 | 6376 |  |  | 0.53951
2019-09-23 16:00 | 6377 |  |  | 0.34772
2019-09-23 17:00 | 6378 |  |  | 0.11852
2019-09-23 18:00 | 6379 |  |  | 0.0020003
2019-09-23 19:00 | 6380 |  |  | 0
2019-09-23 20:00 | 6381 |  |  | 0
2019-09-23 21:00 | 6382 |  |  | 0
2019-09-23 22:00 | 6383 |  |  | 0
2019-09-23 23:00 | 6384 |  |  | 0
2019-09-24 | 6385 |  |  | 0
2019-09-24 01:00 | 6386 |  |  | 0
2019-09-24 02:00 | 6387 |  |  | 0
2019-09-24 03:00 | 6388 |  |  | 0
2019-09-24 04:00 | 6389 |  |  | 0
2019-09-24 05:00 | 6390 |  |  | 0
2019-09-24 06:00 | 6391 |  |  | 0.0083347
2019-09-24 07:00 | 6392 |  |  | 0.088598
2019-09-24 08:00 | 6393 |  |  | 0.16278
2019-09-24 09:00 | 6394 |  |  | 0.22154
2019-09-24 10:00 | 6395 |  |  | 0.42532
2019-09-24 11:00 | 6396 |  |  | 0.43574
2019-09-24 12:00 | 6397 |  |  | 0.67553
2019-09-24 13:00 | 6398 |  |  | 0.63244
2019-09-24 14:00 | 6399 |  |  | 0.30347
2019-09-24 15:00 | 6400 |  |  | 0.47916
2019-09-24 16:00 | 6401 |  |  | 0.34581
2019-09-24 17:00 | 6402 |  |  | 0.09735
2019-09-24 18:00 | 6403 |  |  | 0.002167
2019-09-24 19:00 | 6404 |  |  | 0
2019-09-24 20:00 | 6405 |  |  | 0
2019-09-24 21:00 | 6406 |  |  | 0
2019-09-24 22:00 | 6407 |  |  | 0
2019-09-24 23:00 | 6408 |  |  | 0
2019-09-25 | 6409 |  |  | 0
2019-09-25 01:00 | 6410 |  |  | 0
2019-09-25 02:00 | 6411 |  |  | 0
2019-09-25 03:00 | 6412 |  |  | 0
2019-09-25 04:00 | 6413 |  |  | 0
2019-09-25 05:00 | 6414 |  |  | 0
2019-09-25 06:00 | 6415 |  |  | 0.0049175
2019-09-25 07:00 | 6416 |  |  | 0.056843
2019-09-25 08:00 | 6417 |  |  | 0.21779
2019-09-25 09:00 | 6418 |  |  | 0.40298
2019-09-25 10:00 | 6419 |  |  | 0.55693
2019-09-25 11:00 | 6420 |  |  | 0.68211
2019-09-25 12:00 | 6421 |  |  | 0.71895
2019-09-25 13:00 | 6422 |  |  | 0.66669
2019-09-25 14:00 | 6423 |  |  | 0.55918
2019-09-25 15:00 | 6424 |  |  | 0.50033
2019-09-25 16:00 | 6425 |  |  | 0.28188
2019-09-25 17:00 | 6426 |  |  | 0.087931
2019-09-25 18:00 | 6427 |  |  | 0.003834
2019-09-25 19:00 | 6428 |  |  | 0
2019-09-25 20:00 | 6429 |  |  | 0
2019-09-25 21:00 | 6430 |  |  | 0
2019-09-25 22:00 | 6431 |  |  | 0
2019-09-25 23:00 | 6432 |  |  | 0
2019-09-26 | 6433 |  |  | 0
2019-09-26 01:00 | 6434 |  |  | 0
2019-09-26 02:00 | 6435 |  |  | 0
2019-09-26 03:00 | 6436 |  |  | 0
2019-09-26 04:00 | 6437 |  |  | 0
2019-09-26 05:00 | 6438 |  |  | 0
2019-09-26 06:00 | 6439 |  |  | 0.0078346
2019-09-26 07:00 | 6440 |  |  | 0.041174
2019-09-26 08:00 | 6441 |  |  | 0.13852
2019-09-26 09:00 | 6442 |  |  | 0.31089
2019-09-26 10:00 | 6443 |  |  | 0.4044
2019-09-26 11:00 | 6444 |  |  | 0.57976
2019-09-26 12:00 | 6445 |  |  | 0.55551
2019-09-26 13:00 | 6446 |  |  | 0.39615
2019-09-26 14:00 | 6447 |  |  | 0.51009
2019-09-26 15:00 | 6448 |  |  | 0.35614
2019-09-26 16:00 | 6449 |  |  | 0.085681
2019-09-26 17:00 | 6450 |  |  | 0.049925
2019-09-26 18:00 | 6451 |  |  | 0.0020003
2019-09-26 19:00 | 6452 |  |  | 0
2019-09-26 20:00 | 6453 |  |  | 0
2019-09-26 21:00 | 6454 |  |  | 0
2019-09-26 22:00 | 6455 |  |  | 0
2019-09-26 23:00 | 6456 |  |  | 0
2019-09-27 | 6457 |  |  | 0
2019-09-27 01:00 | 6458 |  |  | 0
2019-09-27 02:00 | 6459 |  |  | 0
2019-09-27 03:00 | 6460 |  |  | 0
2019-09-27 04:00 | 6461 |  |  | 0
2019-09-27 05:00 | 6462 |  |  | 0
2019-09-27 06:00 | 6463 |  |  | 0.0034172
2019-09-27 07:00 | 6464 |  |  | 0.033006
2019-09-27 08:00 | 6465 |  |  | 0.099933
2019-09-27 09:00 | 6466 |  |  | 0.17461
2019-09-27 10:00 | 6467 |  |  | 0.3889
2019-09-27 11:00 | 6468 |  |  | 0.38023
2019-09-27 12:00 | 6469 |  |  | 0.42432
2019-09-27 13:00 | 6470 |  |  | 0.29072
2019-09-27 14:00 | 6471 |  |  | 0.27963
2019-09-27 15:00 | 6472 |  |  | 0.13019
2019-09-27 16:00 | 6473 |  |  | 0.13769
2019-09-27 17:00 | 6474 |  |  | 0.013502
2019-09-27 18:00 | 6475 |  |  | 0
2019-09-27 19:00 | 6476 |  |  | 0
2019-09-27 20:00 | 6477 |  |  | 0
2019-09-27 21:00 | 6478 |  |  | 0
2019-09-27 22:00 | 6479 |  |  | 0
2019-09-27 23:00 | 6480 |  |  | 0
2019-09-28 | 6481 |  |  | 0
2019-09-28 01:00 | 6482 |  |  | 0
2019-09-28 02:00 | 6483 |  |  | 0
2019-09-28 03:00 | 6484 |  |  | 0
2019-09-28 04:00 | 6485 |  |  | 0
2019-09-28 05:00 | 6486 |  |  | 0
2019-09-28 06:00 | 6487 |  |  | 0.0067511
2019-09-28 07:00 | 6488 |  |  | 0.077763
2019-09-28 08:00 | 6489 |  |  | 0.15603
2019-09-28 09:00 | 6490 |  |  | 0.3158
2019-09-28 10:00 | 6491 |  |  | 0.3929
2019-09-28 11:00 | 6492 |  |  | 0.55168
2019-09-28 12:00 | 6493 |  |  | 0.48583
2019-09-28 13:00 | 6494 |  |  | 0.44516
2019-09-28 14:00 | 6495 |  |  | 0.52217
2019-09-28 15:00 | 6496 |  |  | 0.38465
2019-09-28 16:00 | 6497 |  |  | 0.2132
2019-09-28 17:00 | 6498 |  |  | 0.089182
2019-09-28 18:00 | 6499 |  |  | 0.0016669
2019-09-28 19:00 | 6500 |  |  | 0
2019-09-28 20:00 | 6501 |  |  | 0
2019-09-28 21:00 | 6502 |  |  | 0
2019-09-28 22:00 | 6503 |  |  | 0
2019-09-28 23:00 | 6504 |  |  | 0
2019-09-29 | 6505 |  |  | 0
2019-09-29 01:00 | 6506 |  |  | 0
2019-09-29 02:00 | 6507 |  |  | 0
2019-09-29 03:00 | 6508 |  |  | 0
2019-09-29 04:00 | 6509 |  |  | 0
2019-09-29 05:00 | 6510 |  |  | 0
2019-09-29 06:00 | 6511 |  |  | 0.003834
2019-09-29 07:00 | 6512 |  |  | 0.053176
2019-09-29 08:00 | 6513 |  |  | 0.18703
2019-09-29 09:00 | 6514 |  |  | 0.34031
2019-09-29 10:00 | 6515 |  |  | 0.52425
2019-09-29 11:00 | 6516 |  |  | 0.50792
2019-09-29 12:00 | 6517 |  |  | 0.24879
2019-09-29 13:00 | 6518 |  |  | 0.4064
2019-09-29 14:00 | 6519 |  |  | 0.27146
2019-09-29 15:00 | 6520 |  |  | 0.18961
2019-09-29 16:00 | 6521 |  |  | 0.071512
2019-09-29 17:00 | 6522 |  |  | 0.015753
2019-09-29 18:00 | 6523 |  |  | 0.00025004
2019-09-29 19:00 | 6524 |  |  | 0
2019-09-29 20:00 | 6525 |  |  | 0
2019-09-29 21:00 | 6526 |  |  | 0
2019-09-29 22:00 | 6527 |  |  | 0
2019-09-29 23:00 | 6528 |  |  | 0
2019-09-30 | 6529 |  |  | 0
2019-09-30 01:00 | 6530 |  |  | 0
2019-09-30 02:00 | 6531 |  |  | 0
2019-09-30 03:00 | 6532 |  |  | 0
2019-09-30 04:00 | 6533 |  |  | 0
2019-09-30 05:00 | 6534 |  |  | 0
2019-09-30 06:00 | 6535 |  |  | 0.0086681
2019-09-30 07:00 | 6536 |  |  | 0.073929
2019-09-30 08:00 | 6537 |  |  | 0.20953
2019-09-30 09:00 | 6538 |  |  | 0.38731
2019-09-30 10:00 | 6539 |  |  | 0.51609
2019-09-30 11:00 | 6540 |  |  | 0.64352
2019-09-30 12:00 | 6541 |  |  | 0.67178
2019-09-30 13:00 | 6542 |  |  | 0.65978
2019-09-30 14:00 | 6543 |  |  | 0.58443
2019-09-30 15:00 | 6544 |  |  | 0.48633
2019-09-30 16:00 | 6545 |  |  | 0.29163
2019-09-30 17:00 | 6546 |  |  | 0.082597
2019-09-30 18:00 | 6547 |  |  | 0.00050008
2019-09-30 19:00 | 6548 |  |  | 0
2019-09-30 20:00 | 6549 |  |  | 0
2019-09-30 21:00 | 6550 |  |  | 0
2019-09-30 22:00 | 6551 |  |  | 0
2019-09-30 23:00 | 6552 |  |  | 0
2019-10-01 | 6553 |  |  | 0
2019-10-01 01:00 | 6554 |  |  | 0
2019-10-01 02:00 | 6555 |  |  | 0
2019-10-01 03:00 | 6556 |  |  | 0
2019-10-01 04:00 | 6557 |  |  | 0
2019-10-01 05:00 | 6558 |  |  | 0
2019-10-01 06:00 | 6559 |  |  | 0.0050842
2019-10-01 07:00 | 6560 |  |  | 0.054842
2019-10-01 08:00 | 6561 |  |  | 0.16769
2019-10-01 09:00 | 6562 |  |  | 0.36139
2019-10-01 10:00 | 6563 |  |  | 0.43224
2019-10-01 11:00 | 6564 |  |  | 0.57176
2019-10-01 12:00 | 6565 |  |  | 0.36198
2019-10-01 13:00 | 6566 |  |  | 0.40248
2019-10-01 14:00 | 6567 |  |  | 0.13794
2019-10-01 15:00 | 6568 |  |  | 0.056676
2019-10-01 16:00 | 6569 |  |  | 0.028588
2019-10-01 17:00 | 6570 |  |  | 0.0033339
2019-10-01 18:00 | 6571 |  |  | 0
2019-10-01 19:00 | 6572 |  |  | 0
2019-10-01 20:00 | 6573 |  |  | 0
2019-10-01 21:00 | 6574 |  |  | 0
2019-10-01 22:00 | 6575 |  |  | 0
2019-10-01 23:00 | 6576 |  |  | 0
2019-10-02 | 6577 |  |  | 0
2019-10-02 01:00 | 6578 |  |  | 0
2019-10-02 02:00 | 6579 |  |  | 0
2019-10-02 03:00 | 6580 |  |  | 0
2019-10-02 04:00 | 6581 |  |  | 0
2019-10-02 05:00 | 6582 |  |  | 0
2019-10-02 06:00 | 6583 |  |  | 0.0030838
2019-10-02 07:00 | 6584 |  |  | 0.051092
2019-10-02 08:00 | 6585 |  |  | 0.14952
2019-10-02 09:00 | 6586 |  |  | 0.41924
2019-10-02 10:00 | 6587 |  |  | 0.57368
2019-10-02 11:00 | 6588 |  |  | 0.67003
2019-10-02 12:00 | 6589 |  |  | 0.69912
2019-10-02 13:00 | 6590 |  |  | 0.69595
2019-10-02 14:00 | 6591 |  |  | 0.63819
2019-10-02 15:00 | 6592 |  |  | 0.49875
2019-10-02 16:00 | 6593 |  |  | 0.29597
2019-10-02 17:00 | 6594 |  |  | 0.077596
2019-10-02 18:00 | 6595 |  |  | 0.00033339
2019-10-02 19:00 | 6596 |  |  | 0
2019-10-02 20:00 | 6597 |  |  | 0
2019-10-02 21:00 | 6598 |  |  | 0
2019-10-02 22:00 | 6599 |  |  | 0
2019-10-02 23:00 | 6600 |  |  | 0
2019-10-03 | 6601 |  |  | 0
2019-10-03 01:00 | 6602 |  |  | 0
2019-10-03 02:00 | 6603 |  |  | 0
2019-10-03 03:00 | 6604 |  |  | 0
2019-10-03 04:00 | 6605 |  |  | 0
2019-10-03 05:00 | 6606 |  |  | 0
2019-10-03 06:00 | 6607 |  |  | 0.0033339
2019-10-03 07:00 | 6608 |  |  | 0.048258
2019-10-03 08:00 | 6609 |  |  | 0.22895
2019-10-03 09:00 | 6610 |  |  | 0.44241
2019-10-03 10:00 | 6611 |  |  | 0.60393
2019-10-03 11:00 | 6612 |  |  | 0.69403
2019-10-03 12:00 | 6613 |  |  | 0.75496
2019-10-03 13:00 | 6614 |  |  | 0.74696
2019-10-03 14:00 | 6615 |  |  | 0.6752
2019-10-03 15:00 | 6616 |  |  | 0.53609
2019-10-03 16:00 | 6617 |  |  | 0.26604
2019-10-03 17:00 | 6618 |  |  | 0.041924
2019-10-03 18:00 | 6619 |  |  | 8.3347e-05
2019-10-03 19:00 | 6620 |  |  | 0
2019-10-03 20:00 | 6621 |  |  | 0
2019-10-03 21:00 | 6622 |  |  | 0
2019-10-03 22:00 | 6623 |  |  | 0
2019-10-03 23:00 | 6624 |  |  | 0
2019-10-04 | 6625 |  |  | 0
2019-10-04 01:00 | 6626 |  |  | 0
2019-10-04 02:00 | 6627 |  |  | 0
2019-10-04 03:00 | 6628 |  |  | 0
2019-10-04 04:00 | 6629 |  |  | 0
2019-10-04 05:00 | 6630 |  |  | 0
2019-10-04 06:00 | 6631 |  |  | 0.0031672
2019-10-04 07:00 | 6632 |  |  | 0.052175
2019-10-04 08:00 | 6633 |  |  | 0.21679
2019-10-04 09:00 | 6634 |  |  | 0.42074
2019-10-04 10:00 | 6635 |  |  | 0.56201
2019-10-04 11:00 | 6636 |  |  | 0.66394
2019-10-04 12:00 | 6637 |  |  | 0.73354
2019-10-04 13:00 | 6638 |  |  | 0.69362
2019-10-04 14:00 | 6639 |  |  | 0.54526
2019-10-04 15:00 | 6640 |  |  | 0.4925
2019-10-04 16:00 | 6641 |  |  | 0.26479
2019-10-04 17:00 | 6642 |  |  | 0.052175
2019-10-04 18:00 | 6643 |  |  | 8.3347e-05
2019-10-04 19:00 | 6644 |  |  | 0
2019-10-04 20:00 | 6645 |  |  | 0
2019-10-04 21:00 | 6646 |  |  | 0
2019-10-04 22:00 | 6647 |  |  | 0
2019-10-04 23:00 | 6648 |  |  | 0
2019-10-05 | 6649 |  |  | 0
2019-10-05 01:00 | 6650 |  |  | 0
2019-10-05 02:00 | 6651 |  |  | 0
2019-10-05 03:00 | 6652 |  |  | 0
2019-10-05 04:00 | 6653 |  |  | 0
2019-10-05 05:00 | 6654 |  |  | 0
2019-10-05 06:00 | 6655 |  |  | 0.0030838
2019-10-05 07:00 | 6656 |  |  | 0.047425
2019-10-05 08:00 | 6657 |  |  | 0.21387
2019-10-05 09:00 | 6658 |  |  | 0.41574
2019-10-05 10:00 | 6659 |  |  | 0.5726
2019-10-05 11:00 | 6660 |  |  | 0.65311
2019-10-05 12:00 | 6661 |  |  | 0.54209
2019-10-05 13:00 | 6662 |  |  | 0.70203
2019-10-05 14:00 | 6663 |  |  | 0.56459
2019-10-05 15:00 | 6664 |  |  | 0.4254
2019-10-05 16:00 | 6665 |  |  | 0.24296
2019-10-05 17:00 | 6666 |  |  | 0.05776
2019-10-05 18:00 | 6667 |  |  | 8.3347e-05
2019-10-05 19:00 | 6668 |  |  | 0
2019-10-05 20:00 | 6669 |  |  | 0
2019-10-05 21:00 | 6670 |  |  | 0
2019-10-05 22:00 | 6671 |  |  | 0
2019-10-05 23:00 | 6672 |  |  | 0
2019-10-06 | 6673 |  |  | 0
2019-10-06 01:00 | 6674 |  |  | 0
2019-10-06 02:00 | 6675 |  |  | 0
2019-10-06 03:00 | 6676 |  |  | 0
2019-10-06 04:00 | 6677 |  |  | 0
2019-10-06 05:00 | 6678 |  |  | 0
2019-10-06 06:00 | 6679 |  |  | 0.0047508
2019-10-06 07:00 | 6680 |  |  | 0.065011
2019-10-06 08:00 | 6681 |  |  | 0.1717
2019-10-06 09:00 | 6682 |  |  | 0.30722
2019-10-06 10:00 | 6683 |  |  | 0.44741
2019-10-06 11:00 | 6684 |  |  | 0.28346
2019-10-06 12:00 | 6685 |  |  | 0.42674
2019-10-06 13:00 | 6686 |  |  | 0.40373
2019-10-06 14:00 | 6687 |  |  | 0.21454
2019-10-06 15:00 | 6688 |  |  | 0.16494
2019-10-06 16:00 | 6689 |  |  | 0.069512
2019-10-06 17:00 | 6690 |  |  | 0.010585
2019-10-06 18:00 | 6691 |  |  | 0
2019-10-06 19:00 | 6692 |  |  | 0
2019-10-06 20:00 | 6693 |  |  | 0
2019-10-06 21:00 | 6694 |  |  | 0
2019-10-06 22:00 | 6695 |  |  | 0
2019-10-06 23:00 | 6696 |  |  | 0
2019-10-07 | 6697 |  |  | 0
2019-10-07 01:00 | 6698 |  |  | 0
2019-10-07 02:00 | 6699 |  |  | 0
2019-10-07 03:00 | 6700 |  |  | 0
2019-10-07 04:00 | 6701 |  |  | 0
2019-10-07 05:00 | 6702 |  |  | 0
2019-10-07 06:00 | 6703 |  |  | 0.0017503
2019-10-07 07:00 | 6704 |  |  | 0.048341
2019-10-07 08:00 | 6705 |  |  | 0.2057
2019-10-07 09:00 | 6706 |  |  | 0.4084
2019-10-07 10:00 | 6707 |  |  | 0.57526
2019-10-07 11:00 | 6708 |  |  | 0.67136
2019-10-07 12:00 | 6709 |  |  | 0.71854
2019-10-07 13:00 | 6710 |  |  | 0.7152
2019-10-07 14:00 | 6711 |  |  | 0.64711
2019-10-07 15:00 | 6712 |  |  | 0.47616
2019-10-07 16:00 | 6713 |  |  | 0.26721
2019-10-07 17:00 | 6714 |  |  | 0.047925
2019-10-07 18:00 | 6715 |  |  | 0
2019-10-07 19:00 | 6716 |  |  | 0
2019-10-07 20:00 | 6717 |  |  | 0
2019-10-07 21:00 | 6718 |  |  | 0
2019-10-07 22:00 | 6719 |  |  | 0
2019-10-07 23:00 | 6720 |  |  | 0
2019-10-08 | 6721 |  |  | 0
2019-10-08 01:00 | 6722 |  |  | 0
2019-10-08 02:00 | 6723 |  |  | 0
2019-10-08 03:00 | 6724 |  |  | 0
2019-10-08 04:00 | 6725 |  |  | 0
2019-10-08 05:00 | 6726 |  |  | 0
2019-10-08 06:00 | 6727 |  |  | 0.0024171
2019-10-08 07:00 | 6728 |  |  | 0.044674
2019-10-08 08:00 | 6729 |  |  | 0.19912
2019-10-08 09:00 | 6730 |  |  | 0.39498
2019-10-08 10:00 | 6731 |  |  | 0.54184
2019-10-08 11:00 | 6732 |  |  | 0.65144
2019-10-08 12:00 | 6733 |  |  | 0.64461
2019-10-08 13:00 | 6734 |  |  | 0.64911
2019-10-08 14:00 | 6735 |  |  | 0.15869
2019-10-08 15:00 | 6736 |  |  | 0.25963
2019-10-08 16:00 | 6737 |  |  | 0.075929
2019-10-08 17:00 | 6738 |  |  | 0.015919
2019-10-08 18:00 | 6739 |  |  | 0
2019-10-08 19:00 | 6740 |  |  | 0
2019-10-08 20:00 | 6741 |  |  | 0
2019-10-08 21:00 | 6742 |  |  | 0
2019-10-08 22:00 | 6743 |  |  | 0
2019-10-08 23:00 | 6744 |  |  | 0
2019-10-09 | 6745 |  |  | 0
2019-10-09 01:00 | 6746 |  |  | 0
2019-10-09 02:00 | 6747 |  |  | 0
2019-10-09 03:00 | 6748 |  |  | 0
2019-10-09 04:00 | 6749 |  |  | 0
2019-10-09 05:00 | 6750 |  |  | 0
2019-10-09 06:00 | 6751 |  |  | 8.3347e-05
2019-10-09 07:00 | 6752 |  |  | 0.012252
2019-10-09 08:00 | 6753 |  |  | 0.030838
2019-10-09 09:00 | 6754 |  |  | 0.052009
2019-10-09 10:00 | 6755 |  |  | 0.083847
2019-10-09 11:00 | 6756 |  |  | 0.12952
2019-10-09 12:00 | 6757 |  |  | 0.10068
2019-10-09 13:00 | 6758 |  |  | 0.084681
2019-10-09 14:00 | 6759 |  |  | 0.061927
2019-10-09 15:00 | 6760 |  |  | 0.10868
2019-10-09 16:00 | 6761 |  |  | 0.093016
2019-10-09 17:00 | 6762 |  |  | 0.0027505
2019-10-09 18:00 | 6763 |  |  | 0
2019-10-09 19:00 | 6764 |  |  | 0
2019-10-09 20:00 | 6765 |  |  | 0
2019-10-09 21:00 | 6766 |  |  | 0
2019-10-09 22:00 | 6767 |  |  | 0
2019-10-09 23:00 | 6768 |  |  | 0
2019-10-10 | 6769 |  |  | 0
2019-10-10 01:00 | 6770 |  |  | 0
2019-10-10 02:00 | 6771 |  |  | 0
2019-10-10 03:00 | 6772 |  |  | 0
2019-10-10 04:00 | 6773 |  |  | 0
2019-10-10 05:00 | 6774 |  |  | 0
2019-10-10 06:00 | 6775 |  |  | 0.00016669
2019-10-10 07:00 | 6776 |  |  | 0.028171
2019-10-10 08:00 | 6777 |  |  | 0.072512
2019-10-10 09:00 | 6778 |  |  | 0.13402
2019-10-10 10:00 | 6779 |  |  | 0.2292
2019-10-10 11:00 | 6780 |  |  | 0.64561
2019-10-10 12:00 | 6781 |  |  | 0.66369
2019-10-10 13:00 | 6782 |  |  | 0.61135
2019-10-10 14:00 | 6783 |  |  | 0.50092
2019-10-10 15:00 | 6784 |  |  | 0.4059
2019-10-10 16:00 | 6785 |  |  | 0.21512
2019-10-10 17:00 | 6786 |  |  | 0.031839
2019-10-10 18:00 | 6787 |  |  | 0
2019-10-10 19:00 | 6788 |  |  | 0
2019-10-10 20:00 | 6789 |  |  | 0
2019-10-10 21:00 | 6790 |  |  | 0
2019-10-10 22:00 | 6791 |  |  | 0
2019-10-10 23:00 | 6792 |  |  | 0
2019-10-11 | 6793 |  |  | 0
2019-10-11 01:00 | 6794 |  |  | 0
2019-10-11 02:00 | 6795 |  |  | 0
2019-10-11 03:00 | 6796 |  |  | 0
2019-10-11 04:00 | 6797 |  |  | 0
2019-10-11 05:00 | 6798 |  |  | 0
2019-10-11 06:00 | 6799 |  |  | 0.0016669
2019-10-11 07:00 | 6800 |  |  | 0.051009
2019-10-11 08:00 | 6801 |  |  | 0.16661
2019-10-11 09:00 | 6802 |  |  | 0.29422
2019-10-11 10:00 | 6803 |  |  | 0.4755
2019-10-11 11:00 | 6804 |  |  | 0.59268
2019-10-11 12:00 | 6805 |  |  | 0.61019
2019-10-11 13:00 | 6806 |  |  | 0.52892
2019-10-11 14:00 | 6807 |  |  | 0.57026
2019-10-11 15:00 | 6808 |  |  | 0.20828
2019-10-11 16:00 | 6809 |  |  | 0.096766
2019-10-11 17:00 | 6810 |  |  | 0.014252
2019-10-11 18:00 | 6811 |  |  | 0
2019-10-11 19:00 | 6812 |  |  | 0
2019-10-11 20:00 | 6813 |  |  | 0
2019-10-11 21:00 | 6814 |  |  | 0
2019-10-11 22:00 | 6815 |  |  | 0
2019-10-11 23:00 | 6816 |  |  | 0
2019-10-12 | 6817 |  |  | 0
2019-10-12 01:00 | 6818 |  |  | 0
2019-10-12 02:00 | 6819 |  |  | 0
2019-10-12 03:00 | 6820 |  |  | 0
2019-10-12 04:00 | 6821 |  |  | 0
2019-10-12 05:00 | 6822 |  |  | 0
2019-10-12 06:00 | 6823 |  |  | 0.0016669
2019-10-12 07:00 | 6824 |  |  | 0.059343
2019-10-12 08:00 | 6825 |  |  | 0.16444
2019-10-12 09:00 | 6826 |  |  | 0.33781
2019-10-12 10:00 | 6827 |  |  | 0.44491
2019-10-12 11:00 | 6828 |  |  | 0.3924
2019-10-12 12:00 | 6829 |  |  | 0.48075
2019-10-12 13:00 | 6830 |  |  | 0.34972
2019-10-12 14:00 | 6831 |  |  | 0.43007
2019-10-12 15:00 | 6832 |  |  | 0.30697
2019-10-12 16:00 | 6833 |  |  | 0.13711
2019-10-12 17:00 | 6834 |  |  | 0.020003
2019-10-12 18:00 | 6835 |  |  | 0
2019-10-12 19:00 | 6836 |  |  | 0
2019-10-12 20:00 | 6837 |  |  | 0
2019-10-12 21:00 | 6838 |  |  | 0
2019-10-12 22:00 | 6839 |  |  | 0
2019-10-12 23:00 | 6840 |  |  | 0
2019-10-13 | 6841 |  |  | 0
2019-10-13 01:00 | 6842 |  |  | 0
2019-10-13 02:00 | 6843 |  |  | 0
2019-10-13 03:00 | 6844 |  |  | 0
2019-10-13 04:00 | 6845 |  |  | 0
2019-10-13 05:00 | 6846 |  |  | 0
2019-10-13 06:00 | 6847 |  |  | 0.00033339
2019-10-13 07:00 | 6848 |  |  | 0.052342
2019-10-13 08:00 | 6849 |  |  | 0.13777
2019-10-13 09:00 | 6850 |  |  | 0.31122
2019-10-13 10:00 | 6851 |  |  | 0.44191
2019-10-13 11:00 | 6852 |  |  | 0.36739
2019-10-13 12:00 | 6853 |  |  | 0.56551
2019-10-13 13:00 | 6854 |  |  | 0.57893
2019-10-13 14:00 | 6855 |  |  | 0.4244
2019-10-13 15:00 | 6856 |  |  | 0.1852
2019-10-13 16:00 | 6857 |  |  | 0.13744
2019-10-13 17:00 | 6858 |  |  | 0.017003
2019-10-13 18:00 | 6859 |  |  | 0
2019-10-13 19:00 | 6860 |  |  | 0
2019-10-13 20:00 | 6861 |  |  | 0
2019-10-13 21:00 | 6862 |  |  | 0
2019-10-13 22:00 | 6863 |  |  | 0
2019-10-13 23:00 | 6864 |  |  | 0
2019-10-14 | 6865 |  |  | 0
2019-10-14 01:00 | 6866 |  |  | 0
2019-10-14 02:00 | 6867 |  |  | 0
2019-10-14 03:00 | 6868 |  |  | 0
2019-10-14 04:00 | 6869 |  |  | 0
2019-10-14 05:00 | 6870 |  |  | 0
2019-10-14 06:00 | 6871 |  |  | 8.3347e-05
2019-10-14 07:00 | 6872 |  |  | 0.018503
2019-10-14 08:00 | 6873 |  |  | 0.050092
2019-10-14 09:00 | 6874 |  |  | 0.093932
2019-10-14 10:00 | 6875 |  |  | 0.12794
2019-10-14 11:00 | 6876 |  |  | 0.17836
2019-10-14 12:00 | 6877 |  |  | 0.17045
2019-10-14 13:00 | 6878 |  |  | 0.18636
2019-10-14 14:00 | 6879 |  |  | 0.35789
2019-10-14 15:00 | 6880 |  |  | 0.19828
2019-10-14 16:00 | 6881 |  |  | 0.069262
2019-10-14 17:00 | 6882 |  |  | 0.0031672
2019-10-14 18:00 | 6883 |  |  | 0
2019-10-14 19:00 | 6884 |  |  | 0
2019-10-14 20:00 | 6885 |  |  | 0
2019-10-14 21:00 | 6886 |  |  | 0
2019-10-14 22:00 | 6887 |  |  | 0
2019-10-14 23:00 | 6888 |  |  | 0
2019-10-15 | 6889 |  |  | 0
2019-10-15 01:00 | 6890 |  |  | 0
2019-10-15 02:00 | 6891 |  |  | 0
2019-10-15 03:00 | 6892 |  |  | 0
2019-10-15 04:00 | 6893 |  |  | 0
2019-10-15 05:00 | 6894 |  |  | 0
2019-10-15 06:00 | 6895 |  |  | 0
2019-10-15 07:00 | 6896 |  |  | 0
2019-10-15 08:00 | 6897 |  |  | 0
2019-10-15 09:00 | 6898 |  |  | 0.013752
2019-10-15 10:00 | 6899 |  |  | 0.026671
2019-10-15 11:00 | 6900 |  |  | 0.013336
2019-10-15 12:00 | 6901 |  |  | 0.036089
2019-10-15 13:00 | 6902 |  |  | 0.071845
2019-10-15 14:00 | 6903 |  |  | 0.28071
2019-10-15 15:00 | 6904 |  |  | 0.14361
2019-10-15 16:00 | 6905 |  |  | 0.083264
2019-10-15 17:00 | 6906 |  |  | 0.02142
2019-10-15 18:00 | 6907 |  |  | 0
2019-10-15 19:00 | 6908 |  |  | 0
2019-10-15 20:00 | 6909 |  |  | 0
2019-10-15 21:00 | 6910 |  |  | 0
2019-10-15 22:00 | 6911 |  |  | 0
2019-10-15 23:00 | 6912 |  |  | 0
2019-10-16 | 6913 |  |  | 0
2019-10-16 01:00 | 6914 |  |  | 0
2019-10-16 02:00 | 6915 |  |  | 0
2019-10-16 03:00 | 6916 |  |  | 0
2019-10-16 04:00 | 6917 |  |  | 0
2019-10-16 05:00 | 6918 |  |  | 0
2019-10-16 06:00 | 6919 |  |  | 0.0010002
2019-10-16 07:00 | 6920 |  |  | 0.054009
2019-10-16 08:00 | 6921 |  |  | 0.15353
2019-10-16 09:00 | 6922 |  |  | 0.39257
2019-10-16 10:00 | 6923 |  |  | 0.54434
2019-10-16 11:00 | 6924 |  |  | 0.63236
2019-10-16 12:00 | 6925 |  |  | 0.69337
2019-10-16 13:00 | 6926 |  |  | 0.68878
2019-10-16 14:00 | 6927 |  |  | 0.58501
2019-10-16 15:00 | 6928 |  |  | 0.40982
2019-10-16 16:00 | 6929 |  |  | 0.19137
2019-10-16 17:00 | 6930 |  |  | 0.012419
2019-10-16 18:00 | 6931 |  |  | 0
2019-10-16 19:00 | 6932 |  |  | 0
2019-10-16 20:00 | 6933 |  |  | 0
2019-10-16 21:00 | 6934 |  |  | 0
2019-10-16 22:00 | 6935 |  |  | 0
2019-10-16 23:00 | 6936 |  |  | 0
2019-10-17 | 6937 |  |  | 0
2019-10-17 01:00 | 6938 |  |  | 0
2019-10-17 02:00 | 6939 |  |  | 0
2019-10-17 03:00 | 6940 |  |  | 0
2019-10-17 04:00 | 6941 |  |  | 0
2019-10-17 05:00 | 6942 |  |  | 0
2019-10-17 06:00 | 6943 |  |  | 0.00075013
2019-10-17 07:00 | 6944 |  |  | 0.04159
2019-10-17 08:00 | 6945 |  |  | 0.18053
2019-10-17 09:00 | 6946 |  |  | 0.36214
2019-10-17 10:00 | 6947 |  |  | 0.43124
2019-10-17 11:00 | 6948 |  |  | 0.43282
2019-10-17 12:00 | 6949 |  |  | 0.6161
2019-10-17 13:00 | 6950 |  |  | 0.63402
2019-10-17 14:00 | 6951 |  |  | 0.53392
2019-10-17 15:00 | 6952 |  |  | 0.098766
2019-10-17 16:00 | 6953 |  |  | 0.0032505
2019-10-17 17:00 | 6954 |  |  | 0
2019-10-17 18:00 | 6955 |  |  | 0
2019-10-17 19:00 | 6956 |  |  | 0
2019-10-17 20:00 | 6957 |  |  | 0
2019-10-17 21:00 | 6958 |  |  | 0
2019-10-17 22:00 | 6959 |  |  | 0
2019-10-17 23:00 | 6960 |  |  | 0
2019-10-18 | 6961 |  |  | 0
2019-10-18 01:00 | 6962 |  |  | 0
2019-10-18 02:00 | 6963 |  |  | 0
2019-10-18 03:00 | 6964 |  |  | 0
2019-10-18 04:00 | 6965 |  |  | 0
2019-10-18 05:00 | 6966 |  |  | 0
2019-10-18 06:00 | 6967 |  |  | 0
2019-10-18 07:00 | 6968 |  |  | 0.0056676
2019-10-18 08:00 | 6969 |  |  | 0.030255
2019-10-18 09:00 | 6970 |  |  | 0.05701
2019-10-18 10:00 | 6971 |  |  | 0.080263
2019-10-18 11:00 | 6972 |  |  | 0.15644
2019-10-18 12:00 | 6973 |  |  | 0.20312
2019-10-18 13:00 | 6974 |  |  | 0.3123
2019-10-18 14:00 | 6975 |  |  | 0.20345
2019-10-18 15:00 | 6976 |  |  | 0.1051
2019-10-18 16:00 | 6977 |  |  | 0.038256
2019-10-18 17:00 | 6978 |  |  | 0.0025004
2019-10-18 18:00 | 6979 |  |  | 0
2019-10-18 19:00 | 6980 |  |  | 0
2019-10-18 20:00 | 6981 |  |  | 0
2019-10-18 21:00 | 6982 |  |  | 0
2019-10-18 22:00 | 6983 |  |  | 0
2019-10-18 23:00 | 6984 |  |  | 0
2019-10-19 | 6985 |  |  | 0
2019-10-19 01:00 | 6986 |  |  | 0
2019-10-19 02:00 | 6987 |  |  | 0
2019-10-19 03:00 | 6988 |  |  | 0
2019-10-19 04:00 | 6989 |  |  | 0
2019-10-19 05:00 | 6990 |  |  | 0
2019-10-19 06:00 | 6991 |  |  | 0
2019-10-19 07:00 | 6992 |  |  | 0.00075013
2019-10-19 08:00 | 6993 |  |  | 0.014002
2019-10-19 09:00 | 6994 |  |  | 0.083097
2019-10-19 10:00 | 6995 |  |  | 0.10268
2019-10-19 11:00 | 6996 |  |  | 0.063844
2019-10-19 12:00 | 6997 |  |  | 0.1111
2019-10-19 13:00 | 6998 |  |  | 0.070428
2019-10-19 14:00 | 6999 |  |  | 0.024254
2019-10-19 15:00 | 7000 |  |  | 0.017836
2019-10-19 16:00 | 7001 |  |  | 0.0073346
2019-10-19 17:00 | 7002 |  |  | 0
2019-10-19 18:00 | 7003 |  |  | 0
2019-10-19 19:00 | 7004 |  |  | 0
2019-10-19 20:00 | 7005 |  |  | 0
2019-10-19 21:00 | 7006 |  |  | 0
2019-10-19 22:00 | 7007 |  |  | 0
2019-10-19 23:00 | 7008 |  |  | 0
2019-10-20 | 7009 |  |  | 0
2019-10-20 01:00 | 7010 |  |  | 0
2019-10-20 02:00 | 7011 |  |  | 0
2019-10-20 03:00 | 7012 |  |  | 0
2019-10-20 04:00 | 7013 |  |  | 0
2019-10-20 05:00 | 7014 |  |  | 0
2019-10-20 06:00 | 7015 |  |  | 0
2019-10-20 07:00 | 7016 |  |  | 0.00066678
2019-10-20 08:00 | 7017 |  |  | 0.0063344
2019-10-20 09:00 | 7018 |  |  | 0.021837
2019-10-20 10:00 | 7019 |  |  | 0.031255
2019-10-20 11:00 | 7020 |  |  | 0.031339
2019-10-20 12:00 | 7021 |  |  | 0.01967
2019-10-20 13:00 | 7022 |  |  | 0.036173
2019-10-20 14:00 | 7023 |  |  | 0.023671
2019-10-20 15:00 | 7024 |  |  | 0.014502
2019-10-20 16:00 | 7025 |  |  | 0.0077513
2019-10-20 17:00 | 7026 |  |  | 8.3347e-05
2019-10-20 18:00 | 7027 |  |  | 0
2019-10-20 19:00 | 7028 |  |  | 0
2019-10-20 20:00 | 7029 |  |  | 0
2019-10-20 21:00 | 7030 |  |  | 0
2019-10-20 22:00 | 7031 |  |  | 0
2019-10-20 23:00 | 7032 |  |  | 0
2019-10-21 | 7033 |  |  | 0
2019-10-21 01:00 | 7034 |  |  | 0
2019-10-21 02:00 | 7035 |  |  | 0
2019-10-21 03:00 | 7036 |  |  | 0
2019-10-21 04:00 | 7037 |  |  | 0
2019-10-21 05:00 | 7038 |  |  | 0
2019-10-21 06:00 | 7039 |  |  | 0
2019-10-21 07:00 | 7040 |  |  | 0.00066678
2019-10-21 08:00 | 7041 |  |  | 0.0075013
2019-10-21 09:00 | 7042 |  |  | 0.01917
2019-10-21 10:00 | 7043 |  |  | 0.074429
2019-10-21 11:00 | 7044 |  |  | 0.11385
2019-10-21 12:00 | 7045 |  |  | 0.078263
2019-10-21 13:00 | 7046 |  |  | 0.066261
2019-10-21 14:00 | 7047 |  |  | 0.0075013
2019-10-21 15:00 | 7048 |  |  | 0.012085
2019-10-21 16:00 | 7049 |  |  | 8.3347e-05
2019-10-21 17:00 | 7050 |  |  | 0
2019-10-21 18:00 | 7051 |  |  | 0
2019-10-21 19:00 | 7052 |  |  | 0
2019-10-21 20:00 | 7053 |  |  | 0
2019-10-21 21:00 | 7054 |  |  | 0
2019-10-21 22:00 | 7055 |  |  | 0
2019-10-21 23:00 | 7056 |  |  | 0
2019-10-22 | 7057 |  |  | 0
2019-10-22 01:00 | 7058 |  |  | 0
2019-10-22 02:00 | 7059 |  |  | 0
2019-10-22 03:00 | 7060 |  |  | 0
2019-10-22 04:00 | 7061 |  |  | 0
2019-10-22 05:00 | 7062 |  |  | 0
2019-10-22 06:00 | 7063 |  |  | 0
2019-10-22 07:00 | 7064 |  |  | 0.00033339
2019-10-22 08:00 | 7065 |  |  | 0.012502
2019-10-22 09:00 | 7066 |  |  | 0.055093
2019-10-22 10:00 | 7067 |  |  | 0.041424
2019-10-22 11:00 | 7068 |  |  | 0.047008
2019-10-22 12:00 | 7069 |  |  | 0.054009
2019-10-22 13:00 | 7070 |  |  | 0.13669
2019-10-22 14:00 | 7071 |  |  | 0.17478
2019-10-22 15:00 | 7072 |  |  | 0.11635
2019-10-22 16:00 | 7073 |  |  | 0.045508
2019-10-22 17:00 | 7074 |  |  | 0.0029172
2019-10-22 18:00 | 7075 |  |  | 0
2019-10-22 19:00 | 7076 |  |  | 0
2019-10-22 20:00 | 7077 |  |  | 0
2019-10-22 21:00 | 7078 |  |  | 0
2019-10-22 22:00 | 7079 |  |  | 0
2019-10-22 23:00 | 7080 |  |  | 0
2019-10-23 | 7081 |  |  | 0
2019-10-23 01:00 | 7082 |  |  | 0
2019-10-23 02:00 | 7083 |  |  | 0
2019-10-23 03:00 | 7084 |  |  | 0
2019-10-23 04:00 | 7085 |  |  | 0
2019-10-23 05:00 | 7086 |  |  | 0
2019-10-23 06:00 | 7087 |  |  | 0
2019-10-23 07:00 | 7088 |  |  | 0.0083347
2019-10-23 08:00 | 7089 |  |  | 0.056926
2019-10-23 09:00 | 7090 |  |  | 0.16186
2019-10-23 10:00 | 7091 |  |  | 0.10093
2019-10-23 11:00 | 7092 |  |  | 0.088265
2019-10-23 12:00 | 7093 |  |  | 0.096183
2019-10-23 13:00 | 7094 |  |  | 0.08218
2019-10-23 14:00 | 7095 |  |  | 0.046174
2019-10-23 15:00 | 7096 |  |  | 0.024337
2019-10-23 16:00 | 7097 |  |  | 0.013919
2019-10-23 17:00 | 7098 |  |  | 0
2019-10-23 18:00 | 7099 |  |  | 0
2019-10-23 19:00 | 7100 |  |  | 0
2019-10-23 20:00 | 7101 |  |  | 0
2019-10-23 21:00 | 7102 |  |  | 0
2019-10-23 22:00 | 7103 |  |  | 0
2019-10-23 23:00 | 7104 |  |  | 0
2019-10-24 | 7105 |  |  | 0
2019-10-24 01:00 | 7106 |  |  | 0
2019-10-24 02:00 | 7107 |  |  | 0
2019-10-24 03:00 | 7108 |  |  | 0
2019-10-24 04:00 | 7109 |  |  | 0
2019-10-24 05:00 | 7110 |  |  | 0
2019-10-24 06:00 | 7111 |  |  | 0
2019-10-24 07:00 | 7112 |  |  | 0
2019-10-24 08:00 | 7113 |  |  | 8.3347e-05
2019-10-24 09:00 | 7114 |  |  | 0.041424
2019-10-24 10:00 | 7115 |  |  | 0.054926
2019-10-24 11:00 | 7116 |  |  | 0.027588
2019-10-24 12:00 | 7117 |  |  | 0.0084181
2019-10-24 13:00 | 7118 |  |  | 0.011669
2019-10-24 14:00 | 7119 |  |  | 0.018503
2019-10-24 15:00 | 7120 |  |  | 0.010585
2019-10-24 16:00 | 7121 |  |  | 0.0052509
2019-10-24 17:00 | 7122 |  |  | 8.3347e-05
2019-10-24 18:00 | 7123 |  |  | 0
2019-10-24 19:00 | 7124 |  |  | 0
2019-10-24 20:00 | 7125 |  |  | 0
2019-10-24 21:00 | 7126 |  |  | 0
2019-10-24 22:00 | 7127 |  |  | 0
2019-10-24 23:00 | 7128 |  |  | 0
2019-10-25 | 7129 |  |  | 0
2019-10-25 01:00 | 7130 |  |  | 0
2019-10-25 02:00 | 7131 |  |  | 0
2019-10-25 03:00 | 7132 |  |  | 0
2019-10-25 04:00 | 7133 |  |  | 0
2019-10-25 05:00 | 7134 |  |  | 0
2019-10-25 06:00 | 7135 |  |  | 0
2019-10-25 07:00 | 7136 |  |  | 0.023254
2019-10-25 08:00 | 7137 |  |  | 0.10352
2019-10-25 09:00 | 7138 |  |  | 0.25696
2019-10-25 10:00 | 7139 |  |  | 0.34972
2019-10-25 11:00 | 7140 |  |  | 0.42782
2019-10-25 12:00 | 7141 |  |  | 0.48491
2019-10-25 13:00 | 7142 |  |  | 0.40007
2019-10-25 14:00 | 7143 |  |  | 0.27005
2019-10-25 15:00 | 7144 |  |  | 0.24521
2019-10-25 16:00 | 7145 |  |  | 0.081014
2019-10-25 17:00 | 7146 |  |  | 0.0033339
2019-10-25 18:00 | 7147 |  |  | 0
2019-10-25 19:00 | 7148 |  |  | 0
2019-10-25 20:00 | 7149 |  |  | 0
2019-10-25 21:00 | 7150 |  |  | 0
2019-10-25 22:00 | 7151 |  |  | 0
2019-10-25 23:00 | 7152 |  |  | 0
2019-10-26 | 7153 |  |  | 0
2019-10-26 01:00 | 7154 |  |  | 0
2019-10-26 02:00 | 7155 |  |  | 0
2019-10-26 03:00 | 7156 |  |  | 0
2019-10-26 04:00 | 7157 |  |  | 0
2019-10-26 05:00 | 7158 |  |  | 0
2019-10-26 06:00 | 7159 |  |  | 0
2019-10-26 07:00 | 7160 |  |  | 0.02242
2019-10-26 08:00 | 7161 |  |  | 0.15811
2019-10-26 09:00 | 7162 |  |  | 0.35364
2019-10-26 10:00 | 7163 |  |  | 0.50267
2019-10-26 11:00 | 7164 |  |  | 0.60177
2019-10-26 12:00 | 7165 |  |  | 0.63511
2019-10-26 13:00 | 7166 |  |  | 0.61035
2019-10-26 14:00 | 7167 |  |  | 0.48458
2019-10-26 15:00 | 7168 |  |  | 0.31372
2019-10-26 16:00 | 7169 |  |  | 0.11194
2019-10-26 17:00 | 7170 |  |  | 0.0035839
2019-10-26 18:00 | 7171 |  |  | 0
2019-10-26 19:00 | 7172 |  |  | 0
2019-10-26 20:00 | 7173 |  |  | 0
2019-10-26 21:00 | 7174 |  |  | 0
2019-10-26 22:00 | 7175 |  |  | 0
2019-10-26 23:00 | 7176 |  |  | 0
2019-10-27 | 7177 |  |  | 0
2019-10-27 01:00 | 7178 |  |  | 0
2019-10-27 02:00 | 7179 |  |  | 0
2019-10-27 03:00 | 7180 |  |  | 0
2019-10-27 04:00 | 7181 |  |  | 0
2019-10-27 05:00 | 7182 |  |  | 0
2019-10-27 06:00 | 7183 |  |  | 0.02192
2019-10-27 07:00 | 7184 |  |  | 0.15361
2019-10-27 08:00 | 7185 |  |  | 0.34422
2019-10-27 09:00 | 7186 |  |  | 0.50158
2019-10-27 10:00 | 7187 |  |  | 0.59327
2019-10-27 11:00 | 7188 |  |  | 0.62994
2019-10-27 12:00 | 7189 |  |  | 0.5921
2019-10-27 13:00 | 7190 |  |  | 0.37573
2019-10-27 14:00 | 7191 |  |  | 0.25071
2019-10-27 15:00 | 7192 |  |  | 0.07943
2019-10-27 16:00 | 7193 |  |  | 0.0046674
2019-10-27 17:00 | 7194 |  |  | 0
2019-10-27 18:00 | 7195 |  |  | 0
2019-10-27 19:00 | 7196 |  |  | 0
2019-10-27 20:00 | 7197 |  |  | 0
2019-10-27 21:00 | 7198 |  |  | 0
2019-10-27 22:00 | 7199 |  |  | 0
2019-10-27 23:00 | 7200 |  |  | 0
2019-10-28 | 7201 |  |  | 0
2019-10-28 01:00 | 7202 |  |  | 0
2019-10-28 02:00 | 7203 |  |  | 0
2019-10-28 03:00 | 7204 |  |  | 0
2019-10-28 04:00 | 7205 |  |  | 0
2019-10-28 05:00 | 7206 |  |  | 0
2019-10-28 06:00 | 7207 |  |  | 0.02217
2019-10-28 07:00 | 7208 |  |  | 0.10077
2019-10-28 08:00 | 7209 |  |  | 0.17636
2019-10-28 09:00 | 7210 |  |  | 0.35056
2019-10-28 10:00 | 7211 |  |  | 0.52575
2019-10-28 11:00 | 7212 |  |  | 0.40848
2019-10-28 12:00 | 7213 |  |  | 0.28113
2019-10-28 13:00 | 7214 |  |  | 0.28038
2019-10-28 14:00 | 7215 |  |  | 0.12044
2019-10-28 15:00 | 7216 |  |  | 0.02092
2019-10-28 16:00 | 7217 |  |  | 8.3347e-05
2019-10-28 17:00 | 7218 |  |  | 0
2019-10-28 18:00 | 7219 |  |  | 0
2019-10-28 19:00 | 7220 |  |  | 0
2019-10-28 20:00 | 7221 |  |  | 0
2019-10-28 21:00 | 7222 |  |  | 0
2019-10-28 22:00 | 7223 |  |  | 0
2019-10-28 23:00 | 7224 |  |  | 0
2019-10-29 | 7225 |  |  | 0
2019-10-29 01:00 | 7226 |  |  | 0
2019-10-29 02:00 | 7227 |  |  | 0
2019-10-29 03:00 | 7228 |  |  | 0
2019-10-29 04:00 | 7229 |  |  | 0
2019-10-29 05:00 | 7230 |  |  | 0
2019-10-29 06:00 | 7231 |  |  | 0.0012502
2019-10-29 07:00 | 7232 |  |  | 0.017086
2019-10-29 08:00 | 7233 |  |  | 0.032505
2019-10-29 09:00 | 7234 |  |  | 0.078846
2019-10-29 10:00 | 7235 |  |  | 0.14594
2019-10-29 11:00 | 7236 |  |  | 0.11752
2019-10-29 12:00 | 7237 |  |  | 0.091599
2019-10-29 13:00 | 7238 |  |  | 0.07793
2019-10-29 14:00 | 7239 |  |  | 0.041757
2019-10-29 15:00 | 7240 |  |  | 0.0090015
2019-10-29 16:00 | 7241 |  |  | 0
2019-10-29 17:00 | 7242 |  |  | 0
2019-10-29 18:00 | 7243 |  |  | 0
2019-10-29 19:00 | 7244 |  |  | 0
2019-10-29 20:00 | 7245 |  |  | 0
2019-10-29 21:00 | 7246 |  |  | 0
2019-10-29 22:00 | 7247 |  |  | 0
2019-10-29 23:00 | 7248 |  |  | 0
2019-10-30 | 7249 |  |  | 0
2019-10-30 01:00 | 7250 |  |  | 0
2019-10-30 02:00 | 7251 |  |  | 0
2019-10-30 03:00 | 7252 |  |  | 0
2019-10-30 04:00 | 7253 |  |  | 0
2019-10-30 05:00 | 7254 |  |  | 0
2019-10-30 06:00 | 7255 |  |  | 0.0015003
2019-10-30 07:00 | 7256 |  |  | 0.016336
2019-10-30 08:00 | 7257 |  |  | 0.06076
2019-10-30 09:00 | 7258 |  |  | 0.14686
2019-10-30 10:00 | 7259 |  |  | 0.22312
2019-10-30 11:00 | 7260 |  |  | 0.15678
2019-10-30 12:00 | 7261 |  |  | 0.18445
2019-10-30 13:00 | 7262 |  |  | 0.095266
2019-10-30 14:00 | 7263 |  |  | 0.044341
2019-10-30 15:00 | 7264 |  |  | 0.013086
2019-10-30 16:00 | 7265 |  |  | 0
2019-10-30 17:00 | 7266 |  |  | 0
2019-10-30 18:00 | 7267 |  |  | 0
2019-10-30 19:00 | 7268 |  |  | 0
2019-10-30 20:00 | 7269 |  |  | 0
2019-10-30 21:00 | 7270 |  |  | 0
2019-10-30 22:00 | 7271 |  |  | 0
2019-10-30 23:00 | 7272 |  |  | 0
2019-10-31 | 7273 |  |  | 0
2019-10-31 01:00 | 7274 |  |  | 0
2019-10-31 02:00 | 7275 |  |  | 0
2019-10-31 03:00 | 7276 |  |  | 0
2019-10-31 04:00 | 7277 |  |  | 0
2019-10-31 05:00 | 7278 |  |  | 0
2019-10-31 06:00 | 7279 |  |  | 0.0016669
2019-10-31 07:00 | 7280 |  |  | 0.017586
2019-10-31 08:00 | 7281 |  |  | 0.031672
2019-10-31 09:00 | 7282 |  |  | 0.030088
2019-10-31 10:00 | 7283 |  |  | 0.04259
2019-10-31 11:00 | 7284 |  |  | 0.059427
2019-10-31 12:00 | 7285 |  |  | 0.035506
2019-10-31 13:00 | 7286 |  |  | 0.03809
2019-10-31 14:00 | 7287 |  |  | 0.025088
2019-10-31 15:00 | 7288 |  |  | 0.0094182
2019-10-31 16:00 | 7289 |  |  | 0
2019-10-31 17:00 | 7290 |  |  | 0
2019-10-31 18:00 | 7291 |  |  | 0
2019-10-31 19:00 | 7292 |  |  | 0
2019-10-31 20:00 | 7293 |  |  | 0
2019-10-31 21:00 | 7294 |  |  | 0
2019-10-31 22:00 | 7295 |  |  | 0
2019-10-31 23:00 | 7296 |  |  | 0
2019-11-01 | 7297 |  |  | 0
2019-11-01 01:00 | 7298 |  |  | 0
2019-11-01 02:00 | 7299 |  |  | 0
2019-11-01 03:00 | 7300 |  |  | 0
2019-11-01 04:00 | 7301 |  |  | 0
2019-11-01 05:00 | 7302 |  |  | 0
2019-11-01 06:00 | 7303 |  |  | 0
2019-11-01 07:00 | 7304 |  |  | 0.0050842
2019-11-01 08:00 | 7305 |  |  | 0.019837
2019-11-01 09:00 | 7306 |  |  | 0.014086
2019-11-01 10:00 | 7307 |  |  | 0.029255
2019-11-01 11:00 | 7308 |  |  | 0.025004
2019-11-01 12:00 | 7309 |  |  | 0.025254
2019-11-01 13:00 | 7310 |  |  | 0.029672
2019-11-01 14:00 | 7311 |  |  | 0.0085014
2019-11-01 15:00 | 7312 |  |  | 0.0015836
2019-11-01 16:00 | 7313 |  |  | 0
2019-11-01 17:00 | 7314 |  |  | 0
2019-11-01 18:00 | 7315 |  |  | 0
2019-11-01 19:00 | 7316 |  |  | 0
2019-11-01 20:00 | 7317 |  |  | 0
2019-11-01 21:00 | 7318 |  |  | 0
2019-11-01 22:00 | 7319 |  |  | 0
2019-11-01 23:00 | 7320 |  |  | 0
2019-11-02 | 7321 |  |  | 0
2019-11-02 01:00 | 7322 |  |  | 0
2019-11-02 02:00 | 7323 |  |  | 0
2019-11-02 03:00 | 7324 |  |  | 0
2019-11-02 04:00 | 7325 |  |  | 0
2019-11-02 05:00 | 7326 |  |  | 0
2019-11-02 06:00 | 7327 |  |  | 0
2019-11-02 07:00 | 7328 |  |  | 0.0034172
2019-11-02 08:00 | 7329 |  |  | 0.010835
2019-11-02 09:00 | 7330 |  |  | 0.05926
2019-11-02 10:00 | 7331 |  |  | 0.081597
2019-11-02 11:00 | 7332 |  |  | 0.072679
2019-11-02 12:00 | 7333 |  |  | 0.042924
2019-11-02 13:00 | 7334 |  |  | 0.0093349
2019-11-02 14:00 | 7335 |  |  | 0.024587
2019-11-02 15:00 | 7336 |  |  | 0.0085848
2019-11-02 16:00 | 7337 |  |  | 0
2019-11-02 17:00 | 7338 |  |  | 0
2019-11-02 18:00 | 7339 |  |  | 0
2019-11-02 19:00 | 7340 |  |  | 0
2019-11-02 20:00 | 7341 |  |  | 0
2019-11-02 21:00 | 7342 |  |  | 0
2019-11-02 22:00 | 7343 |  |  | 0
2019-11-02 23:00 | 7344 |  |  | 0
2019-11-03 | 7345 |  |  | 0
2019-11-03 01:00 | 7346 |  |  | 0
2019-11-03 02:00 | 7347 |  |  | 0
2019-11-03 03:00 | 7348 |  |  | 0
2019-11-03 04:00 | 7349 |  |  | 0
2019-11-03 05:00 | 7350 |  |  | 0
2019-11-03 06:00 | 7351 |  |  | 8.3347e-05
2019-11-03 07:00 | 7352 |  |  | 0.0034172
2019-11-03 08:00 | 7353 |  |  | 0.01742
2019-11-03 09:00 | 7354 |  |  | 0.023837
2019-11-03 10:00 | 7355 |  |  | 0.043757
2019-11-03 11:00 | 7356 |  |  | 0.06101
2019-11-03 12:00 | 7357 |  |  | 0.079513
2019-11-03 13:00 | 7358 |  |  | 0.070012
2019-11-03 14:00 | 7359 |  |  | 0.16161
2019-11-03 15:00 | 7360 |  |  | 0.047341
2019-11-03 16:00 | 7361 |  |  | 0.0020837
2019-11-03 17:00 | 7362 |  |  | 0
2019-11-03 18:00 | 7363 |  |  | 0
2019-11-03 19:00 | 7364 |  |  | 0
2019-11-03 20:00 | 7365 |  |  | 0
2019-11-03 21:00 | 7366 |  |  | 0
2019-11-03 22:00 | 7367 |  |  | 0
2019-11-03 23:00 | 7368 |  |  | 0
2019-11-04 | 7369 |  |  | 0
2019-11-04 01:00 | 7370 |  |  | 0
2019-11-04 02:00 | 7371 |  |  | 0
2019-11-04 03:00 | 7372 |  |  | 0
2019-11-04 04:00 | 7373 |  |  | 0
2019-11-04 05:00 | 7374 |  |  | 0
2019-11-04 06:00 | 7375 |  |  | 0.0076679
2019-11-04 07:00 | 7376 |  |  | 0.095766
2019-11-04 08:00 | 7377 |  |  | 0.34106
2019-11-04 09:00 | 7378 |  |  | 0.50025
2019-11-04 10:00 | 7379 |  |  | 0.61652
2019-11-04 11:00 | 7380 |  |  | 0.64444
2019-11-04 12:00 | 7381 |  |  | 0.48408
2019-11-04 13:00 | 7382 |  |  | 0.45624
2019-11-04 14:00 | 7383 |  |  | 0.26613
2019-11-04 15:00 | 7384 |  |  | 0.049008
2019-11-04 16:00 | 7385 |  |  | 0.00025004
2019-11-04 17:00 | 7386 |  |  | 0
2019-11-04 18:00 | 7387 |  |  | 0
2019-11-04 19:00 | 7388 |  |  | 0
2019-11-04 20:00 | 7389 |  |  | 0
2019-11-04 21:00 | 7390 |  |  | 0
2019-11-04 22:00 | 7391 |  |  | 0
2019-11-04 23:00 | 7392 |  |  | 0
2019-11-05 | 7393 |  |  | 0
2019-11-05 01:00 | 7394 |  |  | 0
2019-11-05 02:00 | 7395 |  |  | 0
2019-11-05 03:00 | 7396 |  |  | 0
2019-11-05 04:00 | 7397 |  |  | 0
2019-11-05 05:00 | 7398 |  |  | 0
2019-11-05 06:00 | 7399 |  |  | 0.0078346
2019-11-05 07:00 | 7400 |  |  | 0.11694
2019-11-05 08:00 | 7401 |  |  | 0.31722
2019-11-05 09:00 | 7402 |  |  | 0.48116
2019-11-05 10:00 | 7403 |  |  | 0.56818
2019-11-05 11:00 | 7404 |  |  | 0.55243
2019-11-05 12:00 | 7405 |  |  | 0.29447
2019-11-05 13:00 | 7406 |  |  | 0.41515
2019-11-05 14:00 | 7407 |  |  | 0.1712
2019-11-05 15:00 | 7408 |  |  | 0.060177
2019-11-05 16:00 | 7409 |  |  | 0.00025004
2019-11-05 17:00 | 7410 |  |  | 0
2019-11-05 18:00 | 7411 |  |  | 0
2019-11-05 19:00 | 7412 |  |  | 0
2019-11-05 20:00 | 7413 |  |  | 0
2019-11-05 21:00 | 7414 |  |  | 0
2019-11-05 22:00 | 7415 |  |  | 0
2019-11-05 23:00 | 7416 |  |  | 0
2019-11-06 | 7417 |  |  | 0
2019-11-06 01:00 | 7418 |  |  | 0
2019-11-06 02:00 | 7419 |  |  | 0
2019-11-06 03:00 | 7420 |  |  | 0
2019-11-06 04:00 | 7421 |  |  | 0
2019-11-06 05:00 | 7422 |  |  | 0
2019-11-06 06:00 | 7423 |  |  | 0.0095849
2019-11-06 07:00 | 7424 |  |  | 0.044924
2019-11-06 08:00 | 7425 |  |  | 0.23729
2019-11-06 09:00 | 7426 |  |  | 0.25421
2019-11-06 10:00 | 7427 |  |  | 0.44541
2019-11-06 11:00 | 7428 |  |  | 0.45224
2019-11-06 12:00 | 7429 |  |  | 0.42399
2019-11-06 13:00 | 7430 |  |  | 0.23796
2019-11-06 14:00 | 7431 |  |  | 0.056093
2019-11-06 15:00 | 7432 |  |  | 0.048175
2019-11-06 16:00 | 7433 |  |  | 0.00050008
2019-11-06 17:00 | 7434 |  |  | 0
2019-11-06 18:00 | 7435 |  |  | 0
2019-11-06 19:00 | 7436 |  |  | 0
2019-11-06 20:00 | 7437 |  |  | 0
2019-11-06 21:00 | 7438 |  |  | 0
2019-11-06 22:00 | 7439 |  |  | 0
2019-11-06 23:00 | 7440 |  |  | 0
2019-11-07 | 7441 |  |  | 0
2019-11-07 01:00 | 7442 |  |  | 0
2019-11-07 02:00 | 7443 |  |  | 0
2019-11-07 03:00 | 7444 |  |  | 0
2019-11-07 04:00 | 7445 |  |  | 0
2019-11-07 05:00 | 7446 |  |  | 0
2019-11-07 06:00 | 7447 |  |  | 0.0048341
2019-11-07 07:00 | 7448 |  |  | 0.058176
2019-11-07 08:00 | 7449 |  |  | 0.058093
2019-11-07 09:00 | 7450 |  |  | 0.037256
2019-11-07 10:00 | 7451 |  |  | 0.053176
2019-11-07 11:00 | 7452 |  |  | 0.052425
2019-11-07 12:00 | 7453 |  |  | 0.054759
2019-11-07 13:00 | 7454 |  |  | 0.02017
2019-11-07 14:00 | 7455 |  |  | 0.0053342
2019-11-07 15:00 | 7456 |  |  | 0.0022504
2019-11-07 16:00 | 7457 |  |  | 0
2019-11-07 17:00 | 7458 |  |  | 0
2019-11-07 18:00 | 7459 |  |  | 0
2019-11-07 19:00 | 7460 |  |  | 0
2019-11-07 20:00 | 7461 |  |  | 0
2019-11-07 21:00 | 7462 |  |  | 0
2019-11-07 22:00 | 7463 |  |  | 0
2019-11-07 23:00 | 7464 |  |  | 0
2019-11-08 | 7465 |  |  | 0
2019-11-08 01:00 | 7466 |  |  | 0
2019-11-08 02:00 | 7467 |  |  | 0
2019-11-08 03:00 | 7468 |  |  | 0
2019-11-08 04:00 | 7469 |  |  | 0
2019-11-08 05:00 | 7470 |  |  | 0
2019-11-08 06:00 | 7471 |  |  | 0.00033339
2019-11-08 07:00 | 7472 |  |  | 0.018086
2019-11-08 08:00 | 7473 |  |  | 0.048758
2019-11-08 09:00 | 7474 |  |  | 0.12894
2019-11-08 10:00 | 7475 |  |  | 0.44957
2019-11-08 11:00 | 7476 |  |  | 0.16436
2019-11-08 12:00 | 7477 |  |  | 0.3283
2019-11-08 13:00 | 7478 |  |  | 0.24796
2019-11-08 14:00 | 7479 |  |  | 0.12302
2019-11-08 15:00 | 7480 |  |  | 0.04034
2019-11-08 16:00 | 7481 |  |  | 0
2019-11-08 17:00 | 7482 |  |  | 0
2019-11-08 18:00 | 7483 |  |  | 0
2019-11-08 19:00 | 7484 |  |  | 0
2019-11-08 20:00 | 7485 |  |  | 0
2019-11-08 21:00 | 7486 |  |  | 0
2019-11-08 22:00 | 7487 |  |  | 0
2019-11-08 23:00 | 7488 |  |  | 0
2019-11-09 | 7489 |  |  | 0
2019-11-09 01:00 | 7490 |  |  | 0
2019-11-09 02:00 | 7491 |  |  | 0
2019-11-09 03:00 | 7492 |  |  | 0
2019-11-09 04:00 | 7493 |  |  | 0
2019-11-09 05:00 | 7494 |  |  | 0
2019-11-09 06:00 | 7495 |  |  | 0.0095016
2019-11-09 07:00 | 7496 |  |  | 0.11652
2019-11-09 08:00 | 7497 |  |  | 0.29297
2019-11-09 09:00 | 7498 |  |  | 0.45133
2019-11-09 10:00 | 7499 |  |  | 0.56176
2019-11-09 11:00 | 7500 |  |  | 0.5926
2019-11-09 12:00 | 7501 |  |  | 0.50967
2019-11-09 13:00 | 7502 |  |  | 0.40698
2019-11-09 14:00 | 7503 |  |  | 0.22912
2019-11-09 15:00 | 7504 |  |  | 0.049925
2019-11-09 16:00 | 7505 |  |  | 0.00025004
2019-11-09 17:00 | 7506 |  |  | 0
2019-11-09 18:00 | 7507 |  |  | 0
2019-11-09 19:00 | 7508 |  |  | 0
2019-11-09 20:00 | 7509 |  |  | 0
2019-11-09 21:00 | 7510 |  |  | 0
2019-11-09 22:00 | 7511 |  |  | 0
2019-11-09 23:00 | 7512 |  |  | 0
2019-11-10 | 7513 |  |  | 0
2019-11-10 01:00 | 7514 |  |  | 0
2019-11-10 02:00 | 7515 |  |  | 0
2019-11-10 03:00 | 7516 |  |  | 0
2019-11-10 04:00 | 7517 |  |  | 0
2019-11-10 05:00 | 7518 |  |  | 0
2019-11-10 06:00 | 7519 |  |  | 0.0012502
2019-11-10 07:00 | 7520 |  |  | 0.031339
2019-11-10 08:00 | 7521 |  |  | 0.074179
2019-11-10 09:00 | 7522 |  |  | 0.12469
2019-11-10 10:00 | 7523 |  |  | 0.27763
2019-11-10 11:00 | 7524 |  |  | 0.16011
2019-11-10 12:00 | 7525 |  |  | 0.11919
2019-11-10 13:00 | 7526 |  |  | 0.11652
2019-11-10 14:00 | 7527 |  |  | 0.06176
2019-11-10 15:00 | 7528 |  |  | 0.015503
2019-11-10 16:00 | 7529 |  |  | 0
2019-11-10 17:00 | 7530 |  |  | 0
2019-11-10 18:00 | 7531 |  |  | 0
2019-11-10 19:00 | 7532 |  |  | 0
2019-11-10 20:00 | 7533 |  |  | 0
2019-11-10 21:00 | 7534 |  |  | 0
2019-11-10 22:00 | 7535 |  |  | 0
2019-11-10 23:00 | 7536 |  |  | 0
2019-11-11 | 7537 |  |  | 0
2019-11-11 01:00 | 7538 |  |  | 0
2019-11-11 02:00 | 7539 |  |  | 0
2019-11-11 03:00 | 7540 |  |  | 0
2019-11-11 04:00 | 7541 |  |  | 0
2019-11-11 05:00 | 7542 |  |  | 0
2019-11-11 06:00 | 7543 |  |  | 0.00041674
2019-11-11 07:00 | 7544 |  |  | 0.01767
2019-11-11 08:00 | 7545 |  |  | 0.067511
2019-11-11 09:00 | 7546 |  |  | 0.12577
2019-11-11 10:00 | 7547 |  |  | 0.17211
2019-11-11 11:00 | 7548 |  |  | 0.10477
2019-11-11 12:00 | 7549 |  |  | 0.096766
2019-11-11 13:00 | 7550 |  |  | 0.065344
2019-11-11 14:00 | 7551 |  |  | 0.022754
2019-11-11 15:00 | 7552 |  |  | 0.0015003
2019-11-11 16:00 | 7553 |  |  | 0
2019-11-11 17:00 | 7554 |  |  | 0
2019-11-11 18:00 | 7555 |  |  | 0
2019-11-11 19:00 | 7556 |  |  | 0
2019-11-11 20:00 | 7557 |  |  | 0
2019-11-11 21:00 | 7558 |  |  | 0
2019-11-11 22:00 | 7559 |  |  | 0
2019-11-11 23:00 | 7560 |  |  | 0
2019-11-12 | 7561 |  |  | 0
2019-11-12 01:00 | 7562 |  |  | 0
2019-11-12 02:00 | 7563 |  |  | 0
2019-11-12 03:00 | 7564 |  |  | 0
2019-11-12 04:00 | 7565 |  |  | 0
2019-11-12 05:00 | 7566 |  |  | 0
2019-11-12 06:00 | 7567 |  |  | 0.0065011
2019-11-12 07:00 | 7568 |  |  | 0.075263
2019-11-12 08:00 | 7569 |  |  | 0.23304
2019-11-12 09:00 | 7570 |  |  | 0.47358
2019-11-12 10:00 | 7571 |  |  | 0.56926
2019-11-12 11:00 | 7572 |  |  | 0.56909
2019-11-12 12:00 | 7573 |  |  | 0.50383
2019-11-12 13:00 | 7574 |  |  | 0.36606
2019-11-12 14:00 | 7575 |  |  | 0.2202
2019-11-12 15:00 | 7576 |  |  | 0.049258
2019-11-12 16:00 | 7577 |  |  | 0.00016669
2019-11-12 17:00 | 7578 |  |  | 0
2019-11-12 18:00 | 7579 |  |  | 0
2019-11-12 19:00 | 7580 |  |  | 0
2019-11-12 20:00 | 7581 |  |  | 0
2019-11-12 21:00 | 7582 |  |  | 0
2019-11-12 22:00 | 7583 |  |  | 0
2019-11-12 23:00 | 7584 |  |  | 0
2019-11-13 | 7585 |  |  | 0
2019-11-13 01:00 | 7586 |  |  | 0
2019-11-13 02:00 | 7587 |  |  | 0
2019-11-13 03:00 | 7588 |  |  | 0
2019-11-13 04:00 | 7589 |  |  | 0
2019-11-13 05:00 | 7590 |  |  | 0
2019-11-13 06:00 | 7591 |  |  | 0.007918
2019-11-13 07:00 | 7592 |  |  | 0.12419
2019-11-13 08:00 | 7593 |  |  | 0.32505
2019-11-13 09:00 | 7594 |  |  | 0.481
2019-11-13 10:00 | 7595 |  |  | 0.5881
2019-11-13 11:00 | 7596 |  |  | 0.61844
2019-11-13 12:00 | 7597 |  |  | 0.52984
2019-11-13 13:00 | 7598 |  |  | 0.38206
2019-11-13 14:00 | 7599 |  |  | 0.15794
2019-11-13 15:00 | 7600 |  |  | 0.06226
2019-11-13 16:00 | 7601 |  |  | 0.00016669
2019-11-13 17:00 | 7602 |  |  | 0
2019-11-13 18:00 | 7603 |  |  | 0
2019-11-13 19:00 | 7604 |  |  | 0
2019-11-13 20:00 | 7605 |  |  | 0
2019-11-13 21:00 | 7606 |  |  | 0
2019-11-13 22:00 | 7607 |  |  | 0
2019-11-13 23:00 | 7608 |  |  | 0
2019-11-14 | 7609 |  |  | 0
2019-11-14 01:00 | 7610 |  |  | 0
2019-11-14 02:00 | 7611 |  |  | 0
2019-11-14 03:00 | 7612 |  |  | 0
2019-11-14 04:00 | 7613 |  |  | 0
2019-11-14 05:00 | 7614 |  |  | 0
2019-11-14 06:00 | 7615 |  |  | 0.0010002
2019-11-14 07:00 | 7616 |  |  | 0.027255
2019-11-14 08:00 | 7617 |  |  | 0.062927
2019-11-14 09:00 | 7618 |  |  | 0.050675
2019-11-14 10:00 | 7619 |  |  | 0.055176
2019-11-14 11:00 | 7620 |  |  | 0.027171
2019-11-14 12:00 | 7621 |  |  | 0.023504
2019-11-14 13:00 | 7622 |  |  | 0.0093349
2019-11-14 14:00 | 7623 |  |  | 0.002167
2019-11-14 15:00 | 7624 |  |  | 0.00041674
2019-11-14 16:00 | 7625 |  |  | 0
2019-11-14 17:00 | 7626 |  |  | 0
2019-11-14 18:00 | 7627 |  |  | 0
2019-11-14 19:00 | 7628 |  |  | 0
2019-11-14 20:00 | 7629 |  |  | 0
2019-11-14 21:00 | 7630 |  |  | 0
2019-11-14 22:00 | 7631 |  |  | 0
2019-11-14 23:00 | 7632 |  |  | 0
2019-11-15 | 7633 |  |  | 0
2019-11-15 01:00 | 7634 |  |  | 0
2019-11-15 02:00 | 7635 |  |  | 0
2019-11-15 03:00 | 7636 |  |  | 0
2019-11-15 04:00 | 7637 |  |  | 0
2019-11-15 05:00 | 7638 |  |  | 0
2019-11-15 06:00 | 7639 |  |  | 0.0011669
2019-11-15 07:00 | 7640 |  |  | 0.024671
2019-11-15 08:00 | 7641 |  |  | 0.029255
2019-11-15 09:00 | 7642 |  |  | 0.044841
2019-11-15 10:00 | 7643 |  |  | 0.06076
2019-11-15 11:00 | 7644 |  |  | 0.097266
2019-11-15 12:00 | 7645 |  |  | 0.16078
2019-11-15 13:00 | 7646 |  |  | 0.097016
2019-11-15 14:00 | 7647 |  |  | 0.041924
2019-11-15 15:00 | 7648 |  |  | 0.011419
2019-11-15 16:00 | 7649 |  |  | 0
2019-11-15 17:00 | 7650 |  |  | 0
2019-11-15 18:00 | 7651 |  |  | 0
2019-11-15 19:00 | 7652 |  |  | 0
2019-11-15 20:00 | 7653 |  |  | 0
2019-11-15 21:00 | 7654 |  |  | 0
2019-11-15 22:00 | 7655 |  |  | 0
2019-11-15 23:00 | 7656 |  |  | 0
2019-11-16 | 7657 |  |  | 0
2019-11-16 01:00 | 7658 |  |  | 0
2019-11-16 02:00 | 7659 |  |  | 0
2019-11-16 03:00 | 7660 |  |  | 0
2019-11-16 04:00 | 7661 |  |  | 0
2019-11-16 05:00 | 7662 |  |  | 0
2019-11-16 06:00 | 7663 |  |  | 0
2019-11-16 07:00 | 7664 |  |  | 0.02192
2019-11-16 08:00 | 7665 |  |  | 0.06026
2019-11-16 09:00 | 7666 |  |  | 0.087598
2019-11-16 10:00 | 7667 |  |  | 0.14511
2019-11-16 11:00 | 7668 |  |  | 0.078263
2019-11-16 12:00 | 7669 |  |  | 0.14902
2019-11-16 13:00 | 7670 |  |  | 0.18803
2019-11-16 14:00 | 7671 |  |  | 0.026921
2019-11-16 15:00 | 7672 |  |  | 0.0030005
2019-11-16 16:00 | 7673 |  |  | 0
2019-11-16 17:00 | 7674 |  |  | 0
2019-11-16 18:00 | 7675 |  |  | 0
2019-11-16 19:00 | 7676 |  |  | 0
2019-11-16 20:00 | 7677 |  |  | 0
2019-11-16 21:00 | 7678 |  |  | 0
2019-11-16 22:00 | 7679 |  |  | 0
2019-11-16 23:00 | 7680 |  |  | 0
2019-11-17 | 7681 |  |  | 0
2019-11-17 01:00 | 7682 |  |  | 0
2019-11-17 02:00 | 7683 |  |  | 0
2019-11-17 03:00 | 7684 |  |  | 0
2019-11-17 04:00 | 7685 |  |  | 0
2019-11-17 05:00 | 7686 |  |  | 0
2019-11-17 06:00 | 7687 |  |  | 0
2019-11-17 07:00 | 7688 |  |  | 0.015919
2019-11-17 08:00 | 7689 |  |  | 0.040173
2019-11-17 09:00 | 7690 |  |  | 0.084931
2019-11-17 10:00 | 7691 |  |  | 0.1797
2019-11-17 11:00 | 7692 |  |  | 0.45199
2019-11-17 12:00 | 7693 |  |  | 0.32647
2019-11-17 13:00 | 7694 |  |  | 0.2192
2019-11-17 14:00 | 7695 |  |  | 0.19212
2019-11-17 15:00 | 7696 |  |  | 0.015003
2019-11-17 16:00 | 7697 |  |  | 0
2019-11-17 17:00 | 7698 |  |  | 0
2019-11-17 18:00 | 7699 |  |  | 0
2019-11-17 19:00 | 7700 |  |  | 0
2019-11-17 20:00 | 7701 |  |  | 0
2019-11-17 21:00 | 7702 |  |  | 0
2019-11-17 22:00 | 7703 |  |  | 0
2019-11-17 23:00 | 7704 |  |  | 0
2019-11-18 | 7705 |  |  | 0
2019-11-18 01:00 | 7706 |  |  | 0
2019-11-18 02:00 | 7707 |  |  | 0
2019-11-18 03:00 | 7708 |  |  | 0
2019-11-18 04:00 | 7709 |  |  | 0
2019-11-18 05:00 | 7710 |  |  | 0
2019-11-18 06:00 | 7711 |  |  | 0
2019-11-18 07:00 | 7712 |  |  | 0.0070845
2019-11-18 08:00 | 7713 |  |  | 0.018336
2019-11-18 09:00 | 7714 |  |  | 0.023087
2019-11-18 10:00 | 7715 |  |  | 0.10793
2019-11-18 11:00 | 7716 |  |  | 0.15186
2019-11-18 12:00 | 7717 |  |  | 0.085931
2019-11-18 13:00 | 7718 |  |  | 0.047091
2019-11-18 14:00 | 7719 |  |  | 0.025004
2019-11-18 15:00 | 7720 |  |  | 0.0028338
2019-11-18 16:00 | 7721 |  |  | 0
2019-11-18 17:00 | 7722 |  |  | 0
2019-11-18 18:00 | 7723 |  |  | 0
2019-11-18 19:00 | 7724 |  |  | 0
2019-11-18 20:00 | 7725 |  |  | 0
2019-11-18 21:00 | 7726 |  |  | 0
2019-11-18 22:00 | 7727 |  |  | 0
2019-11-18 23:00 | 7728 |  |  | 0
2019-11-19 | 7729 |  |  | 0
2019-11-19 01:00 | 7730 |  |  | 0
2019-11-19 02:00 | 7731 |  |  | 0
2019-11-19 03:00 | 7732 |  |  | 0
2019-11-19 04:00 | 7733 |  |  | 0
2019-11-19 05:00 | 7734 |  |  | 0
2019-11-19 06:00 | 7735 |  |  | 0
2019-11-19 07:00 | 7736 |  |  | 0.0045008
2019-11-19 08:00 | 7737 |  |  | 0.023421
2019-11-19 09:00 | 7738 |  |  | 0.034422
2019-11-19 10:00 | 7739 |  |  | 0.044257
2019-11-19 11:00 | 7740 |  |  | 0.16386
2019-11-19 12:00 | 7741 |  |  | 0.21395
2019-11-19 13:00 | 7742 |  |  | 0.12694
2019-11-19 14:00 | 7743 |  |  | 0.057843
2019-11-19 15:00 | 7744 |  |  | 0.0093349
2019-11-19 16:00 | 7745 |  |  | 0
2019-11-19 17:00 | 7746 |  |  | 0
2019-11-19 18:00 | 7747 |  |  | 0
2019-11-19 19:00 | 7748 |  |  | 0
2019-11-19 20:00 | 7749 |  |  | 0
2019-11-19 21:00 | 7750 |  |  | 0
2019-11-19 22:00 | 7751 |  |  | 0
2019-11-19 23:00 | 7752 |  |  | 0
2019-11-20 | 7753 |  |  | 0
2019-11-20 01:00 | 7754 |  |  | 0
2019-11-20 02:00 | 7755 |  |  | 0
2019-11-20 03:00 | 7756 |  |  | 0
2019-11-20 04:00 | 7757 |  |  | 0
2019-11-20 05:00 | 7758 |  |  | 0
2019-11-20 06:00 | 7759 |  |  | 0
2019-11-20 07:00 | 7760 |  |  | 0.031172
2019-11-20 08:00 | 7761 |  |  | 0.045924
2019-11-20 09:00 | 7762 |  |  | 0.095766
2019-11-20 10:00 | 7763 |  |  | 0.1041
2019-11-20 11:00 | 7764 |  |  | 0.35098
2019-11-20 12:00 | 7765 |  |  | 0.18645
2019-11-20 13:00 | 7766 |  |  | 0.14561
2019-11-20 14:00 | 7767 |  |  | 0.083431
2019-11-20 15:00 | 7768 |  |  | 0.01767
2019-11-20 16:00 | 7769 |  |  | 0
2019-11-20 17:00 | 7770 |  |  | 0
2019-11-20 18:00 | 7771 |  |  | 0
2019-11-20 19:00 | 7772 |  |  | 0
2019-11-20 20:00 | 7773 |  |  | 0
2019-11-20 21:00 | 7774 |  |  | 0
2019-11-20 22:00 | 7775 |  |  | 0
2019-11-20 23:00 | 7776 |  |  | 0
2019-11-21 | 7777 |  |  | 0
2019-11-21 01:00 | 7778 |  |  | 0
2019-11-21 02:00 | 7779 |  |  | 0
2019-11-21 03:00 | 7780 |  |  | 0
2019-11-21 04:00 | 7781 |  |  | 0
2019-11-21 05:00 | 7782 |  |  | 0
2019-11-21 06:00 | 7783 |  |  | 8.3347e-05
2019-11-21 07:00 | 7784 |  |  | 0.0089182
2019-11-21 08:00 | 7785 |  |  | 0.036506
2019-11-21 09:00 | 7786 |  |  | 0.10043
2019-11-21 10:00 | 7787 |  |  | 0.056926
2019-11-21 11:00 | 7788 |  |  | 0.045841
2019-11-21 12:00 | 7789 |  |  | 0.084347
2019-11-21 13:00 | 7790 |  |  | 0.042007
2019-11-21 14:00 | 7791 |  |  | 0.019503
2019-11-21 15:00 | 7792 |  |  | 0.0043341
2019-11-21 16:00 | 7793 |  |  | 0
2019-11-21 17:00 | 7794 |  |  | 0
2019-11-21 18:00 | 7795 |  |  | 0
2019-11-21 19:00 | 7796 |  |  | 0
2019-11-21 20:00 | 7797 |  |  | 0
2019-11-21 21:00 | 7798 |  |  | 0
2019-11-21 22:00 | 7799 |  |  | 0
2019-11-21 23:00 | 7800 |  |  | 0
2019-11-22 | 7801 |  |  | 0
2019-11-22 01:00 | 7802 |  |  | 0
2019-11-22 02:00 | 7803 |  |  | 0
2019-11-22 03:00 | 7804 |  |  | 0
2019-11-22 04:00 | 7805 |  |  | 0
2019-11-22 05:00 | 7806 |  |  | 0
2019-11-22 06:00 | 7807 |  |  | 0
2019-11-22 07:00 | 7808 |  |  | 0.00016669
2019-11-22 08:00 | 7809 |  |  | 0.011419
2019-11-22 09:00 | 7810 |  |  | 0.020337
2019-11-22 10:00 | 7811 |  |  | 0.031922
2019-11-22 11:00 | 7812 |  |  | 0.086598
2019-11-22 12:00 | 7813 |  |  | 0.066928
2019-11-22 13:00 | 7814 |  |  | 0.045924
2019-11-22 14:00 | 7815 |  |  | 0.012335
2019-11-22 15:00 | 7816 |  |  | 0
2019-11-22 16:00 | 7817 |  |  | 0
2019-11-22 17:00 | 7818 |  |  | 0
2019-11-22 18:00 | 7819 |  |  | 0
2019-11-22 19:00 | 7820 |  |  | 0
2019-11-22 20:00 | 7821 |  |  | 0
2019-11-22 21:00 | 7822 |  |  | 0
2019-11-22 22:00 | 7823 |  |  | 0
2019-11-22 23:00 | 7824 |  |  | 0
2019-11-23 | 7825 |  |  | 0
2019-11-23 01:00 | 7826 |  |  | 0
2019-11-23 02:00 | 7827 |  |  | 0
2019-11-23 03:00 | 7828 |  |  | 0
2019-11-23 04:00 | 7829 |  |  | 0
2019-11-23 05:00 | 7830 |  |  | 0
2019-11-23 06:00 | 7831 |  |  | 0
2019-11-23 07:00 | 7832 |  |  | 0.00041674
2019-11-23 08:00 | 7833 |  |  | 0.0041674
2019-11-23 09:00 | 7834 |  |  | 0.011419
2019-11-23 10:00 | 7835 |  |  | 0.0087515
2019-11-23 11:00 | 7836 |  |  | 0.017003
2019-11-23 12:00 | 7837 |  |  | 0.013502
2019-11-23 13:00 | 7838 |  |  | 0.012252
2019-11-23 14:00 | 7839 |  |  | 0.0032505
2019-11-23 15:00 | 7840 |  |  | 0
2019-11-23 16:00 | 7841 |  |  | 0
2019-11-23 17:00 | 7842 |  |  | 0
2019-11-23 18:00 | 7843 |  |  | 0
2019-11-23 19:00 | 7844 |  |  | 0
2019-11-23 20:00 | 7845 |  |  | 0
2019-11-23 21:00 | 7846 |  |  | 0
2019-11-23 22:00 | 7847 |  |  | 0
2019-11-23 23:00 | 7848 |  |  | 0
2019-11-24 | 7849 |  |  | 0
2019-11-24 01:00 | 7850 |  |  | 0
2019-11-24 02:00 | 7851 |  |  | 0
2019-11-24 03:00 | 7852 |  |  | 0
2019-11-24 04:00 | 7853 |  |  | 0
2019-11-24 05:00 | 7854 |  |  | 0
2019-11-24 06:00 | 7855 |  |  | 0
2019-11-24 07:00 | 7856 |  |  | 0.00041674
2019-11-24 08:00 | 7857 |  |  | 0.011585
2019-11-24 09:00 | 7858 |  |  | 0.015253
2019-11-24 10:00 | 7859 |  |  | 0.015003
2019-11-24 11:00 | 7860 |  |  | 0.01792
2019-11-24 12:00 | 7861 |  |  | 0.01792
2019-11-24 13:00 | 7862 |  |  | 0.014252
2019-11-24 14:00 | 7863 |  |  | 0.010002
2019-11-24 15:00 | 7864 |  |  | 0.0013336
2019-11-24 16:00 | 7865 |  |  | 0
2019-11-24 17:00 | 7866 |  |  | 0
2019-11-24 18:00 | 7867 |  |  | 0
2019-11-24 19:00 | 7868 |  |  | 0
2019-11-24 20:00 | 7869 |  |  | 0
2019-11-24 21:00 | 7870 |  |  | 0
2019-11-24 22:00 | 7871 |  |  | 0
2019-11-24 23:00 | 7872 |  |  | 0
2019-11-25 | 7873 |  |  | 0
2019-11-25 01:00 | 7874 |  |  | 0
2019-11-25 02:00 | 7875 |  |  | 0
2019-11-25 03:00 | 7876 |  |  | 0
2019-11-25 04:00 | 7877 |  |  | 0
2019-11-25 05:00 | 7878 |  |  | 0
2019-11-25 06:00 | 7879 |  |  | 8.3347e-05
2019-11-25 07:00 | 7880 |  |  | 0.013086
2019-11-25 08:00 | 7881 |  |  | 0.021254
2019-11-25 09:00 | 7882 |  |  | 0.046174
2019-11-25 10:00 | 7883 |  |  | 0.083097
2019-11-25 11:00 | 7884 |  |  | 0.076013
2019-11-25 12:00 | 7885 |  |  | 0.047175
2019-11-25 13:00 | 7886 |  |  | 0.097683
2019-11-25 14:00 | 7887 |  |  | 0.13069
2019-11-25 15:00 | 7888 |  |  | 0.024171
2019-11-25 16:00 | 7889 |  |  | 0
2019-11-25 17:00 | 7890 |  |  | 0
2019-11-25 18:00 | 7891 |  |  | 0
2019-11-25 19:00 | 7892 |  |  | 0
2019-11-25 20:00 | 7893 |  |  | 0
2019-11-25 21:00 | 7894 |  |  | 0
2019-11-25 22:00 | 7895 |  |  | 0
2019-11-25 23:00 | 7896 |  |  | 0
2019-11-26 | 7897 |  |  | 0
2019-11-26 01:00 | 7898 |  |  | 0
2019-11-26 02:00 | 7899 |  |  | 0
2019-11-26 03:00 | 7900 |  |  | 0
2019-11-26 04:00 | 7901 |  |  | 0
2019-11-26 05:00 | 7902 |  |  | 0
2019-11-26 06:00 | 7903 |  |  | 0.0016669
2019-11-26 07:00 | 7904 |  |  | 0.060093
2019-11-26 08:00 | 7905 |  |  | 0.13877
2019-11-26 09:00 | 7906 |  |  | 0.16594
2019-11-26 10:00 | 7907 |  |  | 0.17828
2019-11-26 11:00 | 7908 |  |  | 0.20162
2019-11-26 12:00 | 7909 |  |  | 0.09835
2019-11-26 13:00 | 7910 |  |  | 0.17936
2019-11-26 14:00 | 7911 |  |  | 0.10327
2019-11-26 15:00 | 7912 |  |  | 0.027421
2019-11-26 16:00 | 7913 |  |  | 0
2019-11-26 17:00 | 7914 |  |  | 0
2019-11-26 18:00 | 7915 |  |  | 0
2019-11-26 19:00 | 7916 |  |  | 0
2019-11-26 20:00 | 7917 |  |  | 0
2019-11-26 21:00 | 7918 |  |  | 0
2019-11-26 22:00 | 7919 |  |  | 0
2019-11-26 23:00 | 7920 |  |  | 0
2019-11-27 | 7921 |  |  | 0
2019-11-27 01:00 | 7922 |  |  | 0
2019-11-27 02:00 | 7923 |  |  | 0
2019-11-27 03:00 | 7924 |  |  | 0
2019-11-27 04:00 | 7925 |  |  | 0
2019-11-27 05:00 | 7926 |  |  | 0
2019-11-27 06:00 | 7927 |  |  | 0
2019-11-27 07:00 | 7928 |  |  | 0.0061677
2019-11-27 08:00 | 7929 |  |  | 0.0090015
2019-11-27 09:00 | 7930 |  |  | 0.094016
2019-11-27 10:00 | 7931 |  |  | 0.23246
2019-11-27 11:00 | 7932 |  |  | 0.34947
2019-11-27 12:00 | 7933 |  |  | 0.18595
2019-11-27 13:00 | 7934 |  |  | 0.07943
2019-11-27 14:00 | 7935 |  |  | 0.040673
2019-11-27 15:00 | 7936 |  |  | 0.0020003
2019-11-27 16:00 | 7937 |  |  | 0
2019-11-27 17:00 | 7938 |  |  | 0
2019-11-27 18:00 | 7939 |  |  | 0
2019-11-27 19:00 | 7940 |  |  | 0
2019-11-27 20:00 | 7941 |  |  | 0
2019-11-27 21:00 | 7942 |  |  | 0
2019-11-27 22:00 | 7943 |  |  | 0
2019-11-27 23:00 | 7944 |  |  | 0
2019-11-28 | 7945 |  |  | 0
2019-11-28 01:00 | 7946 |  |  | 0
2019-11-28 02:00 | 7947 |  |  | 0
2019-11-28 03:00 | 7948 |  |  | 0
2019-11-28 04:00 | 7949 |  |  | 0
2019-11-28 05:00 | 7950 |  |  | 0
2019-11-28 06:00 | 7951 |  |  | 0.00016669
2019-11-28 07:00 | 7952 |  |  | 0.02292
2019-11-28 08:00 | 7953 |  |  | 0.11144
2019-11-28 09:00 | 7954 |  |  | 0.12719
2019-11-28 10:00 | 7955 |  |  | 0.36873
2019-11-28 11:00 | 7956 |  |  | 0.44582
2019-11-28 12:00 | 7957 |  |  | 0.38415
2019-11-28 13:00 | 7958 |  |  | 0.2753
2019-11-28 14:00 | 7959 |  |  | 0.12244
2019-11-28 15:00 | 7960 |  |  | 0.017003
2019-11-28 16:00 | 7961 |  |  | 0
2019-11-28 17:00 | 7962 |  |  | 0
2019-11-28 18:00 | 7963 |  |  | 0
2019-11-28 19:00 | 7964 |  |  | 0
2019-11-28 20:00 | 7965 |  |  | 0
2019-11-28 21:00 | 7966 |  |  | 0
2019-11-28 22:00 | 7967 |  |  | 0
2019-11-28 23:00 | 7968 |  |  | 0
2019-11-29 | 7969 |  |  | 0
2019-11-29 01:00 | 7970 |  |  | 0
2019-11-29 02:00 | 7971 |  |  | 0
2019-11-29 03:00 | 7972 |  |  | 0
2019-11-29 04:00 | 7973 |  |  | 0
2019-11-29 05:00 | 7974 |  |  | 0
2019-11-29 06:00 | 7975 |  |  | 0.00041674
2019-11-29 07:00 | 7976 |  |  | 0.064011
2019-11-29 08:00 | 7977 |  |  | 0.23637
2019-11-29 09:00 | 7978 |  |  | 0.3784
2019-11-29 10:00 | 7979 |  |  | 0.45924
2019-11-29 11:00 | 7980 |  |  | 0.47358
2019-11-29 12:00 | 7981 |  |  | 0.44224
2019-11-29 13:00 | 7982 |  |  | 0.31114
2019-11-29 14:00 | 7983 |  |  | 0.14069
2019-11-29 15:00 | 7984 |  |  | 0.020253
2019-11-29 16:00 | 7985 |  |  | 0
2019-11-29 17:00 | 7986 |  |  | 0
2019-11-29 18:00 | 7987 |  |  | 0
2019-11-29 19:00 | 7988 |  |  | 0
2019-11-29 20:00 | 7989 |  |  | 0
2019-11-29 21:00 | 7990 |  |  | 0
2019-11-29 22:00 | 7991 |  |  | 0
2019-11-29 23:00 | 7992 |  |  | 0
2019-11-30 | 7993 |  |  | 0
2019-11-30 01:00 | 7994 |  |  | 0
2019-11-30 02:00 | 7995 |  |  | 0
2019-11-30 03:00 | 7996 |  |  | 0
2019-11-30 04:00 | 7997 |  |  | 0
2019-11-30 05:00 | 7998 |  |  | 0
2019-11-30 06:00 | 7999 |  |  | 0.00058343
2019-11-30 07:00 | 8000 |  |  | 0.069678
2019-11-30 08:00 | 8001 |  |  | 0.25463
2019-11-30 09:00 | 8002 |  |  | 0.40765
2019-11-30 10:00 | 8003 |  |  | 0.43624
2019-11-30 11:00 | 8004 |  |  | 0.3999
2019-11-30 12:00 | 8005 |  |  | 0.43641
2019-11-30 13:00 | 8006 |  |  | 0.31172
2019-11-30 14:00 | 8007 |  |  | 0.081014
2019-11-30 15:00 | 8008 |  |  | 0.012085
2019-11-30 16:00 | 8009 |  |  | 0
2019-11-30 17:00 | 8010 |  |  | 0
2019-11-30 18:00 | 8011 |  |  | 0
2019-11-30 19:00 | 8012 |  |  | 0
2019-11-30 20:00 | 8013 |  |  | 0
2019-11-30 21:00 | 8014 |  |  | 0
2019-11-30 22:00 | 8015 |  |  | 0
2019-11-30 23:00 | 8016 |  |  | 0
2019-12-01 | 8017 |  |  | 0
2019-12-01 01:00 | 8018 |  |  | 0
2019-12-01 02:00 | 8019 |  |  | 0
2019-12-01 03:00 | 8020 |  |  | 0
2019-12-01 04:00 | 8021 |  |  | 0
2019-12-01 05:00 | 8022 |  |  | 0
2019-12-01 06:00 | 8023 |  |  | 0
2019-12-01 07:00 | 8024 |  |  | 0.0027505
2019-12-01 08:00 | 8025 |  |  | 0.011169
2019-12-01 09:00 | 8026 |  |  | 0.014669
2019-12-01 10:00 | 8027 |  |  | 0.040507
2019-12-01 11:00 | 8028 |  |  | 0.028921
2019-12-01 12:00 | 8029 |  |  | 0.027671
2019-12-01 13:00 | 8030 |  |  | 0.027421
2019-12-01 14:00 | 8031 |  |  | 0.010085
2019-12-01 15:00 | 8032 |  |  | 0.0015836
2019-12-01 16:00 | 8033 |  |  | 0
2019-12-01 17:00 | 8034 |  |  | 0
2019-12-01 18:00 | 8035 |  |  | 0
2019-12-01 19:00 | 8036 |  |  | 0
2019-12-01 20:00 | 8037 |  |  | 0
2019-12-01 21:00 | 8038 |  |  | 0
2019-12-01 22:00 | 8039 |  |  | 0
2019-12-01 23:00 | 8040 |  |  | 0
2019-12-02 | 8041 |  |  | 0
2019-12-02 01:00 | 8042 |  |  | 0
2019-12-02 02:00 | 8043 |  |  | 0
2019-12-02 03:00 | 8044 |  |  | 0
2019-12-02 04:00 | 8045 |  |  | 0
2019-12-02 05:00 | 8046 |  |  | 0
2019-12-02 06:00 | 8047 |  |  | 0
2019-12-02 07:00 | 8048 |  |  | 0.012835
2019-12-02 08:00 | 8049 |  |  | 0.19778
2019-12-02 09:00 | 8050 |  |  | 0.31897
2019-12-02 10:00 | 8051 |  |  | 0.48666
2019-12-02 11:00 | 8052 |  |  | 0.4795
2019-12-02 12:00 | 8053 |  |  | 0.44924
2019-12-02 13:00 | 8054 |  |  | 0.30872
2019-12-02 14:00 | 8055 |  |  | 0.13102
2019-12-02 15:00 | 8056 |  |  | 0.018836
2019-12-02 16:00 | 8057 |  |  | 0
2019-12-02 17:00 | 8058 |  |  | 0
2019-12-02 18:00 | 8059 |  |  | 0
2019-12-02 19:00 | 8060 |  |  | 0
2019-12-02 20:00 | 8061 |  |  | 0
2019-12-02 21:00 | 8062 |  |  | 0
2019-12-02 22:00 | 8063 |  |  | 0
2019-12-02 23:00 | 8064 |  |  | 0
2019-12-03 | 8065 |  |  | 0
2019-12-03 01:00 | 8066 |  |  | 0
2019-12-03 02:00 | 8067 |  |  | 0
2019-12-03 03:00 | 8068 |  |  | 0
2019-12-03 04:00 | 8069 |  |  | 0
2019-12-03 05:00 | 8070 |  |  | 0
2019-12-03 06:00 | 8071 |  |  | 0
2019-12-03 07:00 | 8072 |  |  | 0.005751
2019-12-03 08:00 | 8073 |  |  | 0.02167
2019-12-03 09:00 | 8074 |  |  | 0.04284
2019-12-03 10:00 | 8075 |  |  | 0.035256
2019-12-03 11:00 | 8076 |  |  | 0.055176
2019-12-03 12:00 | 8077 |  |  | 0.041757
2019-12-03 13:00 | 8078 |  |  | 0.02292
2019-12-03 14:00 | 8079 |  |  | 0.022754
2019-12-03 15:00 | 8080 |  |  | 0.0035839
2019-12-03 16:00 | 8081 |  |  | 0
2019-12-03 17:00 | 8082 |  |  | 0
2019-12-03 18:00 | 8083 |  |  | 0
2019-12-03 19:00 | 8084 |  |  | 0
2019-12-03 20:00 | 8085 |  |  | 0
2019-12-03 21:00 | 8086 |  |  | 0
2019-12-03 22:00 | 8087 |  |  | 0
2019-12-03 23:00 | 8088 |  |  | 0
2019-12-04 | 8089 |  |  | 0
2019-12-04 01:00 | 8090 |  |  | 0
2019-12-04 02:00 | 8091 |  |  | 0
2019-12-04 03:00 | 8092 |  |  | 0
2019-12-04 04:00 | 8093 |  |  | 0
2019-12-04 05:00 | 8094 |  |  | 0
2019-12-04 06:00 | 8095 |  |  | 0
2019-12-04 07:00 | 8096 |  |  | 0.0080013
2019-12-04 08:00 | 8097 |  |  | 0.032339
2019-12-04 09:00 | 8098 |  |  | 0.054009
2019-12-04 10:00 | 8099 |  |  | 0.098183
2019-12-04 11:00 | 8100 |  |  | 0.13777
2019-12-04 12:00 | 8101 |  |  | 0.11377
2019-12-04 13:00 | 8102 |  |  | 0.097933
2019-12-04 14:00 | 8103 |  |  | 0.088348
2019-12-04 15:00 | 8104 |  |  | 0.014669
2019-12-04 16:00 | 8105 |  |  | 0
2019-12-04 17:00 | 8106 |  |  | 0
2019-12-04 18:00 | 8107 |  |  | 0
2019-12-04 19:00 | 8108 |  |  | 0
2019-12-04 20:00 | 8109 |  |  | 0
2019-12-04 21:00 | 8110 |  |  | 0
2019-12-04 22:00 | 8111 |  |  | 0
2019-12-04 23:00 | 8112 |  |  | 0
2019-12-05 | 8113 |  |  | 0
2019-12-05 01:00 | 8114 |  |  | 0
2019-12-05 02:00 | 8115 |  |  | 0
2019-12-05 03:00 | 8116 |  |  | 0
2019-12-05 04:00 | 8117 |  |  | 0
2019-12-05 05:00 | 8118 |  |  | 0
2019-12-05 06:00 | 8119 |  |  | 8.3347e-05
2019-12-05 07:00 | 8120 |  |  | 0.050508
2019-12-05 08:00 | 8121 |  |  | 0.1882
2019-12-05 09:00 | 8122 |  |  | 0.23112
2019-12-05 10:00 | 8123 |  |  | 0.36106
2019-12-05 11:00 | 8124 |  |  | 0.39398
2019-12-05 12:00 | 8125 |  |  | 0.36356
2019-12-05 13:00 | 8126 |  |  | 0.23454
2019-12-05 14:00 | 8127 |  |  | 0.082514
2019-12-05 15:00 | 8128 |  |  | 0.015003
2019-12-05 16:00 | 8129 |  |  | 0
2019-12-05 17:00 | 8130 |  |  | 0
2019-12-05 18:00 | 8131 |  |  | 0
2019-12-05 19:00 | 8132 |  |  | 0
2019-12-05 20:00 | 8133 |  |  | 0
2019-12-05 21:00 | 8134 |  |  | 0
2019-12-05 22:00 | 8135 |  |  | 0
2019-12-05 23:00 | 8136 |  |  | 0
2019-12-06 | 8137 |  |  | 0
2019-12-06 01:00 | 8138 |  |  | 0
2019-12-06 02:00 | 8139 |  |  | 0
2019-12-06 03:00 | 8140 |  |  | 0
2019-12-06 04:00 | 8141 |  |  | 0
2019-12-06 05:00 | 8142 |  |  | 0
2019-12-06 06:00 | 8143 |  |  | 0
2019-12-06 07:00 | 8144 |  |  | 0.037756
2019-12-06 08:00 | 8145 |  |  | 0.16236
2019-12-06 09:00 | 8146 |  |  | 0.32614
2019-12-06 10:00 | 8147 |  |  | 0.39982
2019-12-06 11:00 | 8148 |  |  | 0.41882
2019-12-06 12:00 | 8149 |  |  | 0.37973
2019-12-06 13:00 | 8150 |  |  | 0.26929
2019-12-06 14:00 | 8151 |  |  | 0.11794
2019-12-06 15:00 | 8152 |  |  | 0.015169
2019-12-06 16:00 | 8153 |  |  | 0
2019-12-06 17:00 | 8154 |  |  | 0
2019-12-06 18:00 | 8155 |  |  | 0
2019-12-06 19:00 | 8156 |  |  | 0
2019-12-06 20:00 | 8157 |  |  | 0
2019-12-06 21:00 | 8158 |  |  | 0
2019-12-06 22:00 | 8159 |  |  | 0
2019-12-06 23:00 | 8160 |  |  | 0
2019-12-07 | 8161 |  |  | 0
2019-12-07 01:00 | 8162 |  |  | 0
2019-12-07 02:00 | 8163 |  |  | 0
2019-12-07 03:00 | 8164 |  |  | 0
2019-12-07 04:00 | 8165 |  |  | 0
2019-12-07 05:00 | 8166 |  |  | 0
2019-12-07 06:00 | 8167 |  |  | 0.00016669
2019-12-07 07:00 | 8168 |  |  | 0.02042
2019-12-07 08:00 | 8169 |  |  | 0.066344
2019-12-07 09:00 | 8170 |  |  | 0.33914
2019-12-07 10:00 | 8171 |  |  | 0.4294
2019-12-07 11:00 | 8172 |  |  | 0.44574
2019-12-07 12:00 | 8173 |  |  | 0.39965
2019-12-07 13:00 | 8174 |  |  | 0.27121
2019-12-07 14:00 | 8175 |  |  | 0.1111
2019-12-07 15:00 | 8176 |  |  | 0.02017
2019-12-07 16:00 | 8177 |  |  | 0
2019-12-07 17:00 | 8178 |  |  | 0
2019-12-07 18:00 | 8179 |  |  | 0
2019-12-07 19:00 | 8180 |  |  | 0
2019-12-07 20:00 | 8181 |  |  | 0
2019-12-07 21:00 | 8182 |  |  | 0
2019-12-07 22:00 | 8183 |  |  | 0
2019-12-07 23:00 | 8184 |  |  | 0
2019-12-08 | 8185 |  |  | 0
2019-12-08 01:00 | 8186 |  |  | 0
2019-12-08 02:00 | 8187 |  |  | 0
2019-12-08 03:00 | 8188 |  |  | 0
2019-12-08 04:00 | 8189 |  |  | 0
2019-12-08 05:00 | 8190 |  |  | 0
2019-12-08 06:00 | 8191 |  |  | 0
2019-12-08 07:00 | 8192 |  |  | 0.02142
2019-12-08 08:00 | 8193 |  |  | 0.16319
2019-12-08 09:00 | 8194 |  |  | 0.33481
2019-12-08 10:00 | 8195 |  |  | 0.37073
2019-12-08 11:00 | 8196 |  |  | 0.4054
2019-12-08 12:00 | 8197 |  |  | 0.36831
2019-12-08 13:00 | 8198 |  |  | 0.25938
2019-12-08 14:00 | 8199 |  |  | 0.12194
2019-12-08 15:00 | 8200 |  |  | 0.017253
2019-12-08 16:00 | 8201 |  |  | 0
2019-12-08 17:00 | 8202 |  |  | 0
2019-12-08 18:00 | 8203 |  |  | 0
2019-12-08 19:00 | 8204 |  |  | 0
2019-12-08 20:00 | 8205 |  |  | 0
2019-12-08 21:00 | 8206 |  |  | 0
2019-12-08 22:00 | 8207 |  |  | 0
2019-12-08 23:00 | 8208 |  |  | 0
2019-12-09 | 8209 |  |  | 0
2019-12-09 01:00 | 8210 |  |  | 0
2019-12-09 02:00 | 8211 |  |  | 0
2019-12-09 03:00 | 8212 |  |  | 0
2019-12-09 04:00 | 8213 |  |  | 0
2019-12-09 05:00 | 8214 |  |  | 0
2019-12-09 06:00 | 8215 |  |  | 0
2019-12-09 07:00 | 8216 |  |  | 0.039423
2019-12-09 08:00 | 8217 |  |  | 0.18003
2019-12-09 09:00 | 8218 |  |  | 0.33656
2019-12-09 10:00 | 8219 |  |  | 0.42882
2019-12-09 11:00 | 8220 |  |  | 0.45149
2019-12-09 12:00 | 8221 |  |  | 0.37306
2019-12-09 13:00 | 8222 |  |  | 0.29647
2019-12-09 14:00 | 8223 |  |  | 0.1296
2019-12-09 15:00 | 8224 |  |  | 0.015836
2019-12-09 16:00 | 8225 |  |  | 0
2019-12-09 17:00 | 8226 |  |  | 0
2019-12-09 18:00 | 8227 |  |  | 0
2019-12-09 19:00 | 8228 |  |  | 0
2019-12-09 20:00 | 8229 |  |  | 0
2019-12-09 21:00 | 8230 |  |  | 0
2019-12-09 22:00 | 8231 |  |  | 0
2019-12-09 23:00 | 8232 |  |  | 0
2019-12-10 | 8233 |  |  | 0
2019-12-10 01:00 | 8234 |  |  | 0
2019-12-10 02:00 | 8235 |  |  | 0
2019-12-10 03:00 | 8236 |  |  | 0
2019-12-10 04:00 | 8237 |  |  | 0
2019-12-10 05:00 | 8238 |  |  | 0
2019-12-10 06:00 | 8239 |  |  | 0
2019-12-10 07:00 | 8240 |  |  | 0.043507
2019-12-10 08:00 | 8241 |  |  | 0.20628
2019-12-10 09:00 | 8242 |  |  | 0.36948
2019-12-10 10:00 | 8243 |  |  | 0.43616
2019-12-10 11:00 | 8244 |  |  | 0.45333
2019-12-10 12:00 | 8245 |  |  | 0.42232
2019-12-10 13:00 | 8246 |  |  | 0.2923
2019-12-10 14:00 | 8247 |  |  | 0.12652
2019-12-10 15:00 | 8248 |  |  | 0.016753
2019-12-10 16:00 | 8249 |  |  | 0
2019-12-10 17:00 | 8250 |  |  | 0
2019-12-10 18:00 | 8251 |  |  | 0
2019-12-10 19:00 | 8252 |  |  | 0
2019-12-10 20:00 | 8253 |  |  | 0
2019-12-10 21:00 | 8254 |  |  | 0
2019-12-10 22:00 | 8255 |  |  | 0
2019-12-10 23:00 | 8256 |  |  | 0
2019-12-11 | 8257 |  |  | 0
2019-12-11 01:00 | 8258 |  |  | 0
2019-12-11 02:00 | 8259 |  |  | 0
2019-12-11 03:00 | 8260 |  |  | 0
2019-12-11 04:00 | 8261 |  |  | 0
2019-12-11 05:00 | 8262 |  |  | 0
2019-12-11 06:00 | 8263 |  |  | 0.00066678
2019-12-11 07:00 | 8264 |  |  | 0.035589
2019-12-11 08:00 | 8265 |  |  | 0.064927
2019-12-11 09:00 | 8266 |  |  | 0.10802
2019-12-11 10:00 | 8267 |  |  | 0.12927
2019-12-11 11:00 | 8268 |  |  | 0.11435
2019-12-11 12:00 | 8269 |  |  | 0.085514
2019-12-11 13:00 | 8270 |  |  | 0.053592
2019-12-11 14:00 | 8271 |  |  | 0.012919
2019-12-11 15:00 | 8272 |  |  | 0.0015003
2019-12-11 16:00 | 8273 |  |  | 0
2019-12-11 17:00 | 8274 |  |  | 0
2019-12-11 18:00 | 8275 |  |  | 0
2019-12-11 19:00 | 8276 |  |  | 0
2019-12-11 20:00 | 8277 |  |  | 0
2019-12-11 21:00 | 8278 |  |  | 0
2019-12-11 22:00 | 8279 |  |  | 0
2019-12-11 23:00 | 8280 |  |  | 0
2019-12-12 | 8281 |  |  | 0
2019-12-12 01:00 | 8282 |  |  | 0
2019-12-12 02:00 | 8283 |  |  | 0
2019-12-12 03:00 | 8284 |  |  | 0
2019-12-12 04:00 | 8285 |  |  | 0
2019-12-12 05:00 | 8286 |  |  | 0
2019-12-12 06:00 | 8287 |  |  | 0
2019-12-12 07:00 | 8288 |  |  | 0.016836
2019-12-12 08:00 | 8289 |  |  | 0.045674
2019-12-12 09:00 | 8290 |  |  | 0.13186
2019-12-12 10:00 | 8291 |  |  | 0.057593
2019-12-12 11:00 | 8292 |  |  | 0.073679
2019-12-12 12:00 | 8293 |  |  | 0.043424
2019-12-12 13:00 | 8294 |  |  | 0.024337
2019-12-12 14:00 | 8295 |  |  | 0.0083347
2019-12-12 15:00 | 8296 |  |  | 8.3347e-05
2019-12-12 16:00 | 8297 |  |  | 0
2019-12-12 17:00 | 8298 |  |  | 0
2019-12-12 18:00 | 8299 |  |  | 0
2019-12-12 19:00 | 8300 |  |  | 0
2019-12-12 20:00 | 8301 |  |  | 0
2019-12-12 21:00 | 8302 |  |  | 0
2019-12-12 22:00 | 8303 |  |  | 0
2019-12-12 23:00 | 8304 |  |  | 0
2019-12-13 | 8305 |  |  | 0
2019-12-13 01:00 | 8306 |  |  | 0
2019-12-13 02:00 | 8307 |  |  | 0
2019-12-13 03:00 | 8308 |  |  | 0
2019-12-13 04:00 | 8309 |  |  | 0
2019-12-13 05:00 | 8310 |  |  | 0
2019-12-13 06:00 | 8311 |  |  | 0
2019-12-13 07:00 | 8312 |  |  | 0
2019-12-13 08:00 | 8313 |  |  | 0.0045841
2019-12-13 09:00 | 8314 |  |  | 0.016753
2019-12-13 10:00 | 8315 |  |  | 0.039423
2019-12-13 11:00 | 8316 |  |  | 0.12102
2019-12-13 12:00 | 8317 |  |  | 0.17153
2019-12-13 13:00 | 8318 |  |  | 0.081264
2019-12-13 14:00 | 8319 |  |  | 0.062927
2019-12-13 15:00 | 8320 |  |  | 0.011335
2019-12-13 16:00 | 8321 |  |  | 0
2019-12-13 17:00 | 8322 |  |  | 0
2019-12-13 18:00 | 8323 |  |  | 0
2019-12-13 19:00 | 8324 |  |  | 0
2019-12-13 20:00 | 8325 |  |  | 0
2019-12-13 21:00 | 8326 |  |  | 0
2019-12-13 22:00 | 8327 |  |  | 0
2019-12-13 23:00 | 8328 |  |  | 0
2019-12-14 | 8329 |  |  | 0
2019-12-14 01:00 | 8330 |  |  | 0
2019-12-14 02:00 | 8331 |  |  | 0
2019-12-14 03:00 | 8332 |  |  | 0
2019-12-14 04:00 | 8333 |  |  | 0
2019-12-14 05:00 | 8334 |  |  | 0
2019-12-14 06:00 | 8335 |  |  | 8.3347e-05
2019-12-14 07:00 | 8336 |  |  | 0.036673
2019-12-14 08:00 | 8337 |  |  | 0.18986
2019-12-14 09:00 | 8338 |  |  | 0.34981
2019-12-14 10:00 | 8339 |  |  | 0.42907
2019-12-14 11:00 | 8340 |  |  | 0.44649
2019-12-14 12:00 | 8341 |  |  | 0.40665
2019-12-14 13:00 | 8342 |  |  | 0.29455
2019-12-14 14:00 | 8343 |  |  | 0.12352
2019-12-14 15:00 | 8344 |  |  | 0.015669
2019-12-14 16:00 | 8345 |  |  | 0
2019-12-14 17:00 | 8346 |  |  | 0
2019-12-14 18:00 | 8347 |  |  | 0
2019-12-14 19:00 | 8348 |  |  | 0
2019-12-14 20:00 | 8349 |  |  | 0
2019-12-14 21:00 | 8350 |  |  | 0
2019-12-14 22:00 | 8351 |  |  | 0
2019-12-14 23:00 | 8352 |  |  | 0
2019-12-15 | 8353 |  |  | 0
2019-12-15 01:00 | 8354 |  |  | 0
2019-12-15 02:00 | 8355 |  |  | 0
2019-12-15 03:00 | 8356 |  |  | 0
2019-12-15 04:00 | 8357 |  |  | 0
2019-12-15 05:00 | 8358 |  |  | 0
2019-12-15 06:00 | 8359 |  |  | 0
2019-12-15 07:00 | 8360 |  |  | 0.0095016
2019-12-15 08:00 | 8361 |  |  | 0.03834
2019-12-15 09:00 | 8362 |  |  | 0.05951
2019-12-15 10:00 | 8363 |  |  | 0.11077
2019-12-15 11:00 | 8364 |  |  | 0.095849
2019-12-15 12:00 | 8365 |  |  | 0.11535
2019-12-15 13:00 | 8366 |  |  | 0.061427
2019-12-15 14:00 | 8367 |  |  | 0.023254
2019-12-15 15:00 | 8368 |  |  | 0.0023337
2019-12-15 16:00 | 8369 |  |  | 0
2019-12-15 17:00 | 8370 |  |  | 0
2019-12-15 18:00 | 8371 |  |  | 0
2019-12-15 19:00 | 8372 |  |  | 0
2019-12-15 20:00 | 8373 |  |  | 0
2019-12-15 21:00 | 8374 |  |  | 0
2019-12-15 22:00 | 8375 |  |  | 0
2019-12-15 23:00 | 8376 |  |  | 0
2019-12-16 | 8377 |  |  | 0
2019-12-16 01:00 | 8378 |  |  | 0
2019-12-16 02:00 | 8379 |  |  | 0
2019-12-16 03:00 | 8380 |  |  | 0
2019-12-16 04:00 | 8381 |  |  | 0
2019-12-16 05:00 | 8382 |  |  | 0
2019-12-16 06:00 | 8383 |  |  | 0
2019-12-16 07:00 | 8384 |  |  | 0.0035006
2019-12-16 08:00 | 8385 |  |  | 0.04084
2019-12-16 09:00 | 8386 |  |  | 0.052425
2019-12-16 10:00 | 8387 |  |  | 0.098433
2019-12-16 11:00 | 8388 |  |  | 0.11019
2019-12-16 12:00 | 8389 |  |  | 0.05801
2019-12-16 13:00 | 8390 |  |  | 0.032339
2019-12-16 14:00 | 8391 |  |  | 0.0053342
2019-12-16 15:00 | 8392 |  |  | 0
2019-12-16 16:00 | 8393 |  |  | 0
2019-12-16 17:00 | 8394 |  |  | 0
2019-12-16 18:00 | 8395 |  |  | 0
2019-12-16 19:00 | 8396 |  |  | 0
2019-12-16 20:00 | 8397 |  |  | 0
2019-12-16 21:00 | 8398 |  |  | 0
2019-12-16 22:00 | 8399 |  |  | 0
2019-12-16 23:00 | 8400 |  |  | 0
2019-12-17 | 8401 |  |  | 0
2019-12-17 01:00 | 8402 |  |  | 0
2019-12-17 02:00 | 8403 |  |  | 0
2019-12-17 03:00 | 8404 |  |  | 0
2019-12-17 04:00 | 8405 |  |  | 0
2019-12-17 05:00 | 8406 |  |  | 0
2019-12-17 06:00 | 8407 |  |  | 0
2019-12-17 07:00 | 8408 |  |  | 0
2019-12-17 08:00 | 8409 |  |  | 0.0033339
2019-12-17 09:00 | 8410 |  |  | 0.0048341
2019-12-17 10:00 | 8411 |  |  | 0.0090848
2019-12-17 11:00 | 8412 |  |  | 0.017836
2019-12-17 12:00 | 8413 |  |  | 0.032005
2019-12-17 13:00 | 8414 |  |  | 0.021587
2019-12-17 14:00 | 8415 |  |  | 0.0087515
2019-12-17 15:00 | 8416 |  |  | 8.3347e-05
2019-12-17 16:00 | 8417 |  |  | 0
2019-12-17 17:00 | 8418 |  |  | 0
2019-12-17 18:00 | 8419 |  |  | 0
2019-12-17 19:00 | 8420 |  |  | 0
2019-12-17 20:00 | 8421 |  |  | 0
2019-12-17 21:00 | 8422 |  |  | 0
2019-12-17 22:00 | 8423 |  |  | 0
2019-12-17 23:00 | 8424 |  |  | 0
2019-12-18 | 8425 |  |  | 0
2019-12-18 01:00 | 8426 |  |  | 0
2019-12-18 02:00 | 8427 |  |  | 0
2019-12-18 03:00 | 8428 |  |  | 0
2019-12-18 04:00 | 8429 |  |  | 0
2019-12-18 05:00 | 8430 |  |  | 0
2019-12-18 06:00 | 8431 |  |  | 0
2019-12-18 07:00 | 8432 |  |  | 0
2019-12-18 08:00 | 8433 |  |  | 0.0084181
2019-12-18 09:00 | 8434 |  |  | 0.010002
2019-12-18 10:00 | 8435 |  |  | 0.02217
2019-12-18 11:00 | 8436 |  |  | 0.019837
2019-12-18 12:00 | 8437 |  |  | 0.016169
2019-12-18 13:00 | 8438 |  |  | 0.006251
2019-12-18 14:00 | 8439 |  |  | 0.0015003
2019-12-18 15:00 | 8440 |  |  | 8.3347e-05
2019-12-18 16:00 | 8441 |  |  | 0
2019-12-18 17:00 | 8442 |  |  | 0
2019-12-18 18:00 | 8443 |  |  | 0
2019-12-18 19:00 | 8444 |  |  | 0
2019-12-18 20:00 | 8445 |  |  | 0
2019-12-18 21:00 | 8446 |  |  | 0
2019-12-18 22:00 | 8447 |  |  | 0
2019-12-18 23:00 | 8448 |  |  | 0
2019-12-19 | 8449 |  |  | 0
2019-12-19 01:00 | 8450 |  |  | 0
2019-12-19 02:00 | 8451 |  |  | 0
2019-12-19 03:00 | 8452 |  |  | 0
2019-12-19 04:00 | 8453 |  |  | 0
2019-12-19 05:00 | 8454 |  |  | 0
2019-12-19 06:00 | 8455 |  |  | 0
2019-12-19 07:00 | 8456 |  |  | 0.0014169
2019-12-19 08:00 | 8457 |  |  | 0.005751
2019-12-19 09:00 | 8458 |  |  | 0.011502
2019-12-19 10:00 | 8459 |  |  | 0.012085
2019-12-19 11:00 | 8460 |  |  | 0.030838
2019-12-19 12:00 | 8461 |  |  | 0.025088
2019-12-19 13:00 | 8462 |  |  | 0.033589
2019-12-19 14:00 | 8463 |  |  | 0.011502
2019-12-19 15:00 | 8464 |  |  | 8.3347e-05
2019-12-19 16:00 | 8465 |  |  | 0
2019-12-19 17:00 | 8466 |  |  | 0
2019-12-19 18:00 | 8467 |  |  | 0
2019-12-19 19:00 | 8468 |  |  | 0
2019-12-19 20:00 | 8469 |  |  | 0
2019-12-19 21:00 | 8470 |  |  | 0
2019-12-19 22:00 | 8471 |  |  | 0
2019-12-19 23:00 | 8472 |  |  | 0
2019-12-20 | 8473 |  |  | 0
2019-12-20 01:00 | 8474 |  |  | 0
2019-12-20 02:00 | 8475 |  |  | 0
2019-12-20 03:00 | 8476 |  |  | 0
2019-12-20 04:00 | 8477 |  |  | 0
2019-12-20 05:00 | 8478 |  |  | 0
2019-12-20 06:00 | 8479 |  |  | 0
2019-12-20 07:00 | 8480 |  |  | 0
2019-12-20 08:00 | 8481 |  |  | 0.0020003
2019-12-20 09:00 | 8482 |  |  | 0.012419
2019-12-20 10:00 | 8483 |  |  | 0.018503
2019-12-20 11:00 | 8484 |  |  | 0.013669
2019-12-20 12:00 | 8485 |  |  | 0.012919
2019-12-20 13:00 | 8486 |  |  | 0.0044174
2019-12-20 14:00 | 8487 |  |  | 0.0023337
2019-12-20 15:00 | 8488 |  |  | 0.0017503
2019-12-20 16:00 | 8489 |  |  | 0
2019-12-20 17:00 | 8490 |  |  | 0
2019-12-20 18:00 | 8491 |  |  | 0
2019-12-20 19:00 | 8492 |  |  | 0
2019-12-20 20:00 | 8493 |  |  | 0
2019-12-20 21:00 | 8494 |  |  | 0
2019-12-20 22:00 | 8495 |  |  | 0
2019-12-20 23:00 | 8496 |  |  | 0
2019-12-21 | 8497 |  |  | 0
2019-12-21 01:00 | 8498 |  |  | 0
2019-12-21 02:00 | 8499 |  |  | 0
2019-12-21 03:00 | 8500 |  |  | 0
2019-12-21 04:00 | 8501 |  |  | 0
2019-12-21 05:00 | 8502 |  |  | 0
2019-12-21 06:00 | 8503 |  |  | 0
2019-12-21 07:00 | 8504 |  |  | 0.020587
2019-12-21 08:00 | 8505 |  |  | 0.14902
2019-12-21 09:00 | 8506 |  |  | 0.29138
2019-12-21 10:00 | 8507 |  |  | 0.40782
2019-12-21 11:00 | 8508 |  |  | 0.44566
2019-12-21 12:00 | 8509 |  |  | 0.40857
2019-12-21 13:00 | 8510 |  |  | 0.29397
2019-12-21 14:00 | 8511 |  |  | 0.13311
2019-12-21 15:00 | 8512 |  |  | 0.014086
2019-12-21 16:00 | 8513 |  |  | 0
2019-12-21 17:00 | 8514 |  |  | 0
2019-12-21 18:00 | 8515 |  |  | 0
2019-12-21 19:00 | 8516 |  |  | 0
2019-12-21 20:00 | 8517 |  |  | 0
2019-12-21 21:00 | 8518 |  |  | 0
2019-12-21 22:00 | 8519 |  |  | 0
2019-12-21 23:00 | 8520 |  |  | 0
2019-12-22 | 8521 |  |  | 0
2019-12-22 01:00 | 8522 |  |  | 0
2019-12-22 02:00 | 8523 |  |  | 0
2019-12-22 03:00 | 8524 |  |  | 0
2019-12-22 04:00 | 8525 |  |  | 0
2019-12-22 05:00 | 8526 |  |  | 0
2019-12-22 06:00 | 8527 |  |  | 0
2019-12-22 07:00 | 8528 |  |  | 0.014836
2019-12-22 08:00 | 8529 |  |  | 0.1732
2019-12-22 09:00 | 8530 |  |  | 0.32697
2019-12-22 10:00 | 8531 |  |  | 0.42432
2019-12-22 11:00 | 8532 |  |  | 0.46474
2019-12-22 12:00 | 8533 |  |  | 0.41932
2019-12-22 13:00 | 8534 |  |  | 0.31205
2019-12-22 14:00 | 8535 |  |  | 0.13986
2019-12-22 15:00 | 8536 |  |  | 0.02092
2019-12-22 16:00 | 8537 |  |  | 0
2019-12-22 17:00 | 8538 |  |  | 0
2019-12-22 18:00 | 8539 |  |  | 0
2019-12-22 19:00 | 8540 |  |  | 0
2019-12-22 20:00 | 8541 |  |  | 0
2019-12-22 21:00 | 8542 |  |  | 0
2019-12-22 22:00 | 8543 |  |  | 0
2019-12-22 23:00 | 8544 |  |  | 0
2019-12-23 | 8545 |  |  | 0
2019-12-23 01:00 | 8546 |  |  | 0
2019-12-23 02:00 | 8547 |  |  | 0
2019-12-23 03:00 | 8548 |  |  | 0
2019-12-23 04:00 | 8549 |  |  | 0
2019-12-23 05:00 | 8550 |  |  | 0
2019-12-23 06:00 | 8551 |  |  | 0
2019-12-23 07:00 | 8552 |  |  | 0.027671
2019-12-23 08:00 | 8553 |  |  | 0.18411
2019-12-23 09:00 | 8554 |  |  | 0.34656
2019-12-23 10:00 | 8555 |  |  | 0.44282
2019-12-23 11:00 | 8556 |  |  | 0.483
2019-12-23 12:00 | 8557 |  |  | 0.43816
2019-12-23 13:00 | 8558 |  |  | 0.31814
2019-12-23 14:00 | 8559 |  |  | 0.14294
2019-12-23 15:00 | 8560 |  |  | 0.02092
2019-12-23 16:00 | 8561 |  |  | 0
2019-12-23 17:00 | 8562 |  |  | 0
2019-12-23 18:00 | 8563 |  |  | 0
2019-12-23 19:00 | 8564 |  |  | 0
2019-12-23 20:00 | 8565 |  |  | 0
2019-12-23 21:00 | 8566 |  |  | 0
2019-12-23 22:00 | 8567 |  |  | 0
2019-12-23 23:00 | 8568 |  |  | 0
2019-12-24 | 8569 |  |  | 0
2019-12-24 01:00 | 8570 |  |  | 0
2019-12-24 02:00 | 8571 |  |  | 0
2019-12-24 03:00 | 8572 |  |  | 0
2019-12-24 04:00 | 8573 |  |  | 0
2019-12-24 05:00 | 8574 |  |  | 0
2019-12-24 06:00 | 8575 |  |  | 0
2019-12-24 07:00 | 8576 |  |  | 0.027421
2019-12-24 08:00 | 8577 |  |  | 0.17753
2019-12-24 09:00 | 8578 |  |  | 0.3058
2019-12-24 10:00 | 8579 |  |  | 0.41032
2019-12-24 11:00 | 8580 |  |  | 0.39882
2019-12-24 12:00 | 8581 |  |  | 0.17961
2019-12-24 13:00 | 8582 |  |  | 0.30905
2019-12-24 14:00 | 8583 |  |  | 0.12819
2019-12-24 15:00 | 8584 |  |  | 0.019087
2019-12-24 16:00 | 8585 |  |  | 0
2019-12-24 17:00 | 8586 |  |  | 0
2019-12-24 18:00 | 8587 |  |  | 0
2019-12-24 19:00 | 8588 |  |  | 0
2019-12-24 20:00 | 8589 |  |  | 0
2019-12-24 21:00 | 8590 |  |  | 0
2019-12-24 22:00 | 8591 |  |  | 0
2019-12-24 23:00 | 8592 |  |  | 0
2019-12-25 | 8593 |  |  | 0
2019-12-25 01:00 | 8594 |  |  | 0
2019-12-25 02:00 | 8595 |  |  | 0
2019-12-25 03:00 | 8596 |  |  | 0
2019-12-25 04:00 | 8597 |  |  | 0
2019-12-25 05:00 | 8598 |  |  | 0
2019-12-25 06:00 | 8599 |  |  | 0
2019-12-25 07:00 | 8600 |  |  | 0.026671
2019-12-25 08:00 | 8601 |  |  | 0.18278
2019-12-25 09:00 | 8602 |  |  | 0.34147
2019-12-25 10:00 | 8603 |  |  | 0.42499
2019-12-25 11:00 | 8604 |  |  | 0.46016
2019-12-25 12:00 | 8605 |  |  | 0.42315
2019-12-25 13:00 | 8606 |  |  | 0.30372
2019-12-25 14:00 | 8607 |  |  | 0.14011
2019-12-25 15:00 | 8608 |  |  | 0.021754
2019-12-25 16:00 | 8609 |  |  | 0
2019-12-25 17:00 | 8610 |  |  | 0
2019-12-25 18:00 | 8611 |  |  | 0
2019-12-25 19:00 | 8612 |  |  | 0
2019-12-25 20:00 | 8613 |  |  | 0
2019-12-25 21:00 | 8614 |  |  | 0
2019-12-25 22:00 | 8615 |  |  | 0
2019-12-25 23:00 | 8616 |  |  | 0
2019-12-26 | 8617 |  |  | 0
2019-12-26 01:00 | 8618 |  |  | 0
2019-12-26 02:00 | 8619 |  |  | 0
2019-12-26 03:00 | 8620 |  |  | 0
2019-12-26 04:00 | 8621 |  |  | 0
2019-12-26 05:00 | 8622 |  |  | 0
2019-12-26 06:00 | 8623 |  |  | 0
2019-12-26 07:00 | 8624 |  |  | 0.013752
2019-12-26 08:00 | 8625 |  |  | 0.1211
2019-12-26 09:00 | 8626 |  |  | 0.24329
2019-12-26 10:00 | 8627 |  |  | 0.27921
2019-12-26 11:00 | 8628 |  |  | 0.23596
2019-12-26 12:00 | 8629 |  |  | 0.11419
2019-12-26 13:00 | 8630 |  |  | 0.15953
2019-12-26 14:00 | 8631 |  |  | 0.14727
2019-12-26 15:00 | 8632 |  |  | 0.024004
2019-12-26 16:00 | 8633 |  |  | 0
2019-12-26 17:00 | 8634 |  |  | 0
2019-12-26 18:00 | 8635 |  |  | 0
2019-12-26 19:00 | 8636 |  |  | 0
2019-12-26 20:00 | 8637 |  |  | 0
2019-12-26 21:00 | 8638 |  |  | 0
2019-12-26 22:00 | 8639 |  |  | 0
2019-12-26 23:00 | 8640 |  |  | 0
2019-12-27 | 8641 |  |  | 0
2019-12-27 01:00 | 8642 |  |  | 0
2019-12-27 02:00 | 8643 |  |  | 0
2019-12-27 03:00 | 8644 |  |  | 0
2019-12-27 04:00 | 8645 |  |  | 0
2019-12-27 05:00 | 8646 |  |  | 0
2019-12-27 06:00 | 8647 |  |  | 0
2019-12-27 07:00 | 8648 |  |  | 0.022004
2019-12-27 08:00 | 8649 |  |  | 0.16761
2019-12-27 09:00 | 8650 |  |  | 0.1962
2019-12-27 10:00 | 8651 |  |  | 0.34447
2019-12-27 11:00 | 8652 |  |  | 0.42774
2019-12-27 12:00 | 8653 |  |  | 0.37823
2019-12-27 13:00 | 8654 |  |  | 0.2848
2019-12-27 14:00 | 8655 |  |  | 0.13494
2019-12-27 15:00 | 8656 |  |  | 0.022254
2019-12-27 16:00 | 8657 |  |  | 0
2019-12-27 17:00 | 8658 |  |  | 0
2019-12-27 18:00 | 8659 |  |  | 0
2019-12-27 19:00 | 8660 |  |  | 0
2019-12-27 20:00 | 8661 |  |  | 0
2019-12-27 21:00 | 8662 |  |  | 0
2019-12-27 22:00 | 8663 |  |  | 0
2019-12-27 23:00 | 8664 |  |  | 0
2019-12-28 | 8665 |  |  | 0
2019-12-28 01:00 | 8666 |  |  | 0
2019-12-28 02:00 | 8667 |  |  | 0
2019-12-28 03:00 | 8668 |  |  | 0
2019-12-28 04:00 | 8669 |  |  | 0
2019-12-28 05:00 | 8670 |  |  | 0
2019-12-28 06:00 | 8671 |  |  | 0
2019-12-28 07:00 | 8672 |  |  | 0.020753
2019-12-28 08:00 | 8673 |  |  | 0.14552
2019-12-28 09:00 | 8674 |  |  | 0.28755
2019-12-28 10:00 | 8675 |  |  | 0.38406
2019-12-28 11:00 | 8676 |  |  | 0.40515
2019-12-28 12:00 | 8677 |  |  | 0.38181
2019-12-28 13:00 | 8678 |  |  | 0.27046
2019-12-28 14:00 | 8679 |  |  | 0.12294
2019-12-28 15:00 | 8680 |  |  | 0.019087
2019-12-28 16:00 | 8681 |  |  | 0
2019-12-28 17:00 | 8682 |  |  | 0
2019-12-28 18:00 | 8683 |  |  | 0
2019-12-28 19:00 | 8684 |  |  | 0
2019-12-28 20:00 | 8685 |  |  | 0
2019-12-28 21:00 | 8686 |  |  | 0
2019-12-28 22:00 | 8687 |  |  | 0
2019-12-28 23:00 | 8688 |  |  | 0
2019-12-29 | 8689 |  |  | 0
2019-12-29 01:00 | 8690 |  |  | 0
2019-12-29 02:00 | 8691 |  |  | 0
2019-12-29 03:00 | 8692 |  |  | 0
2019-12-29 04:00 | 8693 |  |  | 0
2019-12-29 05:00 | 8694 |  |  | 0
2019-12-29 06:00 | 8695 |  |  | 0
2019-12-29 07:00 | 8696 |  |  | 0.0024171
2019-12-29 08:00 | 8697 |  |  | 0.022837
2019-12-29 09:00 | 8698 |  |  | 0.065511
2019-12-29 10:00 | 8699 |  |  | 0.099933
2019-12-29 11:00 | 8700 |  |  | 0.1867
2019-12-29 12:00 | 8701 |  |  | 0.34481
2019-12-29 13:00 | 8702 |  |  | 0.26379
2019-12-29 14:00 | 8703 |  |  | 0.11769
2019-12-29 15:00 | 8704 |  |  | 0.01967
2019-12-29 16:00 | 8705 |  |  | 0
2019-12-29 17:00 | 8706 |  |  | 0
2019-12-29 18:00 | 8707 |  |  | 0
2019-12-29 19:00 | 8708 |  |  | 0
2019-12-29 20:00 | 8709 |  |  | 0
2019-12-29 21:00 | 8710 |  |  | 0
2019-12-29 22:00 | 8711 |  |  | 0
2019-12-29 23:00 | 8712 |  |  | 0
2019-12-30 | 8713 |  |  | 0
2019-12-30 01:00 | 8714 |  |  | 0
2019-12-30 02:00 | 8715 |  |  | 0
2019-12-30 03:00 | 8716 |  |  | 0
2019-12-30 04:00 | 8717 |  |  | 0
2019-12-30 05:00 | 8718 |  |  | 0
2019-12-30 06:00 | 8719 |  |  | 0
2019-12-30 07:00 | 8720 |  |  | 0
2019-12-30 08:00 | 8721 |  |  | 0.0052509
2019-12-30 09:00 | 8722 |  |  | 0.014752
2019-12-30 10:00 | 8723 |  |  | 0.023004
2019-12-30 11:00 | 8724 |  |  | 0.034006
2019-12-30 12:00 | 8725 |  |  | 0.053842
2019-12-30 13:00 | 8726 |  |  | 0.046258
2019-12-30 14:00 | 8727 |  |  | 0.021587
2019-12-30 15:00 | 8728 |  |  | 0.0050008
2019-12-30 16:00 | 8729 |  |  | 0
2019-12-30 17:00 | 8730 |  |  | 0
2019-12-30 18:00 | 8731 |  |  | 0
2019-12-30 19:00 | 8732 |  |  | 0
2019-12-30 20:00 | 8733 |  |  | 0
2019-12-30 21:00 | 8734 |  |  | 0
2019-12-30 22:00 | 8735 |  |  | 0
2019-12-30 23:00 | 8736 |  |  | 0
2019-12-31 | 8737 |  |  | 0
2019-12-31 01:00 | 8738 |  |  | 0
2019-12-31 02:00 | 8739 |  |  | 0
2019-12-31 03:00 | 8740 |  |  | 0
2019-12-31 04:00 | 8741 |  |  | 0
2019-12-31 05:00 | 8742 |  |  | 0
2019-12-31 06:00 | 8743 |  |  | 0
2019-12-31 07:00 | 8744 |  |  | 0.011085
2019-12-31 08:00 | 8745 |  |  | 0.11644
2019-12-31 09:00 | 8746 |  |  | 0.31555
2019-12-31 10:00 | 8747 |  |  | 0.4214
2019-12-31 11:00 | 8748 |  |  | 0.43616
2019-12-31 12:00 | 8749 |  |  | 0.39048
2019-12-31 13:00 | 8750 |  |  | 0.29047
2019-12-31 14:00 | 8751 |  |  | 0.13969
2019-12-31 15:00 | 8752 |  |  | 0.032089
2019-12-31 16:00 | 8753 |  |  | 0
2019-12-31 17:00 | 8754 |  |  | 0
2019-12-31 18:00 | 8755 |  |  | 0
2019-12-31 19:00 | 8756 |  |  | 0
2019-12-31 20:00 | 8757 |  |  | 0
2019-12-31 21:00 | 8758 |  |  | 0
2019-12-31 22:00 | 8759 |  |  | 0
2019-12-31 23:00 | 8760 |  |  | 0

## Clear sky day
Timeserie | DATE_TIME | Hour of the year | Turin2019 PV-MEAS_high_resolution
1 | 2019-03-30 | 2113 | 0
2 | 2019-03-30 00:01 | 2113 | 0
3 | 2019-03-30 00:02 | 2113 | 0
4 | 2019-03-30 00:03 | 2113 | 0
5 | 2019-03-30 00:04 | 2113 | 0
6 | 2019-03-30 00:05 | 2113 | 0
7 | 2019-03-30 00:06 | 2113 | 0
8 | 2019-03-30 00:07 | 2113 | 0
9 | 2019-03-30 00:08 | 2113 | 0
10 | 2019-03-30 00:09 | 2113 | 0
11 | 2019-03-30 00:10 | 2113 | 0
12 | 2019-03-30 00:11 | 2113 | 0
13 | 2019-03-30 00:12 | 2113 | 0
14 | 2019-03-30 00:13 | 2113 | 0
15 | 2019-03-30 00:14 | 2113 | 0
16 | 2019-03-30 00:15 | 2113 | 0
17 | 2019-03-30 00:16 | 2113 | 0
18 | 2019-03-30 00:17 | 2113 | 0
19 | 2019-03-30 00:18 | 2113 | 0
20 | 2019-03-30 00:19 | 2113 | 0
21 | 2019-03-30 00:20 | 2113 | 0
22 | 2019-03-30 00:21 | 2113 | 0
23 | 2019-03-30 00:22 | 2113 | 0
24 | 2019-03-30 00:23 | 2113 | 0
25 | 2019-03-30 00:24 | 2113 | 0
26 | 2019-03-30 00:25 | 2113 | 0
27 | 2019-03-30 00:26 | 2113 | 0
28 | 2019-03-30 00:27 | 2113 | 0
29 | 2019-03-30 00:28 | 2113 | 0
30 | 2019-03-30 00:29 | 2113 | 0
31 | 2019-03-30 00:30 | 2113 | 0
32 | 2019-03-30 00:31 | 2113 | 0
33 | 2019-03-30 00:32 | 2113 | 0
34 | 2019-03-30 00:33 | 2113 | 0
35 | 2019-03-30 00:34 | 2113 | 0
36 | 2019-03-30 00:35 | 2113 | 0
37 | 2019-03-30 00:36 | 2113 | 0
38 | 2019-03-30 00:37 | 2113 | 0
39 | 2019-03-30 00:38 | 2113 | 0
40 | 2019-03-30 00:39 | 2113 | 0
41 | 2019-03-30 00:40 | 2113 | 0
42 | 2019-03-30 00:41 | 2113 | 0
43 | 2019-03-30 00:42 | 2113 | 0
44 | 2019-03-30 00:43 | 2113 | 0
45 | 2019-03-30 00:44 | 2113 | 0
46 | 2019-03-30 00:45 | 2113 | 0
47 | 2019-03-30 00:46 | 2113 | 0
48 | 2019-03-30 00:47 | 2113 | 0
49 | 2019-03-30 00:48 | 2113 | 0
50 | 2019-03-30 00:49 | 2113 | 0
51 | 2019-03-30 00:50 | 2113 | 0
52 | 2019-03-30 00:51 | 2113 | 0
53 | 2019-03-30 00:52 | 2113 | 0
54 | 2019-03-30 00:53 | 2113 | 0
55 | 2019-03-30 00:54 | 2113 | 0
56 | 2019-03-30 00:55 | 2113 | 0
57 | 2019-03-30 00:56 | 2113 | 0
58 | 2019-03-30 00:57 | 2113 | 0
59 | 2019-03-30 00:58 | 2113 | 0
60 | 2019-03-30 00:59 | 2113 | 0
61 | 2019-03-30 01:00 | 2114 | 0
62 | 2019-03-30 01:01 | 2114 | 0
63 | 2019-03-30 01:02 | 2114 | 0
64 | 2019-03-30 01:03 | 2114 | 0
65 | 2019-03-30 01:04 | 2114 | 0
66 | 2019-03-30 01:05 | 2114 | 0
67 | 2019-03-30 01:06 | 2114 | 0
68 | 2019-03-30 01:07 | 2114 | 0
69 | 2019-03-30 01:08 | 2114 | 0
70 | 2019-03-30 01:09 | 2114 | 0
71 | 2019-03-30 01:10 | 2114 | 0
72 | 2019-03-30 01:11 | 2114 | 0
73 | 2019-03-30 01:12 | 2114 | 0
74 | 2019-03-30 01:13 | 2114 | 0
75 | 2019-03-30 01:14 | 2114 | 0
76 | 2019-03-30 01:15 | 2114 | 0
77 | 2019-03-30 01:16 | 2114 | 0
78 | 2019-03-30 01:17 | 2114 | 0
79 | 2019-03-30 01:18 | 2114 | 0
80 | 2019-03-30 01:19 | 2114 | 0
81 | 2019-03-30 01:20 | 2114 | 0
82 | 2019-03-30 01:21 | 2114 | 0
83 | 2019-03-30 01:22 | 2114 | 0
84 | 2019-03-30 01:23 | 2114 | 0
85 | 2019-03-30 01:24 | 2114 | 0
86 | 2019-03-30 01:25 | 2114 | 0
87 | 2019-03-30 01:26 | 2114 | 0
88 | 2019-03-30 01:27 | 2114 | 0
89 | 2019-03-30 01:28 | 2114 | 0
90 | 2019-03-30 01:29 | 2114 | 0
91 | 2019-03-30 01:30 | 2114 | 0
92 | 2019-03-30 01:31 | 2114 | 0
93 | 2019-03-30 01:32 | 2114 | 0
94 | 2019-03-30 01:33 | 2114 | 0
95 | 2019-03-30 01:34 | 2114 | 0
96 | 2019-03-30 01:35 | 2114 | 0
97 | 2019-03-30 01:36 | 2114 | 0
98 | 2019-03-30 01:37 | 2114 | 0
99 | 2019-03-30 01:38 | 2114 | 0
100 | 2019-03-30 01:39 | 2114 | 0
101 | 2019-03-30 01:40 | 2114 | 0
102 | 2019-03-30 01:41 | 2114 | 0
103 | 2019-03-30 01:42 | 2114 | 0
104 | 2019-03-30 01:43 | 2114 | 0
105 | 2019-03-30 01:44 | 2114 | 0
106 | 2019-03-30 01:45 | 2114 | 0
107 | 2019-03-30 01:46 | 2114 | 0
108 | 2019-03-30 01:47 | 2114 | 0
109 | 2019-03-30 01:48 | 2114 | 0
110 | 2019-03-30 01:49 | 2114 | 0
111 | 2019-03-30 01:50 | 2114 | 0
112 | 2019-03-30 01:51 | 2114 | 0
113 | 2019-03-30 01:52 | 2114 | 0
114 | 2019-03-30 01:53 | 2114 | 0
115 | 2019-03-30 01:54 | 2114 | 0
116 | 2019-03-30 01:55 | 2114 | 0
117 | 2019-03-30 01:56 | 2114 | 0
118 | 2019-03-30 01:57 | 2114 | 0
119 | 2019-03-30 01:58 | 2114 | 0
120 | 2019-03-30 01:59 | 2114 | 0
121 | 2019-03-30 02:00 | 2114 | 0
122 | 2019-03-30 02:01 | 2115 | 0
123 | 2019-03-30 02:02 | 2115 | 0
124 | 2019-03-30 02:03 | 2115 | 0
125 | 2019-03-30 02:04 | 2115 | 0
126 | 2019-03-30 02:05 | 2115 | 0
127 | 2019-03-30 02:06 | 2115 | 0
128 | 2019-03-30 02:07 | 2115 | 0
129 | 2019-03-30 02:08 | 2115 | 0
130 | 2019-03-30 02:09 | 2115 | 0
131 | 2019-03-30 02:10 | 2115 | 0
132 | 2019-03-30 02:11 | 2115 | 0
133 | 2019-03-30 02:12 | 2115 | 0
134 | 2019-03-30 02:13 | 2115 | 0
135 | 2019-03-30 02:14 | 2115 | 0
136 | 2019-03-30 02:15 | 2115 | 0
137 | 2019-03-30 02:16 | 2115 | 0
138 | 2019-03-30 02:17 | 2115 | 0
139 | 2019-03-30 02:18 | 2115 | 0
140 | 2019-03-30 02:19 | 2115 | 0
141 | 2019-03-30 02:20 | 2115 | 0
142 | 2019-03-30 02:21 | 2115 | 0
143 | 2019-03-30 02:22 | 2115 | 0
144 | 2019-03-30 02:23 | 2115 | 0
145 | 2019-03-30 02:24 | 2115 | 0
146 | 2019-03-30 02:25 | 2115 | 0
147 | 2019-03-30 02:26 | 2115 | 0
148 | 2019-03-30 02:27 | 2115 | 0
149 | 2019-03-30 02:28 | 2115 | 0
150 | 2019-03-30 02:29 | 2115 | 0
151 | 2019-03-30 02:30 | 2115 | 0
152 | 2019-03-30 02:31 | 2115 | 0
153 | 2019-03-30 02:32 | 2115 | 0
154 | 2019-03-30 02:33 | 2115 | 0
155 | 2019-03-30 02:34 | 2115 | 0
156 | 2019-03-30 02:35 | 2115 | 0
157 | 2019-03-30 02:36 | 2115 | 0
158 | 2019-03-30 02:37 | 2115 | 0
159 | 2019-03-30 02:38 | 2115 | 0
160 | 2019-03-30 02:39 | 2115 | 0
161 | 2019-03-30 02:40 | 2115 | 0
162 | 2019-03-30 02:41 | 2115 | 0
163 | 2019-03-30 02:42 | 2115 | 0
164 | 2019-03-30 02:43 | 2115 | 0
165 | 2019-03-30 02:44 | 2115 | 0
166 | 2019-03-30 02:45 | 2115 | 0
167 | 2019-03-30 02:46 | 2115 | 0
168 | 2019-03-30 02:47 | 2115 | 0
169 | 2019-03-30 02:48 | 2115 | 0
170 | 2019-03-30 02:49 | 2115 | 0
171 | 2019-03-30 02:50 | 2115 | 0
172 | 2019-03-30 02:51 | 2115 | 0
173 | 2019-03-30 02:52 | 2115 | 0
174 | 2019-03-30 02:53 | 2115 | 0
175 | 2019-03-30 02:54 | 2115 | 0
176 | 2019-03-30 02:55 | 2115 | 0
177 | 2019-03-30 02:56 | 2115 | 0
178 | 2019-03-30 02:57 | 2115 | 0
179 | 2019-03-30 02:58 | 2115 | 0
180 | 2019-03-30 02:59 | 2115 | 0
181 | 2019-03-30 03:00 | 2116 | 0
182 | 2019-03-30 03:01 | 2116 | 0
183 | 2019-03-30 03:02 | 2116 | 0
184 | 2019-03-30 03:03 | 2116 | 0
185 | 2019-03-30 03:04 | 2116 | 0
186 | 2019-03-30 03:05 | 2116 | 0
187 | 2019-03-30 03:06 | 2116 | 0
188 | 2019-03-30 03:07 | 2116 | 0
189 | 2019-03-30 03:08 | 2116 | 0
190 | 2019-03-30 03:09 | 2116 | 0
191 | 2019-03-30 03:10 | 2116 | 0
192 | 2019-03-30 03:11 | 2116 | 0
193 | 2019-03-30 03:12 | 2116 | 0
194 | 2019-03-30 03:13 | 2116 | 0
195 | 2019-03-30 03:14 | 2116 | 0
196 | 2019-03-30 03:15 | 2116 | 0
197 | 2019-03-30 03:16 | 2116 | 0
198 | 2019-03-30 03:17 | 2116 | 0
199 | 2019-03-30 03:18 | 2116 | 0
200 | 2019-03-30 03:19 | 2116 | 0
201 | 2019-03-30 03:20 | 2116 | 0
202 | 2019-03-30 03:21 | 2116 | 0
203 | 2019-03-30 03:22 | 2116 | 0
204 | 2019-03-30 03:23 | 2116 | 0
205 | 2019-03-30 03:24 | 2116 | 0
206 | 2019-03-30 03:25 | 2116 | 0
207 | 2019-03-30 03:26 | 2116 | 0
208 | 2019-03-30 03:27 | 2116 | 0
209 | 2019-03-30 03:28 | 2116 | 0
210 | 2019-03-30 03:29 | 2116 | 0
211 | 2019-03-30 03:30 | 2116 | 0
212 | 2019-03-30 03:31 | 2116 | 0
213 | 2019-03-30 03:32 | 2116 | 0
214 | 2019-03-30 03:33 | 2116 | 0
215 | 2019-03-30 03:34 | 2116 | 0
216 | 2019-03-30 03:35 | 2116 | 0
217 | 2019-03-30 03:36 | 2116 | 0
218 | 2019-03-30 03:37 | 2116 | 0
219 | 2019-03-30 03:38 | 2116 | 0
220 | 2019-03-30 03:39 | 2116 | 0
221 | 2019-03-30 03:40 | 2116 | 0
222 | 2019-03-30 03:41 | 2116 | 0
223 | 2019-03-30 03:42 | 2116 | 0
224 | 2019-03-30 03:43 | 2116 | 0
225 | 2019-03-30 03:44 | 2116 | 0
226 | 2019-03-30 03:45 | 2116 | 0
227 | 2019-03-30 03:46 | 2116 | 0
228 | 2019-03-30 03:47 | 2116 | 0
229 | 2019-03-30 03:48 | 2116 | 0
230 | 2019-03-30 03:49 | 2116 | 0
231 | 2019-03-30 03:50 | 2116 | 0
232 | 2019-03-30 03:51 | 2116 | 0
233 | 2019-03-30 03:52 | 2116 | 0
234 | 2019-03-30 03:53 | 2116 | 0
235 | 2019-03-30 03:54 | 2116 | 0
236 | 2019-03-30 03:55 | 2116 | 0
237 | 2019-03-30 03:56 | 2116 | 0
238 | 2019-03-30 03:57 | 2116 | 0
239 | 2019-03-30 03:58 | 2116 | 0
240 | 2019-03-30 03:59 | 2116 | 0
241 | 2019-03-30 04:00 | 2117 | 0
242 | 2019-03-30 04:01 | 2117 | 0
243 | 2019-03-30 04:02 | 2117 | 0
244 | 2019-03-30 04:03 | 2117 | 0
245 | 2019-03-30 04:04 | 2117 | 0
246 | 2019-03-30 04:05 | 2117 | 0
247 | 2019-03-30 04:06 | 2117 | 0
248 | 2019-03-30 04:07 | 2117 | 0
249 | 2019-03-30 04:08 | 2117 | 0
250 | 2019-03-30 04:09 | 2117 | 0
251 | 2019-03-30 04:10 | 2117 | 0
252 | 2019-03-30 04:11 | 2117 | 0
253 | 2019-03-30 04:12 | 2117 | 0
254 | 2019-03-30 04:13 | 2117 | 0
255 | 2019-03-30 04:14 | 2117 | 0
256 | 2019-03-30 04:15 | 2117 | 0
257 | 2019-03-30 04:16 | 2117 | 0
258 | 2019-03-30 04:17 | 2117 | 0
259 | 2019-03-30 04:18 | 2117 | 0
260 | 2019-03-30 04:19 | 2117 | 0
261 | 2019-03-30 04:20 | 2117 | 0
262 | 2019-03-30 04:21 | 2117 | 0
263 | 2019-03-30 04:22 | 2117 | 0
264 | 2019-03-30 04:23 | 2117 | 0
265 | 2019-03-30 04:24 | 2117 | 0
266 | 2019-03-30 04:25 | 2117 | 0
267 | 2019-03-30 04:26 | 2117 | 0
268 | 2019-03-30 04:27 | 2117 | 0
269 | 2019-03-30 04:28 | 2117 | 0
270 | 2019-03-30 04:29 | 2117 | 0
271 | 2019-03-30 04:30 | 2117 | 0
272 | 2019-03-30 04:31 | 2117 | 0
273 | 2019-03-30 04:32 | 2117 | 0
274 | 2019-03-30 04:33 | 2117 | 0
275 | 2019-03-30 04:34 | 2117 | 0
276 | 2019-03-30 04:35 | 2117 | 0
277 | 2019-03-30 04:36 | 2117 | 0
278 | 2019-03-30 04:37 | 2117 | 0
279 | 2019-03-30 04:38 | 2117 | 0
280 | 2019-03-30 04:39 | 2117 | 0
281 | 2019-03-30 04:40 | 2117 | 0
282 | 2019-03-30 04:41 | 2117 | 0
283 | 2019-03-30 04:42 | 2117 | 0
284 | 2019-03-30 04:43 | 2117 | 0
285 | 2019-03-30 04:44 | 2117 | 0
286 | 2019-03-30 04:45 | 2117 | 0
287 | 2019-03-30 04:46 | 2117 | 0
288 | 2019-03-30 04:47 | 2117 | 0
289 | 2019-03-30 04:48 | 2117 | 0
290 | 2019-03-30 04:49 | 2117 | 0
291 | 2019-03-30 04:50 | 2117 | 0
292 | 2019-03-30 04:51 | 2117 | 0
293 | 2019-03-30 04:52 | 2117 | 0
294 | 2019-03-30 04:53 | 2117 | 0
295 | 2019-03-30 04:54 | 2117 | 0
296 | 2019-03-30 04:55 | 2117 | 0
297 | 2019-03-30 04:56 | 2117 | 0
298 | 2019-03-30 04:57 | 2117 | 0
299 | 2019-03-30 04:58 | 2117 | 0
300 | 2019-03-30 04:59 | 2117 | 0
301 | 2019-03-30 05:00 | 2117 | 0
302 | 2019-03-30 05:01 | 2118 | 0
303 | 2019-03-30 05:02 | 2118 | 0
304 | 2019-03-30 05:03 | 2118 | 0
305 | 2019-03-30 05:04 | 2118 | 0
306 | 2019-03-30 05:05 | 2118 | 0
307 | 2019-03-30 05:06 | 2118 | 0
308 | 2019-03-30 05:07 | 2118 | 0
309 | 2019-03-30 05:08 | 2118 | 0
310 | 2019-03-30 05:09 | 2118 | 0
311 | 2019-03-30 05:10 | 2118 | 0
312 | 2019-03-30 05:11 | 2118 | 0
313 | 2019-03-30 05:12 | 2118 | 0
314 | 2019-03-30 05:13 | 2118 | 0
315 | 2019-03-30 05:14 | 2118 | 0
316 | 2019-03-30 05:15 | 2118 | 0
317 | 2019-03-30 05:16 | 2118 | 0
318 | 2019-03-30 05:17 | 2118 | 0
319 | 2019-03-30 05:18 | 2118 | 0
320 | 2019-03-30 05:19 | 2118 | 0
321 | 2019-03-30 05:20 | 2118 | 0
322 | 2019-03-30 05:21 | 2118 | 0
323 | 2019-03-30 05:22 | 2118 | 0
324 | 2019-03-30 05:23 | 2118 | 0
325 | 2019-03-30 05:24 | 2118 | 0
326 | 2019-03-30 05:25 | 2118 | 0
327 | 2019-03-30 05:26 | 2118 | 0
328 | 2019-03-30 05:27 | 2118 | 0
329 | 2019-03-30 05:28 | 2118 | 0
330 | 2019-03-30 05:29 | 2118 | 0
331 | 2019-03-30 05:30 | 2118 | 0
332 | 2019-03-30 05:31 | 2118 | 0
333 | 2019-03-30 05:32 | 2118 | 0
334 | 2019-03-30 05:33 | 2118 | 0
335 | 2019-03-30 05:34 | 2118 | 0
336 | 2019-03-30 05:35 | 2118 | 0
337 | 2019-03-30 05:36 | 2118 | 0
338 | 2019-03-30 05:37 | 2118 | 0
339 | 2019-03-30 05:38 | 2118 | 0
340 | 2019-03-30 05:39 | 2118 | 0
341 | 2019-03-30 05:40 | 2118 | 0
342 | 2019-03-30 05:41 | 2118 | 0
343 | 2019-03-30 05:42 | 2118 | 0
344 | 2019-03-30 05:43 | 2118 | 0
345 | 2019-03-30 05:44 | 2118 | 0
346 | 2019-03-30 05:45 | 2118 | 0
347 | 2019-03-30 05:46 | 2118 | 0
348 | 2019-03-30 05:47 | 2118 | 0
349 | 2019-03-30 05:48 | 2118 | 0
350 | 2019-03-30 05:49 | 2118 | 0
351 | 2019-03-30 05:50 | 2118 | 0
352 | 2019-03-30 05:51 | 2118 | 0
353 | 2019-03-30 05:52 | 2118 | 0
354 | 2019-03-30 05:53 | 2118 | 0
355 | 2019-03-30 05:54 | 2118 | 0
356 | 2019-03-30 05:55 | 2118 | 0
357 | 2019-03-30 05:56 | 2118 | 0
358 | 2019-03-30 05:57 | 2118 | 0
359 | 2019-03-30 05:58 | 2118 | 0
360 | 2019-03-30 05:59 | 2118 | 0
361 | 2019-03-30 06:00 | 2119 | 0
362 | 2019-03-30 06:01 | 2119 | 0
363 | 2019-03-30 06:02 | 2119 | 0
364 | 2019-03-30 06:03 | 2119 | 0
365 | 2019-03-30 06:04 | 2119 | 0
366 | 2019-03-30 06:05 | 2119 | 0
367 | 2019-03-30 06:06 | 2119 | 0
368 | 2019-03-30 06:07 | 2119 | 0
369 | 2019-03-30 06:08 | 2119 | 0
370 | 2019-03-30 06:09 | 2119 | 0
371 | 2019-03-30 06:10 | 2119 | 0
372 | 2019-03-30 06:11 | 2119 | 0
373 | 2019-03-30 06:12 | 2119 | 0
374 | 2019-03-30 06:13 | 2119 | 0
375 | 2019-03-30 06:14 | 2119 | 0
376 | 2019-03-30 06:15 | 2119 | 0
377 | 2019-03-30 06:16 | 2119 | 0
378 | 2019-03-30 06:17 | 2119 | 0
379 | 2019-03-30 06:18 | 2119 | 0
380 | 2019-03-30 06:19 | 2119 | 0
381 | 2019-03-30 06:20 | 2119 | 0
382 | 2019-03-30 06:21 | 2119 | 0.004962
383 | 2019-03-30 06:22 | 2119 | 0
384 | 2019-03-30 06:23 | 2119 | 0
385 | 2019-03-30 06:24 | 2119 | 0
386 | 2019-03-30 06:25 | 2119 | 0.004962
387 | 2019-03-30 06:26 | 2119 | 0
388 | 2019-03-30 06:27 | 2119 | 0.004962
389 | 2019-03-30 06:28 | 2119 | 0.004962
390 | 2019-03-30 06:29 | 2119 | 0.004962
391 | 2019-03-30 06:30 | 2119 | 0.0099239
392 | 2019-03-30 06:31 | 2119 | 0.004962
393 | 2019-03-30 06:32 | 2119 | 0.0099239
394 | 2019-03-30 06:33 | 2119 | 0.004962
395 | 2019-03-30 06:34 | 2119 | 0.0099239
396 | 2019-03-30 06:35 | 2119 | 0.0099239
397 | 2019-03-30 06:36 | 2119 | 0.0099239
398 | 2019-03-30 06:37 | 2119 | 0.014886
399 | 2019-03-30 06:38 | 2119 | 0.0099239
400 | 2019-03-30 06:39 | 2119 | 0.014886
401 | 2019-03-30 06:40 | 2119 | 0.0099239
402 | 2019-03-30 06:41 | 2119 | 0.014886
403 | 2019-03-30 06:42 | 2119 | 0.014886
404 | 2019-03-30 06:43 | 2119 | 0.014886
405 | 2019-03-30 06:44 | 2119 | 0.014886
406 | 2019-03-30 06:45 | 2119 | 0.014886
407 | 2019-03-30 06:46 | 2119 | 0.019848
408 | 2019-03-30 06:47 | 2119 | 0.014886
409 | 2019-03-30 06:48 | 2119 | 0.019848
410 | 2019-03-30 06:49 | 2119 | 0.019848
411 | 2019-03-30 06:50 | 2119 | 0.019848
412 | 2019-03-30 06:51 | 2119 | 0.019848
413 | 2019-03-30 06:52 | 2119 | 0.019848
414 | 2019-03-30 06:53 | 2119 | 0.019848
415 | 2019-03-30 06:54 | 2119 | 0.02481
416 | 2019-03-30 06:55 | 2119 | 0.02481
417 | 2019-03-30 06:56 | 2119 | 0.019848
418 | 2019-03-30 06:57 | 2119 | 0.02481
419 | 2019-03-30 06:58 | 2119 | 0.02481
420 | 2019-03-30 06:59 | 2119 | 0.029772
421 | 2019-03-30 07:00 | 2120 | 0.02481
422 | 2019-03-30 07:01 | 2120 | 0.02481
423 | 2019-03-30 07:02 | 2120 | 0.029772
424 | 2019-03-30 07:03 | 2120 | 0.02481
425 | 2019-03-30 07:04 | 2120 | 0.029772
426 | 2019-03-30 07:05 | 2120 | 0.029772
427 | 2019-03-30 07:06 | 2120 | 0.029772
428 | 2019-03-30 07:07 | 2120 | 0.029772
429 | 2019-03-30 07:08 | 2120 | 0.029772
430 | 2019-03-30 07:09 | 2120 | 0.034734
431 | 2019-03-30 07:10 | 2120 | 0.029772
432 | 2019-03-30 07:11 | 2120 | 0.034734
433 | 2019-03-30 07:12 | 2120 | 0.034734
434 | 2019-03-30 07:13 | 2120 | 0.034734
435 | 2019-03-30 07:14 | 2120 | 0.034734
436 | 2019-03-30 07:15 | 2120 | 0.034734
437 | 2019-03-30 07:16 | 2120 | 0.034734
438 | 2019-03-30 07:17 | 2120 | 0.034734
439 | 2019-03-30 07:18 | 2120 | 0.039696
440 | 2019-03-30 07:19 | 2120 | 0.034734
441 | 2019-03-30 07:20 | 2120 | 0.039696
442 | 2019-03-30 07:21 | 2120 | 0.039696
443 | 2019-03-30 07:22 | 2120 | 0.044658
444 | 2019-03-30 07:23 | 2120 | 0.039696
445 | 2019-03-30 07:24 | 2120 | 0.044658
446 | 2019-03-30 07:25 | 2120 | 0.044658
447 | 2019-03-30 07:26 | 2120 | 0.044658
448 | 2019-03-30 07:27 | 2120 | 0.044658
449 | 2019-03-30 07:28 | 2120 | 0.044658
450 | 2019-03-30 07:29 | 2120 | 0.04962
451 | 2019-03-30 07:30 | 2120 | 0.04962
452 | 2019-03-30 07:31 | 2120 | 0.04962
453 | 2019-03-30 07:32 | 2120 | 0.054582
454 | 2019-03-30 07:33 | 2120 | 0.054582
455 | 2019-03-30 07:34 | 2120 | 0.054582
456 | 2019-03-30 07:35 | 2120 | 0.054582
457 | 2019-03-30 07:36 | 2120 | 0.059543
458 | 2019-03-30 07:37 | 2120 | 0.054582
459 | 2019-03-30 07:38 | 2120 | 0.064505
460 | 2019-03-30 07:39 | 2120 | 0.059543
461 | 2019-03-30 07:40 | 2120 | 0.064505
462 | 2019-03-30 07:41 | 2120 | 0.064505
463 | 2019-03-30 07:42 | 2120 | 0.069467
464 | 2019-03-30 07:43 | 2120 | 0.069467
465 | 2019-03-30 07:44 | 2120 | 0.074429
466 | 2019-03-30 07:45 | 2120 | 0.069467
467 | 2019-03-30 07:46 | 2120 | 0.079391
468 | 2019-03-30 07:47 | 2120 | 0.074429
469 | 2019-03-30 07:48 | 2120 | 0.079391
470 | 2019-03-30 07:49 | 2120 | 0.084353
471 | 2019-03-30 07:50 | 2120 | 0.084353
472 | 2019-03-30 07:51 | 2120 | 0.084353
473 | 2019-03-30 07:52 | 2120 | 0.089315
474 | 2019-03-30 07:53 | 2120 | 0.094277
475 | 2019-03-30 07:54 | 2120 | 0.094277
476 | 2019-03-30 07:55 | 2120 | 0.094277
477 | 2019-03-30 07:56 | 2120 | 0.099239
478 | 2019-03-30 07:57 | 2120 | 0.1042
479 | 2019-03-30 07:58 | 2120 | 0.1042
480 | 2019-03-30 07:59 | 2120 | 0.10916
481 | 2019-03-30 08:00 | 2120 | 0.11413
482 | 2019-03-30 08:01 | 2121 | 0.10916
483 | 2019-03-30 08:02 | 2121 | 0.11909
484 | 2019-03-30 08:03 | 2121 | 0.11909
485 | 2019-03-30 08:04 | 2121 | 0.12405
486 | 2019-03-30 08:05 | 2121 | 0.12405
487 | 2019-03-30 08:06 | 2121 | 0.13397
488 | 2019-03-30 08:07 | 2121 | 0.12901
489 | 2019-03-30 08:08 | 2121 | 0.13893
490 | 2019-03-30 08:09 | 2121 | 0.13397
491 | 2019-03-30 08:10 | 2121 | 0.1439
492 | 2019-03-30 08:11 | 2121 | 0.1439
493 | 2019-03-30 08:12 | 2121 | 0.14886
494 | 2019-03-30 08:13 | 2121 | 0.15382
495 | 2019-03-30 08:14 | 2121 | 0.15382
496 | 2019-03-30 08:15 | 2121 | 0.15878
497 | 2019-03-30 08:16 | 2121 | 0.16374
498 | 2019-03-30 08:17 | 2121 | 0.16374
499 | 2019-03-30 08:18 | 2121 | 0.16871
500 | 2019-03-30 08:19 | 2121 | 0.16871
501 | 2019-03-30 08:20 | 2121 | 0.17863
502 | 2019-03-30 08:21 | 2121 | 0.17863
503 | 2019-03-30 08:22 | 2121 | 0.17863
504 | 2019-03-30 08:23 | 2121 | 0.18855
505 | 2019-03-30 08:24 | 2121 | 0.18855
506 | 2019-03-30 08:25 | 2121 | 0.18855
507 | 2019-03-30 08:26 | 2121 | 0.19848
508 | 2019-03-30 08:27 | 2121 | 0.19848
509 | 2019-03-30 08:28 | 2121 | 0.20344
510 | 2019-03-30 08:29 | 2121 | 0.20344
511 | 2019-03-30 08:30 | 2121 | 0.2084
512 | 2019-03-30 08:31 | 2121 | 0.21336
513 | 2019-03-30 08:32 | 2121 | 0.21833
514 | 2019-03-30 08:33 | 2121 | 0.21833
515 | 2019-03-30 08:34 | 2121 | 0.22329
516 | 2019-03-30 08:35 | 2121 | 0.22825
517 | 2019-03-30 08:36 | 2121 | 0.23321
518 | 2019-03-30 08:37 | 2121 | 0.23321
519 | 2019-03-30 08:38 | 2121 | 0.23817
520 | 2019-03-30 08:39 | 2121 | 0.24314
521 | 2019-03-30 08:40 | 2121 | 0.2481
522 | 2019-03-30 08:41 | 2121 | 0.2481
523 | 2019-03-30 08:42 | 2121 | 0.25306
524 | 2019-03-30 08:43 | 2121 | 0.25802
525 | 2019-03-30 08:44 | 2121 | 0.26298
526 | 2019-03-30 08:45 | 2121 | 0.26298
527 | 2019-03-30 08:46 | 2121 | 0.26795
528 | 2019-03-30 08:47 | 2121 | 0.26795
529 | 2019-03-30 08:48 | 2121 | 0.27291
530 | 2019-03-30 08:49 | 2121 | 0.27787
531 | 2019-03-30 08:50 | 2121 | 0.27787
532 | 2019-03-30 08:51 | 2121 | 0.28283
533 | 2019-03-30 08:52 | 2121 | 0.28779
534 | 2019-03-30 08:53 | 2121 | 0.29276
535 | 2019-03-30 08:54 | 2121 | 0.29276
536 | 2019-03-30 08:55 | 2121 | 0.29772
537 | 2019-03-30 08:56 | 2121 | 0.30268
538 | 2019-03-30 08:57 | 2121 | 0.30268
539 | 2019-03-30 08:58 | 2121 | 0.30764
540 | 2019-03-30 08:59 | 2121 | 0.3126
541 | 2019-03-30 09:00 | 2122 | 0.31757
542 | 2019-03-30 09:01 | 2122 | 0.32253
543 | 2019-03-30 09:02 | 2122 | 0.32253
544 | 2019-03-30 09:03 | 2122 | 0.32749
545 | 2019-03-30 09:04 | 2122 | 0.33245
546 | 2019-03-30 09:05 | 2122 | 0.33245
547 | 2019-03-30 09:06 | 2122 | 0.33741
548 | 2019-03-30 09:07 | 2122 | 0.34238
549 | 2019-03-30 09:08 | 2122 | 0.34238
550 | 2019-03-30 09:09 | 2122 | 0.34734
551 | 2019-03-30 09:10 | 2122 | 0.3523
552 | 2019-03-30 09:11 | 2122 | 0.3523
553 | 2019-03-30 09:12 | 2122 | 0.36222
554 | 2019-03-30 09:13 | 2122 | 0.36222
555 | 2019-03-30 09:14 | 2122 | 0.36718
556 | 2019-03-30 09:15 | 2122 | 0.36718
557 | 2019-03-30 09:16 | 2122 | 0.37215
558 | 2019-03-30 09:17 | 2122 | 0.37711
559 | 2019-03-30 09:18 | 2122 | 0.38207
560 | 2019-03-30 09:19 | 2122 | 0.38207
561 | 2019-03-30 09:20 | 2122 | 0.39199
562 | 2019-03-30 09:21 | 2122 | 0.39199
563 | 2019-03-30 09:22 | 2122 | 0.39199
564 | 2019-03-30 09:23 | 2122 | 0.40192
565 | 2019-03-30 09:24 | 2122 | 0.40192
566 | 2019-03-30 09:25 | 2122 | 0.40192
567 | 2019-03-30 09:26 | 2122 | 0.41184
568 | 2019-03-30 09:27 | 2122 | 0.41184
569 | 2019-03-30 09:28 | 2122 | 0.41184
570 | 2019-03-30 09:29 | 2122 | 0.42177
571 | 2019-03-30 09:30 | 2122 | 0.42177
572 | 2019-03-30 09:31 | 2122 | 0.42177
573 | 2019-03-30 09:32 | 2122 | 0.42673
574 | 2019-03-30 09:33 | 2122 | 0.42673
575 | 2019-03-30 09:34 | 2122 | 0.43169
576 | 2019-03-30 09:35 | 2122 | 0.43665
577 | 2019-03-30 09:36 | 2122 | 0.44161
578 | 2019-03-30 09:37 | 2122 | 0.44161
579 | 2019-03-30 09:38 | 2122 | 0.44161
580 | 2019-03-30 09:39 | 2122 | 0.45154
581 | 2019-03-30 09:40 | 2122 | 0.45154
582 | 2019-03-30 09:41 | 2122 | 0.45154
583 | 2019-03-30 09:42 | 2122 | 0.4565
584 | 2019-03-30 09:43 | 2122 | 0.46146
585 | 2019-03-30 09:44 | 2122 | 0.46146
586 | 2019-03-30 09:45 | 2122 | 0.47139
587 | 2019-03-30 09:46 | 2122 | 0.46642
588 | 2019-03-30 09:47 | 2122 | 0.47139
589 | 2019-03-30 09:48 | 2122 | 0.47635
590 | 2019-03-30 09:49 | 2122 | 0.48131
591 | 2019-03-30 09:50 | 2122 | 0.48131
592 | 2019-03-30 09:51 | 2122 | 0.48627
593 | 2019-03-30 09:52 | 2122 | 0.49123
594 | 2019-03-30 09:53 | 2122 | 0.48627
595 | 2019-03-30 09:54 | 2122 | 0.4962
596 | 2019-03-30 09:55 | 2122 | 0.4962
597 | 2019-03-30 09:56 | 2122 | 0.50116
598 | 2019-03-30 09:57 | 2122 | 0.50116
599 | 2019-03-30 09:58 | 2122 | 0.51108
600 | 2019-03-30 09:59 | 2122 | 0.51108
601 | 2019-03-30 10:00 | 2123 | 0.51108
602 | 2019-03-30 10:01 | 2123 | 0.51604
603 | 2019-03-30 10:02 | 2123 | 0.52597
604 | 2019-03-30 10:03 | 2123 | 0.52101
605 | 2019-03-30 10:04 | 2123 | 0.53093
606 | 2019-03-30 10:05 | 2123 | 0.53093
607 | 2019-03-30 10:06 | 2123 | 0.53093
608 | 2019-03-30 10:07 | 2123 | 0.53589
609 | 2019-03-30 10:08 | 2123 | 0.54085
610 | 2019-03-30 10:09 | 2123 | 0.54582
611 | 2019-03-30 10:10 | 2123 | 0.54582
612 | 2019-03-30 10:11 | 2123 | 0.54582
613 | 2019-03-30 10:12 | 2123 | 0.55078
614 | 2019-03-30 10:13 | 2123 | 0.55078
615 | 2019-03-30 10:14 | 2123 | 0.55574
616 | 2019-03-30 10:15 | 2123 | 0.55078
617 | 2019-03-30 10:16 | 2123 | 0.55574
618 | 2019-03-30 10:17 | 2123 | 0.5607
619 | 2019-03-30 10:18 | 2123 | 0.5607
620 | 2019-03-30 10:19 | 2123 | 0.56566
621 | 2019-03-30 10:20 | 2123 | 0.56566
622 | 2019-03-30 10:21 | 2123 | 0.57063
623 | 2019-03-30 10:22 | 2123 | 0.57559
624 | 2019-03-30 10:23 | 2123 | 0.57559
625 | 2019-03-30 10:24 | 2123 | 0.57559
626 | 2019-03-30 10:25 | 2123 | 0.58055
627 | 2019-03-30 10:26 | 2123 | 0.58055
628 | 2019-03-30 10:27 | 2123 | 0.58551
629 | 2019-03-30 10:28 | 2123 | 0.59047
630 | 2019-03-30 10:29 | 2123 | 0.58551
631 | 2019-03-30 10:30 | 2123 | 0.59543
632 | 2019-03-30 10:31 | 2123 | 0.59047
633 | 2019-03-30 10:32 | 2123 | 0.59047
634 | 2019-03-30 10:33 | 2123 | 0.59047
635 | 2019-03-30 10:34 | 2123 | 0.59543
636 | 2019-03-30 10:35 | 2123 | 0.59543
637 | 2019-03-30 10:36 | 2123 | 0.6004
638 | 2019-03-30 10:37 | 2123 | 0.60536
639 | 2019-03-30 10:38 | 2123 | 0.60536
640 | 2019-03-30 10:39 | 2123 | 0.61528
641 | 2019-03-30 10:40 | 2123 | 0.61032
642 | 2019-03-30 10:41 | 2123 | 0.62024
643 | 2019-03-30 10:42 | 2123 | 0.61528
644 | 2019-03-30 10:43 | 2123 | 0.62024
645 | 2019-03-30 10:44 | 2123 | 0.62521
646 | 2019-03-30 10:45 | 2123 | 0.62024
647 | 2019-03-30 10:46 | 2123 | 0.62521
648 | 2019-03-30 10:47 | 2123 | 0.63017
649 | 2019-03-30 10:48 | 2123 | 0.62521
650 | 2019-03-30 10:49 | 2123 | 0.63017
651 | 2019-03-30 10:50 | 2123 | 0.63017
652 | 2019-03-30 10:51 | 2123 | 0.63513
653 | 2019-03-30 10:52 | 2123 | 0.63017
654 | 2019-03-30 10:53 | 2123 | 0.64009
655 | 2019-03-30 10:54 | 2123 | 0.64009
656 | 2019-03-30 10:55 | 2123 | 0.64505
657 | 2019-03-30 10:56 | 2123 | 0.64505
658 | 2019-03-30 10:57 | 2123 | 0.64505
659 | 2019-03-30 10:58 | 2123 | 0.64505
660 | 2019-03-30 10:59 | 2123 | 0.64505
661 | 2019-03-30 11:00 | 2123 | 0.65002
662 | 2019-03-30 11:01 | 2124 | 0.65002
663 | 2019-03-30 11:02 | 2124 | 0.65002
664 | 2019-03-30 11:03 | 2124 | 0.65498
665 | 2019-03-30 11:04 | 2124 | 0.65994
666 | 2019-03-30 11:05 | 2124 | 0.65498
667 | 2019-03-30 11:06 | 2124 | 0.6649
668 | 2019-03-30 11:07 | 2124 | 0.65994
669 | 2019-03-30 11:08 | 2124 | 0.66986
670 | 2019-03-30 11:09 | 2124 | 0.6649
671 | 2019-03-30 11:10 | 2124 | 0.67483
672 | 2019-03-30 11:11 | 2124 | 0.67483
673 | 2019-03-30 11:12 | 2124 | 0.67979
674 | 2019-03-30 11:13 | 2124 | 0.67483
675 | 2019-03-30 11:14 | 2124 | 0.67483
676 | 2019-03-30 11:15 | 2124 | 0.67483
677 | 2019-03-30 11:16 | 2124 | 0.67979
678 | 2019-03-30 11:17 | 2124 | 0.67483
679 | 2019-03-30 11:18 | 2124 | 0.67979
680 | 2019-03-30 11:19 | 2124 | 0.67483
681 | 2019-03-30 11:20 | 2124 | 0.67979
682 | 2019-03-30 11:21 | 2124 | 0.67979
683 | 2019-03-30 11:22 | 2124 | 0.68475
684 | 2019-03-30 11:23 | 2124 | 0.68475
685 | 2019-03-30 11:24 | 2124 | 0.68475
686 | 2019-03-30 11:25 | 2124 | 0.68971
687 | 2019-03-30 11:26 | 2124 | 0.69467
688 | 2019-03-30 11:27 | 2124 | 0.69964
689 | 2019-03-30 11:28 | 2124 | 0.69467
690 | 2019-03-30 11:29 | 2124 | 0.69964
691 | 2019-03-30 11:30 | 2124 | 0.69467
692 | 2019-03-30 11:31 | 2124 | 0.69964
693 | 2019-03-30 11:32 | 2124 | 0.69964
694 | 2019-03-30 11:33 | 2124 | 0.69964
695 | 2019-03-30 11:34 | 2124 | 0.69964
696 | 2019-03-30 11:35 | 2124 | 0.69964
697 | 2019-03-30 11:36 | 2124 | 0.70956
698 | 2019-03-30 11:37 | 2124 | 0.7046
699 | 2019-03-30 11:38 | 2124 | 0.71452
700 | 2019-03-30 11:39 | 2124 | 0.70956
701 | 2019-03-30 11:40 | 2124 | 0.71452
702 | 2019-03-30 11:41 | 2124 | 0.71452
703 | 2019-03-30 11:42 | 2124 | 0.71452
704 | 2019-03-30 11:43 | 2124 | 0.71948
705 | 2019-03-30 11:44 | 2124 | 0.71452
706 | 2019-03-30 11:45 | 2124 | 0.71452
707 | 2019-03-30 11:46 | 2124 | 0.71948
708 | 2019-03-30 11:47 | 2124 | 0.71948
709 | 2019-03-30 11:48 | 2124 | 0.71948
710 | 2019-03-30 11:49 | 2124 | 0.72445
711 | 2019-03-30 11:50 | 2124 | 0.71948
712 | 2019-03-30 11:51 | 2124 | 0.72445
713 | 2019-03-30 11:52 | 2124 | 0.72941
714 | 2019-03-30 11:53 | 2124 | 0.72445
715 | 2019-03-30 11:54 | 2124 | 0.73437
716 | 2019-03-30 11:55 | 2124 | 0.72941
717 | 2019-03-30 11:56 | 2124 | 0.72445
718 | 2019-03-30 11:57 | 2124 | 0.72941
719 | 2019-03-30 11:58 | 2124 | 0.72941
720 | 2019-03-30 11:59 | 2124 | 0.73437
721 | 2019-03-30 12:00 | 2125 | 0.72941
722 | 2019-03-30 12:01 | 2125 | 0.73437
723 | 2019-03-30 12:02 | 2125 | 0.73933
724 | 2019-03-30 12:03 | 2125 | 0.73933
725 | 2019-03-30 12:04 | 2125 | 0.73933
726 | 2019-03-30 12:05 | 2125 | 0.74429
727 | 2019-03-30 12:06 | 2125 | 0.73933
728 | 2019-03-30 12:07 | 2125 | 0.74429
729 | 2019-03-30 12:08 | 2125 | 0.73933
730 | 2019-03-30 12:09 | 2125 | 0.74429
731 | 2019-03-30 12:10 | 2125 | 0.73933
732 | 2019-03-30 12:11 | 2125 | 0.74429
733 | 2019-03-30 12:12 | 2125 | 0.74926
734 | 2019-03-30 12:13 | 2125 | 0.74429
735 | 2019-03-30 12:14 | 2125 | 0.74429
736 | 2019-03-30 12:15 | 2125 | 0.74429
737 | 2019-03-30 12:16 | 2125 | 0.74926
738 | 2019-03-30 12:17 | 2125 | 0.73933
739 | 2019-03-30 12:18 | 2125 | 0.74926
740 | 2019-03-30 12:19 | 2125 | 0.74926
741 | 2019-03-30 12:20 | 2125 | 0.74926
742 | 2019-03-30 12:21 | 2125 | 0.74926
743 | 2019-03-30 12:22 | 2125 | 0.74926
744 | 2019-03-30 12:23 | 2125 | 0.74926
745 | 2019-03-30 12:24 | 2125 | 0.75422
746 | 2019-03-30 12:25 | 2125 | 0.75918
747 | 2019-03-30 12:26 | 2125 | 0.75422
748 | 2019-03-30 12:27 | 2125 | 0.76414
749 | 2019-03-30 12:28 | 2125 | 0.7691
750 | 2019-03-30 12:29 | 2125 | 0.7691
751 | 2019-03-30 12:30 | 2125 | 0.77407
752 | 2019-03-30 12:31 | 2125 | 0.77407
753 | 2019-03-30 12:32 | 2125 | 0.77407
754 | 2019-03-30 12:33 | 2125 | 0.77407
755 | 2019-03-30 12:34 | 2125 | 0.77407
756 | 2019-03-30 12:35 | 2125 | 0.77903
757 | 2019-03-30 12:36 | 2125 | 0.77903
758 | 2019-03-30 12:37 | 2125 | 0.77903
759 | 2019-03-30 12:38 | 2125 | 0.77903
760 | 2019-03-30 12:39 | 2125 | 0.77407
761 | 2019-03-30 12:40 | 2125 | 0.77903
762 | 2019-03-30 12:41 | 2125 | 0.77407
763 | 2019-03-30 12:42 | 2125 | 0.77903
764 | 2019-03-30 12:43 | 2125 | 0.77407
765 | 2019-03-30 12:44 | 2125 | 0.77407
766 | 2019-03-30 12:45 | 2125 | 0.77407
767 | 2019-03-30 12:46 | 2125 | 0.76414
768 | 2019-03-30 12:47 | 2125 | 0.76414
769 | 2019-03-30 12:48 | 2125 | 0.76414
770 | 2019-03-30 12:49 | 2125 | 0.76414
771 | 2019-03-30 12:50 | 2125 | 0.7691
772 | 2019-03-30 12:51 | 2125 | 0.76414
773 | 2019-03-30 12:52 | 2125 | 0.76414
774 | 2019-03-30 12:53 | 2125 | 0.76414
775 | 2019-03-30 12:54 | 2125 | 0.75918
776 | 2019-03-30 12:55 | 2125 | 0.76414
777 | 2019-03-30 12:56 | 2125 | 0.76414
778 | 2019-03-30 12:57 | 2125 | 0.76414
779 | 2019-03-30 12:58 | 2125 | 0.76414
780 | 2019-03-30 12:59 | 2125 | 0.7691
781 | 2019-03-30 13:00 | 2126 | 0.76414
782 | 2019-03-30 13:01 | 2126 | 0.76414
783 | 2019-03-30 13:02 | 2126 | 0.7691
784 | 2019-03-30 13:03 | 2126 | 0.76414
785 | 2019-03-30 13:04 | 2126 | 0.75918
786 | 2019-03-30 13:05 | 2126 | 0.76414
787 | 2019-03-30 13:06 | 2126 | 0.75918
788 | 2019-03-30 13:07 | 2126 | 0.75918
789 | 2019-03-30 13:08 | 2126 | 0.75918
790 | 2019-03-30 13:09 | 2126 | 0.75918
791 | 2019-03-30 13:10 | 2126 | 0.75918
792 | 2019-03-30 13:11 | 2126 | 0.75918
793 | 2019-03-30 13:12 | 2126 | 0.76414
794 | 2019-03-30 13:13 | 2126 | 0.75918
795 | 2019-03-30 13:14 | 2126 | 0.76414
796 | 2019-03-30 13:15 | 2126 | 0.7691
797 | 2019-03-30 13:16 | 2126 | 0.7691
798 | 2019-03-30 13:17 | 2126 | 0.76414
799 | 2019-03-30 13:18 | 2126 | 0.75918
800 | 2019-03-30 13:19 | 2126 | 0.75918
801 | 2019-03-30 13:20 | 2126 | 0.75918
802 | 2019-03-30 13:21 | 2126 | 0.75422
803 | 2019-03-30 13:22 | 2126 | 0.75422
804 | 2019-03-30 13:23 | 2126 | 0.74926
805 | 2019-03-30 13:24 | 2126 | 0.75422
806 | 2019-03-30 13:25 | 2126 | 0.75422
807 | 2019-03-30 13:26 | 2126 | 0.75918
808 | 2019-03-30 13:27 | 2126 | 0.75918
809 | 2019-03-30 13:28 | 2126 | 0.75918
810 | 2019-03-30 13:29 | 2126 | 0.75422
811 | 2019-03-30 13:30 | 2126 | 0.75918
812 | 2019-03-30 13:31 | 2126 | 0.75918
813 | 2019-03-30 13:32 | 2126 | 0.75918
814 | 2019-03-30 13:33 | 2126 | 0.75918
815 | 2019-03-30 13:34 | 2126 | 0.75918
816 | 2019-03-30 13:35 | 2126 | 0.76414
817 | 2019-03-30 13:36 | 2126 | 0.75422
818 | 2019-03-30 13:37 | 2126 | 0.75422
819 | 2019-03-30 13:38 | 2126 | 0.74429
820 | 2019-03-30 13:39 | 2126 | 0.74926
821 | 2019-03-30 13:40 | 2126 | 0.74429
822 | 2019-03-30 13:41 | 2126 | 0.74926
823 | 2019-03-30 13:42 | 2126 | 0.74926
824 | 2019-03-30 13:43 | 2126 | 0.74926
825 | 2019-03-30 13:44 | 2126 | 0.74926
826 | 2019-03-30 13:45 | 2126 | 0.74429
827 | 2019-03-30 13:46 | 2126 | 0.74429
828 | 2019-03-30 13:47 | 2126 | 0.74429
829 | 2019-03-30 13:48 | 2126 | 0.74429
830 | 2019-03-30 13:49 | 2126 | 0.73933
831 | 2019-03-30 13:50 | 2126 | 0.73437
832 | 2019-03-30 13:51 | 2126 | 0.73933
833 | 2019-03-30 13:52 | 2126 | 0.73933
834 | 2019-03-30 13:53 | 2126 | 0.73933
835 | 2019-03-30 13:54 | 2126 | 0.73437
836 | 2019-03-30 13:55 | 2126 | 0.73437
837 | 2019-03-30 13:56 | 2126 | 0.74429
838 | 2019-03-30 13:57 | 2126 | 0.73933
839 | 2019-03-30 13:58 | 2126 | 0.74429
840 | 2019-03-30 13:59 | 2126 | 0.73933
841 | 2019-03-30 14:00 | 2126 | 0.74429
842 | 2019-03-30 14:01 | 2127 | 0.74429
843 | 2019-03-30 14:02 | 2127 | 0.73933
844 | 2019-03-30 14:03 | 2127 | 0.73437
845 | 2019-03-30 14:04 | 2127 | 0.74429
846 | 2019-03-30 14:05 | 2127 | 0.73437
847 | 2019-03-30 14:06 | 2127 | 0.72941
848 | 2019-03-30 14:07 | 2127 | 0.72941
849 | 2019-03-30 14:08 | 2127 | 0.72445
850 | 2019-03-30 14:09 | 2127 | 0.72445
851 | 2019-03-30 14:10 | 2127 | 0.71948
852 | 2019-03-30 14:11 | 2127 | 0.71948
853 | 2019-03-30 14:12 | 2127 | 0.71948
854 | 2019-03-30 14:13 | 2127 | 0.71948
855 | 2019-03-30 14:14 | 2127 | 0.71948
856 | 2019-03-30 14:15 | 2127 | 0.72445
857 | 2019-03-30 14:16 | 2127 | 0.72445
858 | 2019-03-30 14:17 | 2127 | 0.71948
859 | 2019-03-30 14:18 | 2127 | 0.71948
860 | 2019-03-30 14:19 | 2127 | 0.71452
861 | 2019-03-30 14:20 | 2127 | 0.70956
862 | 2019-03-30 14:21 | 2127 | 0.71452
863 | 2019-03-30 14:22 | 2127 | 0.71452
864 | 2019-03-30 14:23 | 2127 | 0.71452
865 | 2019-03-30 14:24 | 2127 | 0.71452
866 | 2019-03-30 14:25 | 2127 | 0.71948
867 | 2019-03-30 14:26 | 2127 | 0.71948
868 | 2019-03-30 14:27 | 2127 | 0.71948
869 | 2019-03-30 14:28 | 2127 | 0.71948
870 | 2019-03-30 14:29 | 2127 | 0.71452
871 | 2019-03-30 14:30 | 2127 | 0.70956
872 | 2019-03-30 14:31 | 2127 | 0.69964
873 | 2019-03-30 14:32 | 2127 | 0.69964
874 | 2019-03-30 14:33 | 2127 | 0.69964
875 | 2019-03-30 14:34 | 2127 | 0.69467
876 | 2019-03-30 14:35 | 2127 | 0.68971
877 | 2019-03-30 14:36 | 2127 | 0.68971
878 | 2019-03-30 14:37 | 2127 | 0.69467
879 | 2019-03-30 14:38 | 2127 | 0.69467
880 | 2019-03-30 14:39 | 2127 | 0.69467
881 | 2019-03-30 14:40 | 2127 | 0.68971
882 | 2019-03-30 14:41 | 2127 | 0.68971
883 | 2019-03-30 14:42 | 2127 | 0.68971
884 | 2019-03-30 14:43 | 2127 | 0.68971
885 | 2019-03-30 14:44 | 2127 | 0.68971
886 | 2019-03-30 14:45 | 2127 | 0.68971
887 | 2019-03-30 14:46 | 2127 | 0.67979
888 | 2019-03-30 14:47 | 2127 | 0.68475
889 | 2019-03-30 14:48 | 2127 | 0.67979
890 | 2019-03-30 14:49 | 2127 | 0.68475
891 | 2019-03-30 14:50 | 2127 | 0.67979
892 | 2019-03-30 14:51 | 2127 | 0.67483
893 | 2019-03-30 14:52 | 2127 | 0.67483
894 | 2019-03-30 14:53 | 2127 | 0.66986
895 | 2019-03-30 14:54 | 2127 | 0.67483
896 | 2019-03-30 14:55 | 2127 | 0.66986
897 | 2019-03-30 14:56 | 2127 | 0.6649
898 | 2019-03-30 14:57 | 2127 | 0.65994
899 | 2019-03-30 14:58 | 2127 | 0.65498
900 | 2019-03-30 14:59 | 2127 | 0.65498
901 | 2019-03-30 15:00 | 2128 | 0.65002
902 | 2019-03-30 15:01 | 2128 | 0.65002
903 | 2019-03-30 15:02 | 2128 | 0.65002
904 | 2019-03-30 15:03 | 2128 | 0.64505
905 | 2019-03-30 15:04 | 2128 | 0.64505
906 | 2019-03-30 15:05 | 2128 | 0.64009
907 | 2019-03-30 15:06 | 2128 | 0.64505
908 | 2019-03-30 15:07 | 2128 | 0.64009
909 | 2019-03-30 15:08 | 2128 | 0.64009
910 | 2019-03-30 15:09 | 2128 | 0.64009
911 | 2019-03-30 15:10 | 2128 | 0.63513
912 | 2019-03-30 15:11 | 2128 | 0.63513
913 | 2019-03-30 15:12 | 2128 | 0.63017
914 | 2019-03-30 15:13 | 2128 | 0.63513
915 | 2019-03-30 15:14 | 2128 | 0.63513
916 | 2019-03-30 15:15 | 2128 | 0.63513
917 | 2019-03-30 15:16 | 2128 | 0.63017
918 | 2019-03-30 15:17 | 2128 | 0.62024
919 | 2019-03-30 15:18 | 2128 | 0.62024
920 | 2019-03-30 15:19 | 2128 | 0.61528
921 | 2019-03-30 15:20 | 2128 | 0.60536
922 | 2019-03-30 15:21 | 2128 | 0.61032
923 | 2019-03-30 15:22 | 2128 | 0.61528
924 | 2019-03-30 15:23 | 2128 | 0.60536
925 | 2019-03-30 15:24 | 2128 | 0.61032
926 | 2019-03-30 15:25 | 2128 | 0.60536
927 | 2019-03-30 15:26 | 2128 | 0.60536
928 | 2019-03-30 15:27 | 2128 | 0.6004
929 | 2019-03-30 15:28 | 2128 | 0.60536
930 | 2019-03-30 15:29 | 2128 | 0.59543
931 | 2019-03-30 15:30 | 2128 | 0.59543
932 | 2019-03-30 15:31 | 2128 | 0.59543
933 | 2019-03-30 15:32 | 2128 | 0.58055
934 | 2019-03-30 15:33 | 2128 | 0.58551
935 | 2019-03-30 15:34 | 2128 | 0.58055
936 | 2019-03-30 15:35 | 2128 | 0.57559
937 | 2019-03-30 15:36 | 2128 | 0.57559
938 | 2019-03-30 15:37 | 2128 | 0.57063
939 | 2019-03-30 15:38 | 2128 | 0.57063
940 | 2019-03-30 15:39 | 2128 | 0.57063
941 | 2019-03-30 15:40 | 2128 | 0.57559
942 | 2019-03-30 15:41 | 2128 | 0.57063
943 | 2019-03-30 15:42 | 2128 | 0.57063
944 | 2019-03-30 15:43 | 2128 | 0.56566
945 | 2019-03-30 15:44 | 2128 | 0.56566
946 | 2019-03-30 15:45 | 2128 | 0.5607
947 | 2019-03-30 15:46 | 2128 | 0.56566
948 | 2019-03-30 15:47 | 2128 | 0.5607
949 | 2019-03-30 15:48 | 2128 | 0.55574
950 | 2019-03-30 15:49 | 2128 | 0.55078
951 | 2019-03-30 15:50 | 2128 | 0.55574
952 | 2019-03-30 15:51 | 2128 | 0.55078
953 | 2019-03-30 15:52 | 2128 | 0.55078
954 | 2019-03-30 15:53 | 2128 | 0.54085
955 | 2019-03-30 15:54 | 2128 | 0.54085
956 | 2019-03-30 15:55 | 2128 | 0.53589
957 | 2019-03-30 15:56 | 2128 | 0.53093
958 | 2019-03-30 15:57 | 2128 | 0.53093
959 | 2019-03-30 15:58 | 2128 | 0.53093
960 | 2019-03-30 15:59 | 2128 | 0.52101
961 | 2019-03-30 16:00 | 2129 | 0.52101
962 | 2019-03-30 16:01 | 2129 | 0.52101
963 | 2019-03-30 16:02 | 2129 | 0.52101
964 | 2019-03-30 16:03 | 2129 | 0.51604
965 | 2019-03-30 16:04 | 2129 | 0.51604
966 | 2019-03-30 16:05 | 2129 | 0.51604
967 | 2019-03-30 16:06 | 2129 | 0.51108
968 | 2019-03-30 16:07 | 2129 | 0.51108
969 | 2019-03-30 16:08 | 2129 | 0.51108
970 | 2019-03-30 16:09 | 2129 | 0.50116
971 | 2019-03-30 16:10 | 2129 | 0.50116
972 | 2019-03-30 16:11 | 2129 | 0.50116
973 | 2019-03-30 16:12 | 2129 | 0.49123
974 | 2019-03-30 16:13 | 2129 | 0.4962
975 | 2019-03-30 16:14 | 2129 | 0.49123
976 | 2019-03-30 16:15 | 2129 | 0.48627
977 | 2019-03-30 16:16 | 2129 | 0.48131
978 | 2019-03-30 16:17 | 2129 | 0.47635
979 | 2019-03-30 16:18 | 2129 | 0.47635
980 | 2019-03-30 16:19 | 2129 | 0.47635
981 | 2019-03-30 16:20 | 2129 | 0.47139
982 | 2019-03-30 16:21 | 2129 | 0.47139
983 | 2019-03-30 16:22 | 2129 | 0.46146
984 | 2019-03-30 16:23 | 2129 | 0.46146
985 | 2019-03-30 16:24 | 2129 | 0.4565
986 | 2019-03-30 16:25 | 2129 | 0.44658
987 | 2019-03-30 16:26 | 2129 | 0.44658
988 | 2019-03-30 16:27 | 2129 | 0.44658
989 | 2019-03-30 16:28 | 2129 | 0.44161
990 | 2019-03-30 16:29 | 2129 | 0.43665
991 | 2019-03-30 16:30 | 2129 | 0.43169
992 | 2019-03-30 16:31 | 2129 | 0.42673
993 | 2019-03-30 16:32 | 2129 | 0.42177
994 | 2019-03-30 16:33 | 2129 | 0.42673
995 | 2019-03-30 16:34 | 2129 | 0.42673
996 | 2019-03-30 16:35 | 2129 | 0.42177
997 | 2019-03-30 16:36 | 2129 | 0.42177
998 | 2019-03-30 16:37 | 2129 | 0.42673
999 | 2019-03-30 16:38 | 2129 | 0.42177
1000 | 2019-03-30 16:39 | 2129 | 0.4168
1001 | 2019-03-30 16:40 | 2129 | 0.41184
1002 | 2019-03-30 16:41 | 2129 | 0.41184
1003 | 2019-03-30 16:42 | 2129 | 0.40688
1004 | 2019-03-30 16:43 | 2129 | 0.40192
1005 | 2019-03-30 16:44 | 2129 | 0.40192
1006 | 2019-03-30 16:45 | 2129 | 0.39696
1007 | 2019-03-30 16:46 | 2129 | 0.39696
1008 | 2019-03-30 16:47 | 2129 | 0.39199
1009 | 2019-03-30 16:48 | 2129 | 0.38207
1010 | 2019-03-30 16:49 | 2129 | 0.38703
1011 | 2019-03-30 16:50 | 2129 | 0.37711
1012 | 2019-03-30 16:51 | 2129 | 0.37711
1013 | 2019-03-30 16:52 | 2129 | 0.37215
1014 | 2019-03-30 16:53 | 2129 | 0.36718
1015 | 2019-03-30 16:54 | 2129 | 0.36222
1016 | 2019-03-30 16:55 | 2129 | 0.36222
1017 | 2019-03-30 16:56 | 2129 | 0.3523
1018 | 2019-03-30 16:57 | 2129 | 0.3523
1019 | 2019-03-30 16:58 | 2129 | 0.34734
1020 | 2019-03-30 16:59 | 2129 | 0.34238
1021 | 2019-03-30 17:00 | 2129 | 0.33741
1022 | 2019-03-30 17:01 | 2130 | 0.33245
1023 | 2019-03-30 17:02 | 2130 | 0.32749
1024 | 2019-03-30 17:03 | 2130 | 0.31757
1025 | 2019-03-30 17:04 | 2130 | 0.30764
1026 | 2019-03-30 17:05 | 2130 | 0.30268
1027 | 2019-03-30 17:06 | 2130 | 0.29772
1028 | 2019-03-30 17:07 | 2130 | 0.29276
1029 | 2019-03-30 17:08 | 2130 | 0.28283
1030 | 2019-03-30 17:09 | 2130 | 0.28283
1031 | 2019-03-30 17:10 | 2130 | 0.27787
1032 | 2019-03-30 17:11 | 2130 | 0.27291
1033 | 2019-03-30 17:12 | 2130 | 0.27291
1034 | 2019-03-30 17:13 | 2130 | 0.26298
1035 | 2019-03-30 17:14 | 2130 | 0.26298
1036 | 2019-03-30 17:15 | 2130 | 0.25306
1037 | 2019-03-30 17:16 | 2130 | 0.2481
1038 | 2019-03-30 17:17 | 2130 | 0.2481
1039 | 2019-03-30 17:18 | 2130 | 0.23817
1040 | 2019-03-30 17:19 | 2130 | 0.23321
1041 | 2019-03-30 17:20 | 2130 | 0.23817
1042 | 2019-03-30 17:21 | 2130 | 0.22825
1043 | 2019-03-30 17:22 | 2130 | 0.23321
1044 | 2019-03-30 17:23 | 2130 | 0.22825
1045 | 2019-03-30 17:24 | 2130 | 0.22329
1046 | 2019-03-30 17:25 | 2130 | 0.22329
1047 | 2019-03-30 17:26 | 2130 | 0.22329
1048 | 2019-03-30 17:27 | 2130 | 0.21336
1049 | 2019-03-30 17:28 | 2130 | 0.21336
1050 | 2019-03-30 17:29 | 2130 | 0.21336
1051 | 2019-03-30 17:30 | 2130 | 0.20344
1052 | 2019-03-30 17:31 | 2130 | 0.20344
1053 | 2019-03-30 17:32 | 2130 | 0.20344
1054 | 2019-03-30 17:33 | 2130 | 0.19352
1055 | 2019-03-30 17:34 | 2130 | 0.19848
1056 | 2019-03-30 17:35 | 2130 | 0.18855
1057 | 2019-03-30 17:36 | 2130 | 0.18855
1058 | 2019-03-30 17:37 | 2130 | 0.18359
1059 | 2019-03-30 17:38 | 2130 | 0.18359
1060 | 2019-03-30 17:39 | 2130 | 0.17863
1061 | 2019-03-30 17:40 | 2130 | 0.17863
1062 | 2019-03-30 17:41 | 2130 | 0.17367
1063 | 2019-03-30 17:42 | 2130 | 0.16871
1064 | 2019-03-30 17:43 | 2130 | 0.16374
1065 | 2019-03-30 17:44 | 2130 | 0.15382
1066 | 2019-03-30 17:45 | 2130 | 0.14886
1067 | 2019-03-30 17:46 | 2130 | 0.1439
1068 | 2019-03-30 17:47 | 2130 | 0.13893
1069 | 2019-03-30 17:48 | 2130 | 0.13893
1070 | 2019-03-30 17:49 | 2130 | 0.12901
1071 | 2019-03-30 17:50 | 2130 | 0.12901
1072 | 2019-03-30 17:51 | 2130 | 0.12405
1073 | 2019-03-30 17:52 | 2130 | 0.11909
1074 | 2019-03-30 17:53 | 2130 | 0.11909
1075 | 2019-03-30 17:54 | 2130 | 0.11413
1076 | 2019-03-30 17:55 | 2130 | 0.10916
1077 | 2019-03-30 17:56 | 2130 | 0.10916
1078 | 2019-03-30 17:57 | 2130 | 0.1042
1079 | 2019-03-30 17:58 | 2130 | 0.1042
1080 | 2019-03-30 17:59 | 2130 | 0.1042
1081 | 2019-03-30 18:00 | 2131 | 0.094277
1082 | 2019-03-30 18:01 | 2131 | 0.099239
1083 | 2019-03-30 18:02 | 2131 | 0.094277
1084 | 2019-03-30 18:03 | 2131 | 0.089315
1085 | 2019-03-30 18:04 | 2131 | 0.084353
1086 | 2019-03-30 18:05 | 2131 | 0.089315
1087 | 2019-03-30 18:06 | 2131 | 0.079391
1088 | 2019-03-30 18:07 | 2131 | 0.079391
1089 | 2019-03-30 18:08 | 2131 | 0.074429
1090 | 2019-03-30 18:09 | 2131 | 0.074429
1091 | 2019-03-30 18:10 | 2131 | 0.064505
1092 | 2019-03-30 18:11 | 2131 | 0.064505
1093 | 2019-03-30 18:12 | 2131 | 0.059543
1094 | 2019-03-30 18:13 | 2131 | 0.04962
1095 | 2019-03-30 18:14 | 2131 | 0.04962
1096 | 2019-03-30 18:15 | 2131 | 0.04962
1097 | 2019-03-30 18:16 | 2131 | 0.039696
1098 | 2019-03-30 18:17 | 2131 | 0.039696
1099 | 2019-03-30 18:18 | 2131 | 0.034734
1100 | 2019-03-30 18:19 | 2131 | 0.034734
1101 | 2019-03-30 18:20 | 2131 | 0.029772
1102 | 2019-03-30 18:21 | 2131 | 0.02481
1103 | 2019-03-30 18:22 | 2131 | 0.029772
1104 | 2019-03-30 18:23 | 2131 | 0.019848
1105 | 2019-03-30 18:24 | 2131 | 0.02481
1106 | 2019-03-30 18:25 | 2131 | 0.019848
1107 | 2019-03-30 18:26 | 2131 | 0.019848
1108 | 2019-03-30 18:27 | 2131 | 0.014886
1109 | 2019-03-30 18:28 | 2131 | 0.014886
1110 | 2019-03-30 18:29 | 2131 | 0.014886
1111 | 2019-03-30 18:30 | 2131 | 0.014886
1112 | 2019-03-30 18:31 | 2131 | 0.0099239
1113 | 2019-03-30 18:32 | 2131 | 0.014886
1114 | 2019-03-30 18:33 | 2131 | 0.0099239
1115 | 2019-03-30 18:34 | 2131 | 0.0099239
1116 | 2019-03-30 18:35 | 2131 | 0.0099239
1117 | 2019-03-30 18:36 | 2131 | 0.004962
1118 | 2019-03-30 18:37 | 2131 | 0.0099239
1119 | 2019-03-30 18:38 | 2131 | 0.004962
1120 | 2019-03-30 18:39 | 2131 | 0.004962
1121 | 2019-03-30 18:40 | 2131 | 0.004962
1122 | 2019-03-30 18:41 | 2131 | 0.004962
1123 | 2019-03-30 18:42 | 2131 | 0.004962
1124 | 2019-03-30 18:43 | 2131 | 0
1125 | 2019-03-30 18:44 | 2131 | 0.004962
1126 | 2019-03-30 18:45 | 2131 | 0
1127 | 2019-03-30 18:46 | 2131 | 0.004962
1128 | 2019-03-30 18:47 | 2131 | 0
1129 | 2019-03-30 18:48 | 2131 | 0
1130 | 2019-03-30 18:49 | 2131 | 0
1131 | 2019-03-30 18:50 | 2131 | 0
1132 | 2019-03-30 18:51 | 2131 | 0
1133 | 2019-03-30 18:52 | 2131 | 0
1134 | 2019-03-30 18:53 | 2131 | 0
1135 | 2019-03-30 18:54 | 2131 | 0
1136 | 2019-03-30 18:55 | 2131 | 0
1137 | 2019-03-30 18:56 | 2131 | 0
1138 | 2019-03-30 18:57 | 2131 | 0
1139 | 2019-03-30 18:58 | 2131 | 0
1140 | 2019-03-30 18:59 | 2131 | 0
1141 | 2019-03-30 19:00 | 2132 | 0
1142 | 2019-03-30 19:01 | 2132 | 0
1143 | 2019-03-30 19:02 | 2132 | 0
1144 | 2019-03-30 19:03 | 2132 | 0
1145 | 2019-03-30 19:04 | 2132 | 0
1146 | 2019-03-30 19:05 | 2132 | 0
1147 | 2019-03-30 19:06 | 2132 | 0
1148 | 2019-03-30 19:07 | 2132 | 0
1149 | 2019-03-30 19:08 | 2132 | 0
1150 | 2019-03-30 19:09 | 2132 | 0
1151 | 2019-03-30 19:10 | 2132 | 0
1152 | 2019-03-30 19:11 | 2132 | 0
1153 | 2019-03-30 19:12 | 2132 | 0
1154 | 2019-03-30 19:13 | 2132 | 0
1155 | 2019-03-30 19:14 | 2132 | 0
1156 | 2019-03-30 19:15 | 2132 | 0
1157 | 2019-03-30 19:16 | 2132 | 0
1158 | 2019-03-30 19:17 | 2132 | 0
1159 | 2019-03-30 19:18 | 2132 | 0
1160 | 2019-03-30 19:19 | 2132 | 0
1161 | 2019-03-30 19:20 | 2132 | 0
1162 | 2019-03-30 19:21 | 2132 | 0
1163 | 2019-03-30 19:22 | 2132 | 0
1164 | 2019-03-30 19:23 | 2132 | 0
1165 | 2019-03-30 19:24 | 2132 | 0
1166 | 2019-03-30 19:25 | 2132 | 0
1167 | 2019-03-30 19:26 | 2132 | 0
1168 | 2019-03-30 19:27 | 2132 | 0
1169 | 2019-03-30 19:28 | 2132 | 0
1170 | 2019-03-30 19:29 | 2132 | 0
1171 | 2019-03-30 19:30 | 2132 | 0
1172 | 2019-03-30 19:31 | 2132 | 0
1173 | 2019-03-30 19:32 | 2132 | 0
1174 | 2019-03-30 19:33 | 2132 | 0
1175 | 2019-03-30 19:34 | 2132 | 0
1176 | 2019-03-30 19:35 | 2132 | 0
1177 | 2019-03-30 19:36 | 2132 | 0
1178 | 2019-03-30 19:37 | 2132 | 0
1179 | 2019-03-30 19:38 | 2132 | 0
1180 | 2019-03-30 19:39 | 2132 | 0
1181 | 2019-03-30 19:40 | 2132 | 0
1182 | 2019-03-30 19:41 | 2132 | 0
1183 | 2019-03-30 19:42 | 2132 | 0
1184 | 2019-03-30 19:43 | 2132 | 0
1185 | 2019-03-30 19:44 | 2132 | 0
1186 | 2019-03-30 19:45 | 2132 | 0
1187 | 2019-03-30 19:46 | 2132 | 0
1188 | 2019-03-30 19:47 | 2132 | 0
1189 | 2019-03-30 19:48 | 2132 | 0
1190 | 2019-03-30 19:49 | 2132 | 0
1191 | 2019-03-30 19:50 | 2132 | 0
1192 | 2019-03-30 19:51 | 2132 | 0
1193 | 2019-03-30 19:52 | 2132 | 0
1194 | 2019-03-30 19:53 | 2132 | 0
1195 | 2019-03-30 19:54 | 2132 | 0
1196 | 2019-03-30 19:55 | 2132 | 0
1197 | 2019-03-30 19:56 | 2132 | 0
1198 | 2019-03-30 19:57 | 2132 | 0
1199 | 2019-03-30 19:58 | 2132 | 0
1200 | 2019-03-30 19:59 | 2132 | 0
1201 | 2019-03-30 20:00 | 2132 | 0
1202 | 2019-03-30 20:01 | 2133 | 0
1203 | 2019-03-30 20:02 | 2133 | 0
1204 | 2019-03-30 20:03 | 2133 | 0
1205 | 2019-03-30 20:04 | 2133 | 0
1206 | 2019-03-30 20:05 | 2133 | 0
1207 | 2019-03-30 20:06 | 2133 | 0
1208 | 2019-03-30 20:07 | 2133 | 0
1209 | 2019-03-30 20:08 | 2133 | 0
1210 | 2019-03-30 20:09 | 2133 | 0
1211 | 2019-03-30 20:10 | 2133 | 0
1212 | 2019-03-30 20:11 | 2133 | 0
1213 | 2019-03-30 20:12 | 2133 | 0
1214 | 2019-03-30 20:13 | 2133 | 0
1215 | 2019-03-30 20:14 | 2133 | 0
1216 | 2019-03-30 20:15 | 2133 | 0
1217 | 2019-03-30 20:16 | 2133 | 0
1218 | 2019-03-30 20:17 | 2133 | 0
1219 | 2019-03-30 20:18 | 2133 | 0
1220 | 2019-03-30 20:19 | 2133 | 0
1221 | 2019-03-30 20:20 | 2133 | 0
1222 | 2019-03-30 20:21 | 2133 | 0
1223 | 2019-03-30 20:22 | 2133 | 0
1224 | 2019-03-30 20:23 | 2133 | 0
1225 | 2019-03-30 20:24 | 2133 | 0
1226 | 2019-03-30 20:25 | 2133 | 0
1227 | 2019-03-30 20:26 | 2133 | 0
1228 | 2019-03-30 20:27 | 2133 | 0
1229 | 2019-03-30 20:28 | 2133 | 0
1230 | 2019-03-30 20:29 | 2133 | 0
1231 | 2019-03-30 20:30 | 2133 | 0
1232 | 2019-03-30 20:31 | 2133 | 0
1233 | 2019-03-30 20:32 | 2133 | 0
1234 | 2019-03-30 20:33 | 2133 | 0
1235 | 2019-03-30 20:34 | 2133 | 0
1236 | 2019-03-30 20:35 | 2133 | 0
1237 | 2019-03-30 20:36 | 2133 | 0
1238 | 2019-03-30 20:37 | 2133 | 0
1239 | 2019-03-30 20:38 | 2133 | 0
1240 | 2019-03-30 20:39 | 2133 | 0
1241 | 2019-03-30 20:40 | 2133 | 0
1242 | 2019-03-30 20:41 | 2133 | 0
1243 | 2019-03-30 20:42 | 2133 | 0
1244 | 2019-03-30 20:43 | 2133 | 0
1245 | 2019-03-30 20:44 | 2133 | 0
1246 | 2019-03-30 20:45 | 2133 | 0
1247 | 2019-03-30 20:46 | 2133 | 0
1248 | 2019-03-30 20:47 | 2133 | 0
1249 | 2019-03-30 20:48 | 2133 | 0
1250 | 2019-03-30 20:49 | 2133 | 0
1251 | 2019-03-30 20:50 | 2133 | 0
1252 | 2019-03-30 20:51 | 2133 | 0
1253 | 2019-03-30 20:52 | 2133 | 0
1254 | 2019-03-30 20:53 | 2133 | 0
1255 | 2019-03-30 20:54 | 2133 | 0
1256 | 2019-03-30 20:55 | 2133 | 0
1257 | 2019-03-30 20:56 | 2133 | 0
1258 | 2019-03-30 20:57 | 2133 | 0
1259 | 2019-03-30 20:58 | 2133 | 0
1260 | 2019-03-30 20:59 | 2133 | 0
1261 | 2019-03-30 21:00 | 2134 | 0
1262 | 2019-03-30 21:01 | 2134 | 0
1263 | 2019-03-30 21:02 | 2134 | 0
1264 | 2019-03-30 21:03 | 2134 | 0
1265 | 2019-03-30 21:04 | 2134 | 0
1266 | 2019-03-30 21:05 | 2134 | 0
1267 | 2019-03-30 21:06 | 2134 | 0
1268 | 2019-03-30 21:07 | 2134 | 0
1269 | 2019-03-30 21:08 | 2134 | 0
1270 | 2019-03-30 21:09 | 2134 | 0
1271 | 2019-03-30 21:10 | 2134 | 0
1272 | 2019-03-30 21:11 | 2134 | 0
1273 | 2019-03-30 21:12 | 2134 | 0
1274 | 2019-03-30 21:13 | 2134 | 0
1275 | 2019-03-30 21:14 | 2134 | 0
1276 | 2019-03-30 21:15 | 2134 | 0
1277 | 2019-03-30 21:16 | 2134 | 0
1278 | 2019-03-30 21:17 | 2134 | 0
1279 | 2019-03-30 21:18 | 2134 | 0
1280 | 2019-03-30 21:19 | 2134 | 0
1281 | 2019-03-30 21:20 | 2134 | 0
1282 | 2019-03-30 21:21 | 2134 | 0
1283 | 2019-03-30 21:22 | 2134 | 0
1284 | 2019-03-30 21:23 | 2134 | 0
1285 | 2019-03-30 21:24 | 2134 | 0
1286 | 2019-03-30 21:25 | 2134 | 0
1287 | 2019-03-30 21:26 | 2134 | 0
1288 | 2019-03-30 21:27 | 2134 | 0
1289 | 2019-03-30 21:28 | 2134 | 0
1290 | 2019-03-30 21:29 | 2134 | 0
1291 | 2019-03-30 21:30 | 2134 | 0
1292 | 2019-03-30 21:31 | 2134 | 0
1293 | 2019-03-30 21:32 | 2134 | 0
1294 | 2019-03-30 21:33 | 2134 | 0
1295 | 2019-03-30 21:34 | 2134 | 0
1296 | 2019-03-30 21:35 | 2134 | 0
1297 | 2019-03-30 21:36 | 2134 | 0
1298 | 2019-03-30 21:37 | 2134 | 0
1299 | 2019-03-30 21:38 | 2134 | 0
1300 | 2019-03-30 21:39 | 2134 | 0
1301 | 2019-03-30 21:40 | 2134 | 0
1302 | 2019-03-30 21:41 | 2134 | 0
1303 | 2019-03-30 21:42 | 2134 | 0
1304 | 2019-03-30 21:43 | 2134 | 0
1305 | 2019-03-30 21:44 | 2134 | 0
1306 | 2019-03-30 21:45 | 2134 | 0
1307 | 2019-03-30 21:46 | 2134 | 0
1308 | 2019-03-30 21:47 | 2134 | 0
1309 | 2019-03-30 21:48 | 2134 | 0
1310 | 2019-03-30 21:49 | 2134 | 0
1311 | 2019-03-30 21:50 | 2134 | 0
1312 | 2019-03-30 21:51 | 2134 | 0
1313 | 2019-03-30 21:52 | 2134 | 0
1314 | 2019-03-30 21:53 | 2134 | 0
1315 | 2019-03-30 21:54 | 2134 | 0
1316 | 2019-03-30 21:55 | 2134 | 0
1317 | 2019-03-30 21:56 | 2134 | 0
1318 | 2019-03-30 21:57 | 2134 | 0
1319 | 2019-03-30 21:58 | 2134 | 0
1320 | 2019-03-30 21:59 | 2134 | 0
1321 | 2019-03-30 22:00 | 2135 | 0
1322 | 2019-03-30 22:01 | 2135 | 0
1323 | 2019-03-30 22:02 | 2135 | 0
1324 | 2019-03-30 22:03 | 2135 | 0
1325 | 2019-03-30 22:04 | 2135 | 0
1326 | 2019-03-30 22:05 | 2135 | 0
1327 | 2019-03-30 22:06 | 2135 | 0
1328 | 2019-03-30 22:07 | 2135 | 0
1329 | 2019-03-30 22:08 | 2135 | 0
1330 | 2019-03-30 22:09 | 2135 | 0
1331 | 2019-03-30 22:10 | 2135 | 0
1332 | 2019-03-30 22:11 | 2135 | 0
1333 | 2019-03-30 22:12 | 2135 | 0
1334 | 2019-03-30 22:13 | 2135 | 0
1335 | 2019-03-30 22:14 | 2135 | 0
1336 | 2019-03-30 22:15 | 2135 | 0
1337 | 2019-03-30 22:16 | 2135 | 0
1338 | 2019-03-30 22:17 | 2135 | 0
1339 | 2019-03-30 22:18 | 2135 | 0
1340 | 2019-03-30 22:19 | 2135 | 0
1341 | 2019-03-30 22:20 | 2135 | 0
1342 | 2019-03-30 22:21 | 2135 | 0
1343 | 2019-03-30 22:22 | 2135 | 0
1344 | 2019-03-30 22:23 | 2135 | 0
1345 | 2019-03-30 22:24 | 2135 | 0
1346 | 2019-03-30 22:25 | 2135 | 0
1347 | 2019-03-30 22:26 | 2135 | 0
1348 | 2019-03-30 22:27 | 2135 | 0
1349 | 2019-03-30 22:28 | 2135 | 0
1350 | 2019-03-30 22:29 | 2135 | 0
1351 | 2019-03-30 22:30 | 2135 | 0
1352 | 2019-03-30 22:31 | 2135 | 0
1353 | 2019-03-30 22:32 | 2135 | 0
1354 | 2019-03-30 22:33 | 2135 | 0
1355 | 2019-03-30 22:34 | 2135 | 0
1356 | 2019-03-30 22:35 | 2135 | 0
1357 | 2019-03-30 22:36 | 2135 | 0
1358 | 2019-03-30 22:37 | 2135 | 0
1359 | 2019-03-30 22:38 | 2135 | 0
1360 | 2019-03-30 22:39 | 2135 | 0
1361 | 2019-03-30 22:40 | 2135 | 0
1362 | 2019-03-30 22:41 | 2135 | 0
1363 | 2019-03-30 22:42 | 2135 | 0
1364 | 2019-03-30 22:43 | 2135 | 0
1365 | 2019-03-30 22:44 | 2135 | 0
1366 | 2019-03-30 22:45 | 2135 | 0
1367 | 2019-03-30 22:46 | 2135 | 0
1368 | 2019-03-30 22:47 | 2135 | 0
1369 | 2019-03-30 22:48 | 2135 | 0
1370 | 2019-03-30 22:49 | 2135 | 0
1371 | 2019-03-30 22:50 | 2135 | 0
1372 | 2019-03-30 22:51 | 2135 | 0
1373 | 2019-03-30 22:52 | 2135 | 0
1374 | 2019-03-30 22:53 | 2135 | 0
1375 | 2019-03-30 22:54 | 2135 | 0
1376 | 2019-03-30 22:55 | 2135 | 0
1377 | 2019-03-30 22:56 | 2135 | 0
1378 | 2019-03-30 22:57 | 2135 | 0
1379 | 2019-03-30 22:58 | 2135 | 0
1380 | 2019-03-30 22:59 | 2135 | 0
1381 | 2019-03-30 23:00 | 2135 | 0
1382 | 2019-03-30 23:01 | 2136 | 0
1383 | 2019-03-30 23:02 | 2136 | 0
1384 | 2019-03-30 23:03 | 2136 | 0
1385 | 2019-03-30 23:04 | 2136 | 0
1386 | 2019-03-30 23:05 | 2136 | 0
1387 | 2019-03-30 23:06 | 2136 | 0
1388 | 2019-03-30 23:07 | 2136 | 0
1389 | 2019-03-30 23:08 | 2136 | 0
1390 | 2019-03-30 23:09 | 2136 | 0
1391 | 2019-03-30 23:10 | 2136 | 0
1392 | 2019-03-30 23:11 | 2136 | 0
1393 | 2019-03-30 23:12 | 2136 | 0
1394 | 2019-03-30 23:13 | 2136 | 0
1395 | 2019-03-30 23:14 | 2136 | 0
1396 | 2019-03-30 23:15 | 2136 | 0
1397 | 2019-03-30 23:16 | 2136 | 0
1398 | 2019-03-30 23:17 | 2136 | 0
1399 | 2019-03-30 23:18 | 2136 | 0
1400 | 2019-03-30 23:19 | 2136 | 0
1401 | 2019-03-30 23:20 | 2136 | 0
1402 | 2019-03-30 23:21 | 2136 | 0
1403 | 2019-03-30 23:22 | 2136 | 0
1404 | 2019-03-30 23:23 | 2136 | 0
1405 | 2019-03-30 23:24 | 2136 | 0
1406 | 2019-03-30 23:25 | 2136 | 0
1407 | 2019-03-30 23:26 | 2136 | 0
1408 | 2019-03-30 23:27 | 2136 | 0
1409 | 2019-03-30 23:28 | 2136 | 0
1410 | 2019-03-30 23:29 | 2136 | 0
1411 | 2019-03-30 23:30 | 2136 | 0
1412 | 2019-03-30 23:31 | 2136 | 0
1413 | 2019-03-30 23:32 | 2136 | 0
1414 | 2019-03-30 23:33 | 2136 | 0
1415 | 2019-03-30 23:34 | 2136 | 0
1416 | 2019-03-30 23:35 | 2136 | 0
1417 | 2019-03-30 23:36 | 2136 | 0
1418 | 2019-03-30 23:37 | 2136 | 0
1419 | 2019-03-30 23:38 | 2136 | 0
1420 | 2019-03-30 23:39 | 2136 | 0
1421 | 2019-03-30 23:40 | 2136 | 0
1422 | 2019-03-30 23:41 | 2136 | 0
1423 | 2019-03-30 23:42 | 2136 | 0
1424 | 2019-03-30 23:43 | 2136 | 0
1425 | 2019-03-30 23:44 | 2136 | 0
1426 | 2019-03-30 23:45 | 2136 | 0
1427 | 2019-03-30 23:46 | 2136 | 0
1428 | 2019-03-30 23:47 | 2136 | 0
1429 | 2019-03-30 23:48 | 2136 | 0
1430 | 2019-03-30 23:49 | 2136 | 0
1431 | 2019-03-30 23:50 | 2136 | 0
1432 | 2019-03-30 23:51 | 2136 | 0
1433 | 2019-03-30 23:52 | 2136 | 0
1434 | 2019-03-30 23:53 | 2136 | 0
1435 | 2019-03-30 23:54 | 2136 | 0
1436 | 2019-03-30 23:55 | 2136 | 0
1437 | 2019-03-30 23:56 | 2136 | 0
1438 | 2019-03-30 23:57 | 2136 | 0
1439 | 2019-03-30 23:58 | 2136 | 0
1440 | 2019-03-30 23:59 | 2136 | 0

## Cloudy sky day
Timeserie | DATE_TIME | Hour of the year | Turin2019 PV-MEAS_high_resolution
1 | 2019-03-06 | 1537 | 0
2 | 2019-03-06 00:01 | 1537 | 0
3 | 2019-03-06 00:02 | 1537 | 0
4 | 2019-03-06 00:03 | 1537 | 0
5 | 2019-03-06 00:04 | 1537 | 0
6 | 2019-03-06 00:05 | 1537 | 0
7 | 2019-03-06 00:06 | 1537 | 0
8 | 2019-03-06 00:07 | 1537 | 0
9 | 2019-03-06 00:08 | 1537 | 0
10 | 2019-03-06 00:09 | 1537 | 0
11 | 2019-03-06 00:10 | 1537 | 0
12 | 2019-03-06 00:11 | 1537 | 0
13 | 2019-03-06 00:12 | 1537 | 0
14 | 2019-03-06 00:13 | 1537 | 0
15 | 2019-03-06 00:14 | 1537 | 0
16 | 2019-03-06 00:15 | 1537 | 0
17 | 2019-03-06 00:16 | 1537 | 0
18 | 2019-03-06 00:17 | 1537 | 0
19 | 2019-03-06 00:18 | 1537 | 0
20 | 2019-03-06 00:19 | 1537 | 0
21 | 2019-03-06 00:20 | 1537 | 0
22 | 2019-03-06 00:21 | 1537 | 0
23 | 2019-03-06 00:22 | 1537 | 0
24 | 2019-03-06 00:23 | 1537 | 0
25 | 2019-03-06 00:24 | 1537 | 0
26 | 2019-03-06 00:25 | 1537 | 0
27 | 2019-03-06 00:26 | 1537 | 0
28 | 2019-03-06 00:27 | 1537 | 0
29 | 2019-03-06 00:28 | 1537 | 0
30 | 2019-03-06 00:29 | 1537 | 0
31 | 2019-03-06 00:30 | 1537 | 0
32 | 2019-03-06 00:31 | 1537 | 0
33 | 2019-03-06 00:32 | 1537 | 0
34 | 2019-03-06 00:33 | 1537 | 0
35 | 2019-03-06 00:34 | 1537 | 0
36 | 2019-03-06 00:35 | 1537 | 0
37 | 2019-03-06 00:36 | 1537 | 0
38 | 2019-03-06 00:37 | 1537 | 0
39 | 2019-03-06 00:38 | 1537 | 0
40 | 2019-03-06 00:39 | 1537 | 0
41 | 2019-03-06 00:40 | 1537 | 0
42 | 2019-03-06 00:41 | 1537 | 0
43 | 2019-03-06 00:42 | 1537 | 0
44 | 2019-03-06 00:43 | 1537 | 0
45 | 2019-03-06 00:44 | 1537 | 0
46 | 2019-03-06 00:45 | 1537 | 0
47 | 2019-03-06 00:46 | 1537 | 0
48 | 2019-03-06 00:47 | 1537 | 0
49 | 2019-03-06 00:48 | 1537 | 0
50 | 2019-03-06 00:49 | 1537 | 0
51 | 2019-03-06 00:50 | 1537 | 0
52 | 2019-03-06 00:51 | 1537 | 0
53 | 2019-03-06 00:52 | 1537 | 0
54 | 2019-03-06 00:53 | 1537 | 0
55 | 2019-03-06 00:54 | 1537 | 0
56 | 2019-03-06 00:55 | 1537 | 0
57 | 2019-03-06 00:56 | 1537 | 0
58 | 2019-03-06 00:57 | 1537 | 0
59 | 2019-03-06 00:58 | 1537 | 0
60 | 2019-03-06 00:59 | 1537 | 0
61 | 2019-03-06 01:00 | 1538 | 0
62 | 2019-03-06 01:01 | 1538 | 0
63 | 2019-03-06 01:02 | 1538 | 0
64 | 2019-03-06 01:03 | 1538 | 0
65 | 2019-03-06 01:04 | 1538 | 0
66 | 2019-03-06 01:05 | 1538 | 0
67 | 2019-03-06 01:06 | 1538 | 0
68 | 2019-03-06 01:07 | 1538 | 0
69 | 2019-03-06 01:08 | 1538 | 0
70 | 2019-03-06 01:09 | 1538 | 0
71 | 2019-03-06 01:10 | 1538 | 0
72 | 2019-03-06 01:11 | 1538 | 0
73 | 2019-03-06 01:12 | 1538 | 0
74 | 2019-03-06 01:13 | 1538 | 0
75 | 2019-03-06 01:14 | 1538 | 0
76 | 2019-03-06 01:15 | 1538 | 0
77 | 2019-03-06 01:16 | 1538 | 0
78 | 2019-03-06 01:17 | 1538 | 0
79 | 2019-03-06 01:18 | 1538 | 0
80 | 2019-03-06 01:19 | 1538 | 0
81 | 2019-03-06 01:20 | 1538 | 0
82 | 2019-03-06 01:21 | 1538 | 0
83 | 2019-03-06 01:22 | 1538 | 0
84 | 2019-03-06 01:23 | 1538 | 0
85 | 2019-03-06 01:24 | 1538 | 0
86 | 2019-03-06 01:25 | 1538 | 0
87 | 2019-03-06 01:26 | 1538 | 0
88 | 2019-03-06 01:27 | 1538 | 0
89 | 2019-03-06 01:28 | 1538 | 0
90 | 2019-03-06 01:29 | 1538 | 0
91 | 2019-03-06 01:30 | 1538 | 0
92 | 2019-03-06 01:31 | 1538 | 0
93 | 2019-03-06 01:32 | 1538 | 0
94 | 2019-03-06 01:33 | 1538 | 0
95 | 2019-03-06 01:34 | 1538 | 0
96 | 2019-03-06 01:35 | 1538 | 0
97 | 2019-03-06 01:36 | 1538 | 0
98 | 2019-03-06 01:37 | 1538 | 0
99 | 2019-03-06 01:38 | 1538 | 0
100 | 2019-03-06 01:39 | 1538 | 0
101 | 2019-03-06 01:40 | 1538 | 0
102 | 2019-03-06 01:41 | 1538 | 0
103 | 2019-03-06 01:42 | 1538 | 0
104 | 2019-03-06 01:43 | 1538 | 0
105 | 2019-03-06 01:44 | 1538 | 0
106 | 2019-03-06 01:45 | 1538 | 0
107 | 2019-03-06 01:46 | 1538 | 0
108 | 2019-03-06 01:47 | 1538 | 0
109 | 2019-03-06 01:48 | 1538 | 0
110 | 2019-03-06 01:49 | 1538 | 0
111 | 2019-03-06 01:50 | 1538 | 0
112 | 2019-03-06 01:51 | 1538 | 0
113 | 2019-03-06 01:52 | 1538 | 0
114 | 2019-03-06 01:53 | 1538 | 0
115 | 2019-03-06 01:54 | 1538 | 0
116 | 2019-03-06 01:55 | 1538 | 0
117 | 2019-03-06 01:56 | 1538 | 0
118 | 2019-03-06 01:57 | 1538 | 0
119 | 2019-03-06 01:58 | 1538 | 0
120 | 2019-03-06 01:59 | 1538 | 0
121 | 2019-03-06 02:00 | 1538 | 0
122 | 2019-03-06 02:01 | 1539 | 0
123 | 2019-03-06 02:02 | 1539 | 0
124 | 2019-03-06 02:03 | 1539 | 0
125 | 2019-03-06 02:04 | 1539 | 0
126 | 2019-03-06 02:05 | 1539 | 0
127 | 2019-03-06 02:06 | 1539 | 0
128 | 2019-03-06 02:07 | 1539 | 0
129 | 2019-03-06 02:08 | 1539 | 0
130 | 2019-03-06 02:09 | 1539 | 0
131 | 2019-03-06 02:10 | 1539 | 0
132 | 2019-03-06 02:11 | 1539 | 0
133 | 2019-03-06 02:12 | 1539 | 0
134 | 2019-03-06 02:13 | 1539 | 0
135 | 2019-03-06 02:14 | 1539 | 0
136 | 2019-03-06 02:15 | 1539 | 0
137 | 2019-03-06 02:16 | 1539 | 0
138 | 2019-03-06 02:17 | 1539 | 0
139 | 2019-03-06 02:18 | 1539 | 0
140 | 2019-03-06 02:19 | 1539 | 0
141 | 2019-03-06 02:20 | 1539 | 0
142 | 2019-03-06 02:21 | 1539 | 0
143 | 2019-03-06 02:22 | 1539 | 0
144 | 2019-03-06 02:23 | 1539 | 0
145 | 2019-03-06 02:24 | 1539 | 0
146 | 2019-03-06 02:25 | 1539 | 0
147 | 2019-03-06 02:26 | 1539 | 0
148 | 2019-03-06 02:27 | 1539 | 0
149 | 2019-03-06 02:28 | 1539 | 0
150 | 2019-03-06 02:29 | 1539 | 0
151 | 2019-03-06 02:30 | 1539 | 0
152 | 2019-03-06 02:31 | 1539 | 0
153 | 2019-03-06 02:32 | 1539 | 0
154 | 2019-03-06 02:33 | 1539 | 0
155 | 2019-03-06 02:34 | 1539 | 0
156 | 2019-03-06 02:35 | 1539 | 0
157 | 2019-03-06 02:36 | 1539 | 0
158 | 2019-03-06 02:37 | 1539 | 0
159 | 2019-03-06 02:38 | 1539 | 0
160 | 2019-03-06 02:39 | 1539 | 0
161 | 2019-03-06 02:40 | 1539 | 0
162 | 2019-03-06 02:41 | 1539 | 0
163 | 2019-03-06 02:42 | 1539 | 0
164 | 2019-03-06 02:43 | 1539 | 0
165 | 2019-03-06 02:44 | 1539 | 0
166 | 2019-03-06 02:45 | 1539 | 0
167 | 2019-03-06 02:46 | 1539 | 0
168 | 2019-03-06 02:47 | 1539 | 0
169 | 2019-03-06 02:48 | 1539 | 0
170 | 2019-03-06 02:49 | 1539 | 0
171 | 2019-03-06 02:50 | 1539 | 0
172 | 2019-03-06 02:51 | 1539 | 0
173 | 2019-03-06 02:52 | 1539 | 0
174 | 2019-03-06 02:53 | 1539 | 0
175 | 2019-03-06 02:54 | 1539 | 0
176 | 2019-03-06 02:55 | 1539 | 0
177 | 2019-03-06 02:56 | 1539 | 0
178 | 2019-03-06 02:57 | 1539 | 0
179 | 2019-03-06 02:58 | 1539 | 0
180 | 2019-03-06 02:59 | 1539 | 0
181 | 2019-03-06 03:00 | 1540 | 0
182 | 2019-03-06 03:01 | 1540 | 0
183 | 2019-03-06 03:02 | 1540 | 0
184 | 2019-03-06 03:03 | 1540 | 0
185 | 2019-03-06 03:04 | 1540 | 0
186 | 2019-03-06 03:05 | 1540 | 0
187 | 2019-03-06 03:06 | 1540 | 0
188 | 2019-03-06 03:07 | 1540 | 0
189 | 2019-03-06 03:08 | 1540 | 0
190 | 2019-03-06 03:09 | 1540 | 0
191 | 2019-03-06 03:10 | 1540 | 0
192 | 2019-03-06 03:11 | 1540 | 0
193 | 2019-03-06 03:12 | 1540 | 0
194 | 2019-03-06 03:13 | 1540 | 0
195 | 2019-03-06 03:14 | 1540 | 0
196 | 2019-03-06 03:15 | 1540 | 0
197 | 2019-03-06 03:16 | 1540 | 0
198 | 2019-03-06 03:17 | 1540 | 0
199 | 2019-03-06 03:18 | 1540 | 0
200 | 2019-03-06 03:19 | 1540 | 0
201 | 2019-03-06 03:20 | 1540 | 0
202 | 2019-03-06 03:21 | 1540 | 0
203 | 2019-03-06 03:22 | 1540 | 0
204 | 2019-03-06 03:23 | 1540 | 0
205 | 2019-03-06 03:24 | 1540 | 0
206 | 2019-03-06 03:25 | 1540 | 0
207 | 2019-03-06 03:26 | 1540 | 0
208 | 2019-03-06 03:27 | 1540 | 0
209 | 2019-03-06 03:28 | 1540 | 0
210 | 2019-03-06 03:29 | 1540 | 0
211 | 2019-03-06 03:30 | 1540 | 0
212 | 2019-03-06 03:31 | 1540 | 0
213 | 2019-03-06 03:32 | 1540 | 0
214 | 2019-03-06 03:33 | 1540 | 0
215 | 2019-03-06 03:34 | 1540 | 0
216 | 2019-03-06 03:35 | 1540 | 0
217 | 2019-03-06 03:36 | 1540 | 0
218 | 2019-03-06 03:37 | 1540 | 0
219 | 2019-03-06 03:38 | 1540 | 0
220 | 2019-03-06 03:39 | 1540 | 0
221 | 2019-03-06 03:40 | 1540 | 0
222 | 2019-03-06 03:41 | 1540 | 0
223 | 2019-03-06 03:42 | 1540 | 0
224 | 2019-03-06 03:43 | 1540 | 0
225 | 2019-03-06 03:44 | 1540 | 0
226 | 2019-03-06 03:45 | 1540 | 0
227 | 2019-03-06 03:46 | 1540 | 0
228 | 2019-03-06 03:47 | 1540 | 0
229 | 2019-03-06 03:48 | 1540 | 0
230 | 2019-03-06 03:49 | 1540 | 0
231 | 2019-03-06 03:50 | 1540 | 0
232 | 2019-03-06 03:51 | 1540 | 0
233 | 2019-03-06 03:52 | 1540 | 0
234 | 2019-03-06 03:53 | 1540 | 0
235 | 2019-03-06 03:54 | 1540 | 0
236 | 2019-03-06 03:55 | 1540 | 0
237 | 2019-03-06 03:56 | 1540 | 0
238 | 2019-03-06 03:57 | 1540 | 0
239 | 2019-03-06 03:58 | 1540 | 0
240 | 2019-03-06 03:59 | 1540 | 0
241 | 2019-03-06 04:00 | 1541 | 0
242 | 2019-03-06 04:01 | 1541 | 0
243 | 2019-03-06 04:02 | 1541 | 0
244 | 2019-03-06 04:03 | 1541 | 0
245 | 2019-03-06 04:04 | 1541 | 0
246 | 2019-03-06 04:05 | 1541 | 0
247 | 2019-03-06 04:06 | 1541 | 0
248 | 2019-03-06 04:07 | 1541 | 0
249 | 2019-03-06 04:08 | 1541 | 0
250 | 2019-03-06 04:09 | 1541 | 0
251 | 2019-03-06 04:10 | 1541 | 0
252 | 2019-03-06 04:11 | 1541 | 0
253 | 2019-03-06 04:12 | 1541 | 0
254 | 2019-03-06 04:13 | 1541 | 0
255 | 2019-03-06 04:14 | 1541 | 0
256 | 2019-03-06 04:15 | 1541 | 0
257 | 2019-03-06 04:16 | 1541 | 0
258 | 2019-03-06 04:17 | 1541 | 0
259 | 2019-03-06 04:18 | 1541 | 0
260 | 2019-03-06 04:19 | 1541 | 0
261 | 2019-03-06 04:20 | 1541 | 0
262 | 2019-03-06 04:21 | 1541 | 0
263 | 2019-03-06 04:22 | 1541 | 0
264 | 2019-03-06 04:23 | 1541 | 0
265 | 2019-03-06 04:24 | 1541 | 0
266 | 2019-03-06 04:25 | 1541 | 0
267 | 2019-03-06 04:26 | 1541 | 0
268 | 2019-03-06 04:27 | 1541 | 0
269 | 2019-03-06 04:28 | 1541 | 0
270 | 2019-03-06 04:29 | 1541 | 0
271 | 2019-03-06 04:30 | 1541 | 0
272 | 2019-03-06 04:31 | 1541 | 0
273 | 2019-03-06 04:32 | 1541 | 0
274 | 2019-03-06 04:33 | 1541 | 0
275 | 2019-03-06 04:34 | 1541 | 0
276 | 2019-03-06 04:35 | 1541 | 0
277 | 2019-03-06 04:36 | 1541 | 0
278 | 2019-03-06 04:37 | 1541 | 0
279 | 2019-03-06 04:38 | 1541 | 0
280 | 2019-03-06 04:39 | 1541 | 0
281 | 2019-03-06 04:40 | 1541 | 0
282 | 2019-03-06 04:41 | 1541 | 0
283 | 2019-03-06 04:42 | 1541 | 0
284 | 2019-03-06 04:43 | 1541 | 0
285 | 2019-03-06 04:44 | 1541 | 0
286 | 2019-03-06 04:45 | 1541 | 0
287 | 2019-03-06 04:46 | 1541 | 0
288 | 2019-03-06 04:47 | 1541 | 0
289 | 2019-03-06 04:48 | 1541 | 0
290 | 2019-03-06 04:49 | 1541 | 0
291 | 2019-03-06 04:50 | 1541 | 0
292 | 2019-03-06 04:51 | 1541 | 0
293 | 2019-03-06 04:52 | 1541 | 0
294 | 2019-03-06 04:53 | 1541 | 0
295 | 2019-03-06 04:54 | 1541 | 0
296 | 2019-03-06 04:55 | 1541 | 0
297 | 2019-03-06 04:56 | 1541 | 0
298 | 2019-03-06 04:57 | 1541 | 0
299 | 2019-03-06 04:58 | 1541 | 0
300 | 2019-03-06 04:59 | 1541 | 0
301 | 2019-03-06 05:00 | 1541 | 0
302 | 2019-03-06 05:01 | 1542 | 0
303 | 2019-03-06 05:02 | 1542 | 0
304 | 2019-03-06 05:03 | 1542 | 0
305 | 2019-03-06 05:04 | 1542 | 0
306 | 2019-03-06 05:05 | 1542 | 0
307 | 2019-03-06 05:06 | 1542 | 0
308 | 2019-03-06 05:07 | 1542 | 0
309 | 2019-03-06 05:08 | 1542 | 0
310 | 2019-03-06 05:09 | 1542 | 0
311 | 2019-03-06 05:10 | 1542 | 0
312 | 2019-03-06 05:11 | 1542 | 0
313 | 2019-03-06 05:12 | 1542 | 0
314 | 2019-03-06 05:13 | 1542 | 0
315 | 2019-03-06 05:14 | 1542 | 0
316 | 2019-03-06 05:15 | 1542 | 0
317 | 2019-03-06 05:16 | 1542 | 0
318 | 2019-03-06 05:17 | 1542 | 0
319 | 2019-03-06 05:18 | 1542 | 0
320 | 2019-03-06 05:19 | 1542 | 0
321 | 2019-03-06 05:20 | 1542 | 0
322 | 2019-03-06 05:21 | 1542 | 0
323 | 2019-03-06 05:22 | 1542 | 0
324 | 2019-03-06 05:23 | 1542 | 0
325 | 2019-03-06 05:24 | 1542 | 0
326 | 2019-03-06 05:25 | 1542 | 0
327 | 2019-03-06 05:26 | 1542 | 0
328 | 2019-03-06 05:27 | 1542 | 0
329 | 2019-03-06 05:28 | 1542 | 0
330 | 2019-03-06 05:29 | 1542 | 0
331 | 2019-03-06 05:30 | 1542 | 0
332 | 2019-03-06 05:31 | 1542 | 0
333 | 2019-03-06 05:32 | 1542 | 0
334 | 2019-03-06 05:33 | 1542 | 0
335 | 2019-03-06 05:34 | 1542 | 0
336 | 2019-03-06 05:35 | 1542 | 0
337 | 2019-03-06 05:36 | 1542 | 0
338 | 2019-03-06 05:37 | 1542 | 0
339 | 2019-03-06 05:38 | 1542 | 0
340 | 2019-03-06 05:39 | 1542 | 0
341 | 2019-03-06 05:40 | 1542 | 0
342 | 2019-03-06 05:41 | 1542 | 0
343 | 2019-03-06 05:42 | 1542 | 0
344 | 2019-03-06 05:43 | 1542 | 0
345 | 2019-03-06 05:44 | 1542 | 0
346 | 2019-03-06 05:45 | 1542 | 0
347 | 2019-03-06 05:46 | 1542 | 0
348 | 2019-03-06 05:47 | 1542 | 0
349 | 2019-03-06 05:48 | 1542 | 0
350 | 2019-03-06 05:49 | 1542 | 0
351 | 2019-03-06 05:50 | 1542 | 0
352 | 2019-03-06 05:51 | 1542 | 0
353 | 2019-03-06 05:52 | 1542 | 0
354 | 2019-03-06 05:53 | 1542 | 0
355 | 2019-03-06 05:54 | 1542 | 0
356 | 2019-03-06 05:55 | 1542 | 0
357 | 2019-03-06 05:56 | 1542 | 0
358 | 2019-03-06 05:57 | 1542 | 0
359 | 2019-03-06 05:58 | 1542 | 0
360 | 2019-03-06 05:59 | 1542 | 0
361 | 2019-03-06 06:00 | 1543 | 0
362 | 2019-03-06 06:01 | 1543 | 0
363 | 2019-03-06 06:02 | 1543 | 0
364 | 2019-03-06 06:03 | 1543 | 0
365 | 2019-03-06 06:04 | 1543 | 0
366 | 2019-03-06 06:05 | 1543 | 0
367 | 2019-03-06 06:06 | 1543 | 0
368 | 2019-03-06 06:07 | 1543 | 0
369 | 2019-03-06 06:08 | 1543 | 0
370 | 2019-03-06 06:09 | 1543 | 0
371 | 2019-03-06 06:10 | 1543 | 0
372 | 2019-03-06 06:11 | 1543 | 0
373 | 2019-03-06 06:12 | 1543 | 0
374 | 2019-03-06 06:13 | 1543 | 0
375 | 2019-03-06 06:14 | 1543 | 0
376 | 2019-03-06 06:15 | 1543 | 0
377 | 2019-03-06 06:16 | 1543 | 0
378 | 2019-03-06 06:17 | 1543 | 0
379 | 2019-03-06 06:18 | 1543 | 0
380 | 2019-03-06 06:19 | 1543 | 0
381 | 2019-03-06 06:20 | 1543 | 0
382 | 2019-03-06 06:21 | 1543 | 0
383 | 2019-03-06 06:22 | 1543 | 0
384 | 2019-03-06 06:23 | 1543 | 0
385 | 2019-03-06 06:24 | 1543 | 0
386 | 2019-03-06 06:25 | 1543 | 0
387 | 2019-03-06 06:26 | 1543 | 0
388 | 2019-03-06 06:27 | 1543 | 0
389 | 2019-03-06 06:28 | 1543 | 0
390 | 2019-03-06 06:29 | 1543 | 0
391 | 2019-03-06 06:30 | 1543 | 0
392 | 2019-03-06 06:31 | 1543 | 0
393 | 2019-03-06 06:32 | 1543 | 0
394 | 2019-03-06 06:33 | 1543 | 0
395 | 2019-03-06 06:34 | 1543 | 0
396 | 2019-03-06 06:35 | 1543 | 0
397 | 2019-03-06 06:36 | 1543 | 0
398 | 2019-03-06 06:37 | 1543 | 0
399 | 2019-03-06 06:38 | 1543 | 0
400 | 2019-03-06 06:39 | 1543 | 0
401 | 2019-03-06 06:40 | 1543 | 0
402 | 2019-03-06 06:41 | 1543 | 0
403 | 2019-03-06 06:42 | 1543 | 0
404 | 2019-03-06 06:43 | 1543 | 0
405 | 2019-03-06 06:44 | 1543 | 0
406 | 2019-03-06 06:45 | 1543 | 0
407 | 2019-03-06 06:46 | 1543 | 0
408 | 2019-03-06 06:47 | 1543 | 0
409 | 2019-03-06 06:48 | 1543 | 0
410 | 2019-03-06 06:49 | 1543 | 0
411 | 2019-03-06 06:50 | 1543 | 0
412 | 2019-03-06 06:51 | 1543 | 0
413 | 2019-03-06 06:52 | 1543 | 0
414 | 2019-03-06 06:53 | 1543 | 0
415 | 2019-03-06 06:54 | 1543 | 0
416 | 2019-03-06 06:55 | 1543 | 0
417 | 2019-03-06 06:56 | 1543 | 0
418 | 2019-03-06 06:57 | 1543 | 0
419 | 2019-03-06 06:58 | 1543 | 0
420 | 2019-03-06 06:59 | 1543 | 0
421 | 2019-03-06 07:00 | 1544 | 0
422 | 2019-03-06 07:01 | 1544 | 0
423 | 2019-03-06 07:02 | 1544 | 0
424 | 2019-03-06 07:03 | 1544 | 0
425 | 2019-03-06 07:04 | 1544 | 0
426 | 2019-03-06 07:05 | 1544 | 0
427 | 2019-03-06 07:06 | 1544 | 0
428 | 2019-03-06 07:07 | 1544 | 0.004962
429 | 2019-03-06 07:08 | 1544 | 0
430 | 2019-03-06 07:09 | 1544 | 0
431 | 2019-03-06 07:10 | 1544 | 0.004962
432 | 2019-03-06 07:11 | 1544 | 0.004962
433 | 2019-03-06 07:12 | 1544 | 0.004962
434 | 2019-03-06 07:13 | 1544 | 0.004962
435 | 2019-03-06 07:14 | 1544 | 0.0099239
436 | 2019-03-06 07:15 | 1544 | 0.0099239
437 | 2019-03-06 07:16 | 1544 | 0.0099239
438 | 2019-03-06 07:17 | 1544 | 0.0099239
439 | 2019-03-06 07:18 | 1544 | 0.014886
440 | 2019-03-06 07:19 | 1544 | 0.0099239
441 | 2019-03-06 07:20 | 1544 | 0.014886
442 | 2019-03-06 07:21 | 1544 | 0.014886
443 | 2019-03-06 07:22 | 1544 | 0.014886
444 | 2019-03-06 07:23 | 1544 | 0.014886
445 | 2019-03-06 07:24 | 1544 | 0.014886
446 | 2019-03-06 07:25 | 1544 | 0.014886
447 | 2019-03-06 07:26 | 1544 | 0.019848
448 | 2019-03-06 07:27 | 1544 | 0.019848
449 | 2019-03-06 07:28 | 1544 | 0.014886
450 | 2019-03-06 07:29 | 1544 | 0.019848
451 | 2019-03-06 07:30 | 1544 | 0.02481
452 | 2019-03-06 07:31 | 1544 | 0.019848
453 | 2019-03-06 07:32 | 1544 | 0.019848
454 | 2019-03-06 07:33 | 1544 | 0.02481
455 | 2019-03-06 07:34 | 1544 | 0.02481
456 | 2019-03-06 07:35 | 1544 | 0.02481
457 | 2019-03-06 07:36 | 1544 | 0.02481
458 | 2019-03-06 07:37 | 1544 | 0.02481
459 | 2019-03-06 07:38 | 1544 | 0.029772
460 | 2019-03-06 07:39 | 1544 | 0.02481
461 | 2019-03-06 07:40 | 1544 | 0.029772
462 | 2019-03-06 07:41 | 1544 | 0.029772
463 | 2019-03-06 07:42 | 1544 | 0.029772
464 | 2019-03-06 07:43 | 1544 | 0.034734
465 | 2019-03-06 07:44 | 1544 | 0.034734
466 | 2019-03-06 07:45 | 1544 | 0.034734
467 | 2019-03-06 07:46 | 1544 | 0.039696
468 | 2019-03-06 07:47 | 1544 | 0.039696
469 | 2019-03-06 07:48 | 1544 | 0.039696
470 | 2019-03-06 07:49 | 1544 | 0.044658
471 | 2019-03-06 07:50 | 1544 | 0.04962
472 | 2019-03-06 07:51 | 1544 | 0.044658
473 | 2019-03-06 07:52 | 1544 | 0.044658
474 | 2019-03-06 07:53 | 1544 | 0.044658
475 | 2019-03-06 07:54 | 1544 | 0.04962
476 | 2019-03-06 07:55 | 1544 | 0.044658
477 | 2019-03-06 07:56 | 1544 | 0.04962
478 | 2019-03-06 07:57 | 1544 | 0.054582
479 | 2019-03-06 07:58 | 1544 | 0.04962
480 | 2019-03-06 07:59 | 1544 | 0.04962
481 | 2019-03-06 08:00 | 1544 | 0.054582
482 | 2019-03-06 08:01 | 1545 | 0.059543
483 | 2019-03-06 08:02 | 1545 | 0.059543
484 | 2019-03-06 08:03 | 1545 | 0.059543
485 | 2019-03-06 08:04 | 1545 | 0.064505
486 | 2019-03-06 08:05 | 1545 | 0.069467
487 | 2019-03-06 08:06 | 1545 | 0.069467
488 | 2019-03-06 08:07 | 1545 | 0.069467
489 | 2019-03-06 08:08 | 1545 | 0.069467
490 | 2019-03-06 08:09 | 1545 | 0.074429
491 | 2019-03-06 08:10 | 1545 | 0.079391
492 | 2019-03-06 08:11 | 1545 | 0.079391
493 | 2019-03-06 08:12 | 1545 | 0.079391
494 | 2019-03-06 08:13 | 1545 | 0.089315
495 | 2019-03-06 08:14 | 1545 | 0.094277
496 | 2019-03-06 08:15 | 1545 | 0.094277
497 | 2019-03-06 08:16 | 1545 | 0.1042
498 | 2019-03-06 08:17 | 1545 | 0.1042
499 | 2019-03-06 08:18 | 1545 | 0.11413
500 | 2019-03-06 08:19 | 1545 | 0.11413
501 | 2019-03-06 08:20 | 1545 | 0.11413
502 | 2019-03-06 08:21 | 1545 | 0.11909
503 | 2019-03-06 08:22 | 1545 | 0.11413
504 | 2019-03-06 08:23 | 1545 | 0.11413
505 | 2019-03-06 08:24 | 1545 | 0.11413
506 | 2019-03-06 08:25 | 1545 | 0.12405
507 | 2019-03-06 08:26 | 1545 | 0.12405
508 | 2019-03-06 08:27 | 1545 | 0.13893
509 | 2019-03-06 08:28 | 1545 | 0.13893
510 | 2019-03-06 08:29 | 1545 | 0.14886
511 | 2019-03-06 08:30 | 1545 | 0.14886
512 | 2019-03-06 08:31 | 1545 | 0.15382
513 | 2019-03-06 08:32 | 1545 | 0.15878
514 | 2019-03-06 08:33 | 1545 | 0.15878
515 | 2019-03-06 08:34 | 1545 | 0.15878
516 | 2019-03-06 08:35 | 1545 | 0.15382
517 | 2019-03-06 08:36 | 1545 | 0.15878
518 | 2019-03-06 08:37 | 1545 | 0.16374
519 | 2019-03-06 08:38 | 1545 | 0.16374
520 | 2019-03-06 08:39 | 1545 | 0.16871
521 | 2019-03-06 08:40 | 1545 | 0.17367
522 | 2019-03-06 08:41 | 1545 | 0.18359
523 | 2019-03-06 08:42 | 1545 | 0.18359
524 | 2019-03-06 08:43 | 1545 | 0.14886
525 | 2019-03-06 08:44 | 1545 | 0.1439
526 | 2019-03-06 08:45 | 1545 | 0.1439
527 | 2019-03-06 08:46 | 1545 | 0.15878
528 | 2019-03-06 08:47 | 1545 | 0.19352
529 | 2019-03-06 08:48 | 1545 | 0.20344
530 | 2019-03-06 08:49 | 1545 | 0.2084
531 | 2019-03-06 08:50 | 1545 | 0.19848
532 | 2019-03-06 08:51 | 1545 | 0.17367
533 | 2019-03-06 08:52 | 1545 | 0.13893
534 | 2019-03-06 08:53 | 1545 | 0.15382
535 | 2019-03-06 08:54 | 1545 | 0.17863
536 | 2019-03-06 08:55 | 1545 | 0.19352
537 | 2019-03-06 08:56 | 1545 | 0.21336
538 | 2019-03-06 08:57 | 1545 | 0.2084
539 | 2019-03-06 08:58 | 1545 | 0.20344
540 | 2019-03-06 08:59 | 1545 | 0.20344
541 | 2019-03-06 09:00 | 1546 | 0.19848
542 | 2019-03-06 09:01 | 1546 | 0.19848
543 | 2019-03-06 09:02 | 1546 | 0.18359
544 | 2019-03-06 09:03 | 1546 | 0.16374
545 | 2019-03-06 09:04 | 1546 | 0.17367
546 | 2019-03-06 09:05 | 1546 | 0.20344
547 | 2019-03-06 09:06 | 1546 | 0.21833
548 | 2019-03-06 09:07 | 1546 | 0.24314
549 | 2019-03-06 09:08 | 1546 | 0.2481
550 | 2019-03-06 09:09 | 1546 | 0.23321
551 | 2019-03-06 09:10 | 1546 | 0.22825
552 | 2019-03-06 09:11 | 1546 | 0.21833
553 | 2019-03-06 09:12 | 1546 | 0.21833
554 | 2019-03-06 09:13 | 1546 | 0.23321
555 | 2019-03-06 09:14 | 1546 | 0.24314
556 | 2019-03-06 09:15 | 1546 | 0.25802
557 | 2019-03-06 09:16 | 1546 | 0.25802
558 | 2019-03-06 09:17 | 1546 | 0.27291
559 | 2019-03-06 09:18 | 1546 | 0.26298
560 | 2019-03-06 09:19 | 1546 | 0.18359
561 | 2019-03-06 09:20 | 1546 | 0.19848
562 | 2019-03-06 09:21 | 1546 | 0.23817
563 | 2019-03-06 09:22 | 1546 | 0.27291
564 | 2019-03-06 09:23 | 1546 | 0.26795
565 | 2019-03-06 09:24 | 1546 | 0.26298
566 | 2019-03-06 09:25 | 1546 | 0.26298
567 | 2019-03-06 09:26 | 1546 | 0.25802
568 | 2019-03-06 09:27 | 1546 | 0.25802
569 | 2019-03-06 09:28 | 1546 | 0.25802
570 | 2019-03-06 09:29 | 1546 | 0.25802
571 | 2019-03-06 09:30 | 1546 | 0.26298
572 | 2019-03-06 09:31 | 1546 | 0.25802
573 | 2019-03-06 09:32 | 1546 | 0.25306
574 | 2019-03-06 09:33 | 1546 | 0.28779
575 | 2019-03-06 09:34 | 1546 | 0.32253
576 | 2019-03-06 09:35 | 1546 | 0.32253
577 | 2019-03-06 09:36 | 1546 | 0.33245
578 | 2019-03-06 09:37 | 1546 | 0.3523
579 | 2019-03-06 09:38 | 1546 | 0.37711
580 | 2019-03-06 09:39 | 1546 | 0.42177
581 | 2019-03-06 09:40 | 1546 | 0.43665
582 | 2019-03-06 09:41 | 1546 | 0.44161
583 | 2019-03-06 09:42 | 1546 | 0.42177
584 | 2019-03-06 09:43 | 1546 | 0.34734
585 | 2019-03-06 09:44 | 1546 | 0.31757
586 | 2019-03-06 09:45 | 1546 | 0.30764
587 | 2019-03-06 09:46 | 1546 | 0.32749
588 | 2019-03-06 09:47 | 1546 | 0.30268
589 | 2019-03-06 09:48 | 1546 | 0.29276
590 | 2019-03-06 09:49 | 1546 | 0.26795
591 | 2019-03-06 09:50 | 1546 | 0.26795
592 | 2019-03-06 09:51 | 1546 | 0.28779
593 | 2019-03-06 09:52 | 1546 | 0.28779
594 | 2019-03-06 09:53 | 1546 | 0.30764
595 | 2019-03-06 09:54 | 1546 | 0.33741
596 | 2019-03-06 09:55 | 1546 | 0.33245
597 | 2019-03-06 09:56 | 1546 | 0.34734
598 | 2019-03-06 09:57 | 1546 | 0.36222
599 | 2019-03-06 09:58 | 1546 | 0.36222
600 | 2019-03-06 09:59 | 1546 | 0.3523
601 | 2019-03-06 10:00 | 1547 | 0.32253
602 | 2019-03-06 10:01 | 1547 | 0.32749
603 | 2019-03-06 10:02 | 1547 | 0.32253
604 | 2019-03-06 10:03 | 1547 | 0.30764
605 | 2019-03-06 10:04 | 1547 | 0.30764
606 | 2019-03-06 10:05 | 1547 | 0.29772
607 | 2019-03-06 10:06 | 1547 | 0.28283
608 | 2019-03-06 10:07 | 1547 | 0.30268
609 | 2019-03-06 10:08 | 1547 | 0.29772
610 | 2019-03-06 10:09 | 1547 | 0.26298
611 | 2019-03-06 10:10 | 1547 | 0.24314
612 | 2019-03-06 10:11 | 1547 | 0.23817
613 | 2019-03-06 10:12 | 1547 | 0.23817
614 | 2019-03-06 10:13 | 1547 | 0.25306
615 | 2019-03-06 10:14 | 1547 | 0.26795
616 | 2019-03-06 10:15 | 1547 | 0.27291
617 | 2019-03-06 10:16 | 1547 | 0.26298
618 | 2019-03-06 10:17 | 1547 | 0.2481
619 | 2019-03-06 10:18 | 1547 | 0.22329
620 | 2019-03-06 10:19 | 1547 | 0.22329
621 | 2019-03-06 10:20 | 1547 | 0.2084
622 | 2019-03-06 10:21 | 1547 | 0.25306
623 | 2019-03-06 10:22 | 1547 | 0.25306
624 | 2019-03-06 10:23 | 1547 | 0.26795
625 | 2019-03-06 10:24 | 1547 | 0.28779
626 | 2019-03-06 10:25 | 1547 | 0.28283
627 | 2019-03-06 10:26 | 1547 | 0.28779
628 | 2019-03-06 10:27 | 1547 | 0.33741
629 | 2019-03-06 10:28 | 1547 | 0.38703
630 | 2019-03-06 10:29 | 1547 | 0.39199
631 | 2019-03-06 10:30 | 1547 | 0.4168
632 | 2019-03-06 10:31 | 1547 | 0.43169
633 | 2019-03-06 10:32 | 1547 | 0.44658
634 | 2019-03-06 10:33 | 1547 | 0.43665
635 | 2019-03-06 10:34 | 1547 | 0.51108
636 | 2019-03-06 10:35 | 1547 | 0.53589
637 | 2019-03-06 10:36 | 1547 | 0.45154
638 | 2019-03-06 10:37 | 1547 | 0.43665
639 | 2019-03-06 10:38 | 1547 | 0.40688
640 | 2019-03-06 10:39 | 1547 | 0.39696
641 | 2019-03-06 10:40 | 1547 | 0.38703
642 | 2019-03-06 10:41 | 1547 | 0.44161
643 | 2019-03-06 10:42 | 1547 | 0.48627
644 | 2019-03-06 10:43 | 1547 | 0.48131
645 | 2019-03-06 10:44 | 1547 | 0.46146
646 | 2019-03-06 10:45 | 1547 | 0.43665
647 | 2019-03-06 10:46 | 1547 | 0.37711
648 | 2019-03-06 10:47 | 1547 | 0.3523
649 | 2019-03-06 10:48 | 1547 | 0.32749
650 | 2019-03-06 10:49 | 1547 | 0.36222
651 | 2019-03-06 10:50 | 1547 | 0.38703
652 | 2019-03-06 10:51 | 1547 | 0.36718
653 | 2019-03-06 10:52 | 1547 | 0.32749
654 | 2019-03-06 10:53 | 1547 | 0.37711
655 | 2019-03-06 10:54 | 1547 | 0.40192
656 | 2019-03-06 10:55 | 1547 | 0.42673
657 | 2019-03-06 10:56 | 1547 | 0.4565
658 | 2019-03-06 10:57 | 1547 | 0.38703
659 | 2019-03-06 10:58 | 1547 | 0.32253
660 | 2019-03-06 10:59 | 1547 | 0.33741
661 | 2019-03-06 11:00 | 1547 | 0.33741
662 | 2019-03-06 11:01 | 1548 | 0.33741
663 | 2019-03-06 11:02 | 1548 | 0.31757
664 | 2019-03-06 11:03 | 1548 | 0.32749
665 | 2019-03-06 11:04 | 1548 | 0.30764
666 | 2019-03-06 11:05 | 1548 | 0.27291
667 | 2019-03-06 11:06 | 1548 | 0.32749
668 | 2019-03-06 11:07 | 1548 | 0.3126
669 | 2019-03-06 11:08 | 1548 | 0.3126
670 | 2019-03-06 11:09 | 1548 | 0.32749
671 | 2019-03-06 11:10 | 1548 | 0.39199
672 | 2019-03-06 11:11 | 1548 | 0.34238
673 | 2019-03-06 11:12 | 1548 | 0.40192
674 | 2019-03-06 11:13 | 1548 | 0.4168
675 | 2019-03-06 11:14 | 1548 | 0.46146
676 | 2019-03-06 11:15 | 1548 | 0.45154
677 | 2019-03-06 11:16 | 1548 | 0.40192
678 | 2019-03-06 11:17 | 1548 | 0.39696
679 | 2019-03-06 11:18 | 1548 | 0.38703
680 | 2019-03-06 11:19 | 1548 | 0.36222
681 | 2019-03-06 11:20 | 1548 | 0.33741
682 | 2019-03-06 11:21 | 1548 | 0.35726
683 | 2019-03-06 11:22 | 1548 | 0.33741
684 | 2019-03-06 11:23 | 1548 | 0.3523
685 | 2019-03-06 11:24 | 1548 | 0.40688
686 | 2019-03-06 11:25 | 1548 | 0.37215
687 | 2019-03-06 11:26 | 1548 | 0.37711
688 | 2019-03-06 11:27 | 1548 | 0.3523
689 | 2019-03-06 11:28 | 1548 | 0.31757
690 | 2019-03-06 11:29 | 1548 | 0.33741
691 | 2019-03-06 11:30 | 1548 | 0.34238
692 | 2019-03-06 11:31 | 1548 | 0.40192
693 | 2019-03-06 11:32 | 1548 | 0.39696
694 | 2019-03-06 11:33 | 1548 | 0.32749
695 | 2019-03-06 11:34 | 1548 | 0.32749
696 | 2019-03-06 11:35 | 1548 | 0.32749
697 | 2019-03-06 11:36 | 1548 | 0.27787
698 | 2019-03-06 11:37 | 1548 | 0.29276
699 | 2019-03-06 11:38 | 1548 | 0.34238
700 | 2019-03-06 11:39 | 1548 | 0.34734
701 | 2019-03-06 11:40 | 1548 | 0.42673
702 | 2019-03-06 11:41 | 1548 | 0.38207
703 | 2019-03-06 11:42 | 1548 | 0.4565
704 | 2019-03-06 11:43 | 1548 | 0.50612
705 | 2019-03-06 11:44 | 1548 | 0.52101
706 | 2019-03-06 11:45 | 1548 | 0.46146
707 | 2019-03-06 11:46 | 1548 | 0.44161
708 | 2019-03-06 11:47 | 1548 | 0.46146
709 | 2019-03-06 11:48 | 1548 | 0.50612
710 | 2019-03-06 11:49 | 1548 | 0.4565
711 | 2019-03-06 11:50 | 1548 | 0.51108
712 | 2019-03-06 11:51 | 1548 | 0.51108
713 | 2019-03-06 11:52 | 1548 | 0.50612
714 | 2019-03-06 11:53 | 1548 | 0.40192
715 | 2019-03-06 11:54 | 1548 | 0.33245
716 | 2019-03-06 11:55 | 1548 | 0.36718
717 | 2019-03-06 11:56 | 1548 | 0.40688
718 | 2019-03-06 11:57 | 1548 | 0.36222
719 | 2019-03-06 11:58 | 1548 | 0.26298
720 | 2019-03-06 11:59 | 1548 | 0.22825
721 | 2019-03-06 12:00 | 1549 | 0.22329
722 | 2019-03-06 12:01 | 1549 | 0.21833
723 | 2019-03-06 12:02 | 1549 | 0.21336
724 | 2019-03-06 12:03 | 1549 | 0.21336
725 | 2019-03-06 12:04 | 1549 | 0.2084
726 | 2019-03-06 12:05 | 1549 | 0.2084
727 | 2019-03-06 12:06 | 1549 | 0.21336
728 | 2019-03-06 12:07 | 1549 | 0.2084
729 | 2019-03-06 12:08 | 1549 | 0.2084
730 | 2019-03-06 12:09 | 1549 | 0.21336
731 | 2019-03-06 12:10 | 1549 | 0.21833
732 | 2019-03-06 12:11 | 1549 | 0.21336
733 | 2019-03-06 12:12 | 1549 | 0.21833
734 | 2019-03-06 12:13 | 1549 | 0.21336
735 | 2019-03-06 12:14 | 1549 | 0.2084
736 | 2019-03-06 12:15 | 1549 | 0.2084
737 | 2019-03-06 12:16 | 1549 | 0.2084
738 | 2019-03-06 12:17 | 1549 | 0.19848
739 | 2019-03-06 12:18 | 1549 | 0.20344
740 | 2019-03-06 12:19 | 1549 | 0.19848
741 | 2019-03-06 12:20 | 1549 | 0.19848
742 | 2019-03-06 12:21 | 1549 | 0.20344
743 | 2019-03-06 12:22 | 1549 | 0.20344
744 | 2019-03-06 12:23 | 1549 | 0.2084
745 | 2019-03-06 12:24 | 1549 | 0.21336
746 | 2019-03-06 12:25 | 1549 | 0.22329
747 | 2019-03-06 12:26 | 1549 | 0.22329
748 | 2019-03-06 12:27 | 1549 | 0.24314
749 | 2019-03-06 12:28 | 1549 | 0.25802
750 | 2019-03-06 12:29 | 1549 | 0.26795
751 | 2019-03-06 12:30 | 1549 | 0.27291
752 | 2019-03-06 12:31 | 1549 | 0.27291
753 | 2019-03-06 12:32 | 1549 | 0.27787
754 | 2019-03-06 12:33 | 1549 | 0.28283
755 | 2019-03-06 12:34 | 1549 | 0.27787
756 | 2019-03-06 12:35 | 1549 | 0.25802
757 | 2019-03-06 12:36 | 1549 | 0.2481
758 | 2019-03-06 12:37 | 1549 | 0.23321
759 | 2019-03-06 12:38 | 1549 | 0.22329
760 | 2019-03-06 12:39 | 1549 | 0.21833
761 | 2019-03-06 12:40 | 1549 | 0.21336
762 | 2019-03-06 12:41 | 1549 | 0.21336
763 | 2019-03-06 12:42 | 1549 | 0.20344
764 | 2019-03-06 12:43 | 1549 | 0.2084
765 | 2019-03-06 12:44 | 1549 | 0.20344
766 | 2019-03-06 12:45 | 1549 | 0.20344
767 | 2019-03-06 12:46 | 1549 | 0.2084
768 | 2019-03-06 12:47 | 1549 | 0.21336
769 | 2019-03-06 12:48 | 1549 | 0.21833
770 | 2019-03-06 12:49 | 1549 | 0.21833
771 | 2019-03-06 12:50 | 1549 | 0.22825
772 | 2019-03-06 12:51 | 1549 | 0.23321
773 | 2019-03-06 12:52 | 1549 | 0.23817
774 | 2019-03-06 12:53 | 1549 | 0.2481
775 | 2019-03-06 12:54 | 1549 | 0.2481
776 | 2019-03-06 12:55 | 1549 | 0.23321
777 | 2019-03-06 12:56 | 1549 | 0.23321
778 | 2019-03-06 12:57 | 1549 | 0.23321
779 | 2019-03-06 12:58 | 1549 | 0.23817
780 | 2019-03-06 12:59 | 1549 | 0.22825
781 | 2019-03-06 13:00 | 1550 | 0.23321
782 | 2019-03-06 13:01 | 1550 | 0.23321
783 | 2019-03-06 13:02 | 1550 | 0.23321
784 | 2019-03-06 13:03 | 1550 | 0.22825
785 | 2019-03-06 13:04 | 1550 | 0.22825
786 | 2019-03-06 13:05 | 1550 | 0.22825
787 | 2019-03-06 13:06 | 1550 | 0.23321
788 | 2019-03-06 13:07 | 1550 | 0.23817
789 | 2019-03-06 13:08 | 1550 | 0.2481
790 | 2019-03-06 13:09 | 1550 | 0.26795
791 | 2019-03-06 13:10 | 1550 | 0.28283
792 | 2019-03-06 13:11 | 1550 | 0.30764
793 | 2019-03-06 13:12 | 1550 | 0.34238
794 | 2019-03-06 13:13 | 1550 | 0.35726
795 | 2019-03-06 13:14 | 1550 | 0.38703
796 | 2019-03-06 13:15 | 1550 | 0.46642
797 | 2019-03-06 13:16 | 1550 | 0.46642
798 | 2019-03-06 13:17 | 1550 | 0.49123
799 | 2019-03-06 13:18 | 1550 | 0.57559
800 | 2019-03-06 13:19 | 1550 | 0.51108
801 | 2019-03-06 13:20 | 1550 | 0.46642
802 | 2019-03-06 13:21 | 1550 | 0.52597
803 | 2019-03-06 13:22 | 1550 | 0.46146
804 | 2019-03-06 13:23 | 1550 | 0.45154
805 | 2019-03-06 13:24 | 1550 | 0.44161
806 | 2019-03-06 13:25 | 1550 | 0.48131
807 | 2019-03-06 13:26 | 1550 | 0.64009
808 | 2019-03-06 13:27 | 1550 | 0.58055
809 | 2019-03-06 13:28 | 1550 | 0.49123
810 | 2019-03-06 13:29 | 1550 | 0.52101
811 | 2019-03-06 13:30 | 1550 | 0.53589
812 | 2019-03-06 13:31 | 1550 | 0.4565
813 | 2019-03-06 13:32 | 1550 | 0.4168
814 | 2019-03-06 13:33 | 1550 | 0.35726
815 | 2019-03-06 13:34 | 1550 | 0.29276
816 | 2019-03-06 13:35 | 1550 | 0.26795
817 | 2019-03-06 13:36 | 1550 | 0.2481
818 | 2019-03-06 13:37 | 1550 | 0.22825
819 | 2019-03-06 13:38 | 1550 | 0.22825
820 | 2019-03-06 13:39 | 1550 | 0.22825
821 | 2019-03-06 13:40 | 1550 | 0.23321
822 | 2019-03-06 13:41 | 1550 | 0.22825
823 | 2019-03-06 13:42 | 1550 | 0.22825
824 | 2019-03-06 13:43 | 1550 | 0.22825
825 | 2019-03-06 13:44 | 1550 | 0.22329
826 | 2019-03-06 13:45 | 1550 | 0.22329
827 | 2019-03-06 13:46 | 1550 | 0.21833
828 | 2019-03-06 13:47 | 1550 | 0.22825
829 | 2019-03-06 13:48 | 1550 | 0.22825
830 | 2019-03-06 13:49 | 1550 | 0.24314
831 | 2019-03-06 13:50 | 1550 | 0.2481
832 | 2019-03-06 13:51 | 1550 | 0.25802
833 | 2019-03-06 13:52 | 1550 | 0.27291
834 | 2019-03-06 13:53 | 1550 | 0.29276
835 | 2019-03-06 13:54 | 1550 | 0.29276
836 | 2019-03-06 13:55 | 1550 | 0.29772
837 | 2019-03-06 13:56 | 1550 | 0.30268
838 | 2019-03-06 13:57 | 1550 | 0.32253
839 | 2019-03-06 13:58 | 1550 | 0.36718
840 | 2019-03-06 13:59 | 1550 | 0.36222
841 | 2019-03-06 14:00 | 1550 | 0.34734
842 | 2019-03-06 14:01 | 1551 | 0.32749
843 | 2019-03-06 14:02 | 1551 | 0.33245
844 | 2019-03-06 14:03 | 1551 | 0.32749
845 | 2019-03-06 14:04 | 1551 | 0.29276
846 | 2019-03-06 14:05 | 1551 | 0.28283
847 | 2019-03-06 14:06 | 1551 | 0.25306
848 | 2019-03-06 14:07 | 1551 | 0.23817
849 | 2019-03-06 14:08 | 1551 | 0.22825
850 | 2019-03-06 14:09 | 1551 | 0.22329
851 | 2019-03-06 14:10 | 1551 | 0.21833
852 | 2019-03-06 14:11 | 1551 | 0.21336
853 | 2019-03-06 14:12 | 1551 | 0.2084
854 | 2019-03-06 14:13 | 1551 | 0.20344
855 | 2019-03-06 14:14 | 1551 | 0.20344
856 | 2019-03-06 14:15 | 1551 | 0.19848
857 | 2019-03-06 14:16 | 1551 | 0.19848
858 | 2019-03-06 14:17 | 1551 | 0.20344
859 | 2019-03-06 14:18 | 1551 | 0.19848
860 | 2019-03-06 14:19 | 1551 | 0.20344
861 | 2019-03-06 14:20 | 1551 | 0.2084
862 | 2019-03-06 14:21 | 1551 | 0.22329
863 | 2019-03-06 14:22 | 1551 | 0.22825
864 | 2019-03-06 14:23 | 1551 | 0.23321
865 | 2019-03-06 14:24 | 1551 | 0.25306
866 | 2019-03-06 14:25 | 1551 | 0.24314
867 | 2019-03-06 14:26 | 1551 | 0.23817
868 | 2019-03-06 14:27 | 1551 | 0.23321
869 | 2019-03-06 14:28 | 1551 | 0.22825
870 | 2019-03-06 14:29 | 1551 | 0.22825
871 | 2019-03-06 14:30 | 1551 | 0.22329
872 | 2019-03-06 14:31 | 1551 | 0.22329
873 | 2019-03-06 14:32 | 1551 | 0.22329
874 | 2019-03-06 14:33 | 1551 | 0.21833
875 | 2019-03-06 14:34 | 1551 | 0.22329
876 | 2019-03-06 14:35 | 1551 | 0.22329
877 | 2019-03-06 14:36 | 1551 | 0.22329
878 | 2019-03-06 14:37 | 1551 | 0.22825
879 | 2019-03-06 14:38 | 1551 | 0.23321
880 | 2019-03-06 14:39 | 1551 | 0.24314
881 | 2019-03-06 14:40 | 1551 | 0.23817
882 | 2019-03-06 14:41 | 1551 | 0.23321
883 | 2019-03-06 14:42 | 1551 | 0.22329
884 | 2019-03-06 14:43 | 1551 | 0.21833
885 | 2019-03-06 14:44 | 1551 | 0.21336
886 | 2019-03-06 14:45 | 1551 | 0.21833
887 | 2019-03-06 14:46 | 1551 | 0.21336
888 | 2019-03-06 14:47 | 1551 | 0.21833
889 | 2019-03-06 14:48 | 1551 | 0.22329
890 | 2019-03-06 14:49 | 1551 | 0.23321
891 | 2019-03-06 14:50 | 1551 | 0.24314
892 | 2019-03-06 14:51 | 1551 | 0.25306
893 | 2019-03-06 14:52 | 1551 | 0.24314
894 | 2019-03-06 14:53 | 1551 | 0.2481
895 | 2019-03-06 14:54 | 1551 | 0.25802
896 | 2019-03-06 14:55 | 1551 | 0.26795
897 | 2019-03-06 14:56 | 1551 | 0.26298
898 | 2019-03-06 14:57 | 1551 | 0.23817
899 | 2019-03-06 14:58 | 1551 | 0.22329
900 | 2019-03-06 14:59 | 1551 | 0.2084
901 | 2019-03-06 15:00 | 1552 | 0.19848
902 | 2019-03-06 15:01 | 1552 | 0.19352
903 | 2019-03-06 15:02 | 1552 | 0.18855
904 | 2019-03-06 15:03 | 1552 | 0.18359
905 | 2019-03-06 15:04 | 1552 | 0.18359
906 | 2019-03-06 15:05 | 1552 | 0.17367
907 | 2019-03-06 15:06 | 1552 | 0.17367
908 | 2019-03-06 15:07 | 1552 | 0.17367
909 | 2019-03-06 15:08 | 1552 | 0.18359
910 | 2019-03-06 15:09 | 1552 | 0.2084
911 | 2019-03-06 15:10 | 1552 | 0.29772
912 | 2019-03-06 15:11 | 1552 | 0.30268
913 | 2019-03-06 15:12 | 1552 | 0.27787
914 | 2019-03-06 15:13 | 1552 | 0.3126
915 | 2019-03-06 15:14 | 1552 | 0.27787
916 | 2019-03-06 15:15 | 1552 | 0.25802
917 | 2019-03-06 15:16 | 1552 | 0.2481
918 | 2019-03-06 15:17 | 1552 | 0.23321
919 | 2019-03-06 15:18 | 1552 | 0.23321
920 | 2019-03-06 15:19 | 1552 | 0.22329
921 | 2019-03-06 15:20 | 1552 | 0.21833
922 | 2019-03-06 15:21 | 1552 | 0.21833
923 | 2019-03-06 15:22 | 1552 | 0.21336
924 | 2019-03-06 15:23 | 1552 | 0.2084
925 | 2019-03-06 15:24 | 1552 | 0.2084
926 | 2019-03-06 15:25 | 1552 | 0.2084
927 | 2019-03-06 15:26 | 1552 | 0.2084
928 | 2019-03-06 15:27 | 1552 | 0.21336
929 | 2019-03-06 15:28 | 1552 | 0.21336
930 | 2019-03-06 15:29 | 1552 | 0.2084
931 | 2019-03-06 15:30 | 1552 | 0.21833
932 | 2019-03-06 15:31 | 1552 | 0.22825
933 | 2019-03-06 15:32 | 1552 | 0.26298
934 | 2019-03-06 15:33 | 1552 | 0.30268
935 | 2019-03-06 15:34 | 1552 | 0.36718
936 | 2019-03-06 15:35 | 1552 | 0.30764
937 | 2019-03-06 15:36 | 1552 | 0.30268
938 | 2019-03-06 15:37 | 1552 | 0.29276
939 | 2019-03-06 15:38 | 1552 | 0.28779
940 | 2019-03-06 15:39 | 1552 | 0.28283
941 | 2019-03-06 15:40 | 1552 | 0.27291
942 | 2019-03-06 15:41 | 1552 | 0.29276
943 | 2019-03-06 15:42 | 1552 | 0.3126
944 | 2019-03-06 15:43 | 1552 | 0.39696
945 | 2019-03-06 15:44 | 1552 | 0.36718
946 | 2019-03-06 15:45 | 1552 | 0.25306
947 | 2019-03-06 15:46 | 1552 | 0.22825
948 | 2019-03-06 15:47 | 1552 | 0.21336
949 | 2019-03-06 15:48 | 1552 | 0.2084
950 | 2019-03-06 15:49 | 1552 | 0.21336
951 | 2019-03-06 15:50 | 1552 | 0.22329
952 | 2019-03-06 15:51 | 1552 | 0.23817
953 | 2019-03-06 15:52 | 1552 | 0.23321
954 | 2019-03-06 15:53 | 1552 | 0.2481
955 | 2019-03-06 15:54 | 1552 | 0.26795
956 | 2019-03-06 15:55 | 1552 | 0.25802
957 | 2019-03-06 15:56 | 1552 | 0.28779
958 | 2019-03-06 15:57 | 1552 | 0.23321
959 | 2019-03-06 15:58 | 1552 | 0.22329
960 | 2019-03-06 15:59 | 1552 | 0.21336
961 | 2019-03-06 16:00 | 1553 | 0.20344
962 | 2019-03-06 16:01 | 1553 | 0.19352
963 | 2019-03-06 16:02 | 1553 | 0.17367
964 | 2019-03-06 16:03 | 1553 | 0.15878
965 | 2019-03-06 16:04 | 1553 | 0.13397
966 | 2019-03-06 16:05 | 1553 | 0.12405
967 | 2019-03-06 16:06 | 1553 | 0.11413
968 | 2019-03-06 16:07 | 1553 | 0.10916
969 | 2019-03-06 16:08 | 1553 | 0.1042
970 | 2019-03-06 16:09 | 1553 | 0.1042
971 | 2019-03-06 16:10 | 1553 | 0.099239
972 | 2019-03-06 16:11 | 1553 | 0.094277
973 | 2019-03-06 16:12 | 1553 | 0.089315
974 | 2019-03-06 16:13 | 1553 | 0.089315
975 | 2019-03-06 16:14 | 1553 | 0.094277
976 | 2019-03-06 16:15 | 1553 | 0.084353
977 | 2019-03-06 16:16 | 1553 | 0.074429
978 | 2019-03-06 16:17 | 1553 | 0.074429
979 | 2019-03-06 16:18 | 1553 | 0.069467
980 | 2019-03-06 16:19 | 1553 | 0.069467
981 | 2019-03-06 16:20 | 1553 | 0.069467
982 | 2019-03-06 16:21 | 1553 | 0.074429
983 | 2019-03-06 16:22 | 1553 | 0.069467
984 | 2019-03-06 16:23 | 1553 | 0.069467
985 | 2019-03-06 16:24 | 1553 | 0.059543
986 | 2019-03-06 16:25 | 1553 | 0.054582
987 | 2019-03-06 16:26 | 1553 | 0.044658
988 | 2019-03-06 16:27 | 1553 | 0.044658
989 | 2019-03-06 16:28 | 1553 | 0.039696
990 | 2019-03-06 16:29 | 1553 | 0.039696
991 | 2019-03-06 16:30 | 1553 | 0.039696
992 | 2019-03-06 16:31 | 1553 | 0.044658
993 | 2019-03-06 16:32 | 1553 | 0.039696
994 | 2019-03-06 16:33 | 1553 | 0.044658
995 | 2019-03-06 16:34 | 1553 | 0.044658
996 | 2019-03-06 16:35 | 1553 | 0.04962
997 | 2019-03-06 16:36 | 1553 | 0.044658
998 | 2019-03-06 16:37 | 1553 | 0.039696
999 | 2019-03-06 16:38 | 1553 | 0.029772
1000 | 2019-03-06 16:39 | 1553 | 0.02481
1001 | 2019-03-06 16:40 | 1553 | 0.02481
1002 | 2019-03-06 16:41 | 1553 | 0.02481
1003 | 2019-03-06 16:42 | 1553 | 0.019848
1004 | 2019-03-06 16:43 | 1553 | 0.019848
1005 | 2019-03-06 16:44 | 1553 | 0.02481
1006 | 2019-03-06 16:45 | 1553 | 0.019848
1007 | 2019-03-06 16:46 | 1553 | 0.019848
1008 | 2019-03-06 16:47 | 1553 | 0.02481
1009 | 2019-03-06 16:48 | 1553 | 0.019848
1010 | 2019-03-06 16:49 | 1553 | 0.019848
1011 | 2019-03-06 16:50 | 1553 | 0.02481
1012 | 2019-03-06 16:51 | 1553 | 0.02481
1013 | 2019-03-06 16:52 | 1553 | 0.019848
1014 | 2019-03-06 16:53 | 1553 | 0.019848
1015 | 2019-03-06 16:54 | 1553 | 0.014886
1016 | 2019-03-06 16:55 | 1553 | 0.014886
1017 | 2019-03-06 16:56 | 1553 | 0.019848
1018 | 2019-03-06 16:57 | 1553 | 0.014886
1019 | 2019-03-06 16:58 | 1553 | 0.019848
1020 | 2019-03-06 16:59 | 1553 | 0.019848
1021 | 2019-03-06 17:00 | 1553 | 0.019848
1022 | 2019-03-06 17:01 | 1554 | 0.014886
1023 | 2019-03-06 17:02 | 1554 | 0.014886
1024 | 2019-03-06 17:03 | 1554 | 0.019848
1025 | 2019-03-06 17:04 | 1554 | 0.0099239
1026 | 2019-03-06 17:05 | 1554 | 0.014886
1027 | 2019-03-06 17:06 | 1554 | 0.014886
1028 | 2019-03-06 17:07 | 1554 | 0.0099239
1029 | 2019-03-06 17:08 | 1554 | 0.0099239
1030 | 2019-03-06 17:09 | 1554 | 0.0099239
1031 | 2019-03-06 17:10 | 1554 | 0.0099239
1032 | 2019-03-06 17:11 | 1554 | 0.014886
1033 | 2019-03-06 17:12 | 1554 | 0.0099239
1034 | 2019-03-06 17:13 | 1554 | 0.0099239
1035 | 2019-03-06 17:14 | 1554 | 0.014886
1036 | 2019-03-06 17:15 | 1554 | 0.0099239
1037 | 2019-03-06 17:16 | 1554 | 0.0099239
1038 | 2019-03-06 17:17 | 1554 | 0.0099239
1039 | 2019-03-06 17:18 | 1554 | 0.0099239
1040 | 2019-03-06 17:19 | 1554 | 0.004962
1041 | 2019-03-06 17:20 | 1554 | 0.004962
1042 | 2019-03-06 17:21 | 1554 | 0.0099239
1043 | 2019-03-06 17:22 | 1554 | 0.004962
1044 | 2019-03-06 17:23 | 1554 | 0
1045 | 2019-03-06 17:24 | 1554 | 0.004962
1046 | 2019-03-06 17:25 | 1554 | 0.004962
1047 | 2019-03-06 17:26 | 1554 | 0.004962
1048 | 2019-03-06 17:27 | 1554 | 0.004962
1049 | 2019-03-06 17:28 | 1554 | 0
1050 | 2019-03-06 17:29 | 1554 | 0.004962
1051 | 2019-03-06 17:30 | 1554 | 0.004962
1052 | 2019-03-06 17:31 | 1554 | 0
1053 | 2019-03-06 17:32 | 1554 | 0.004962
1054 | 2019-03-06 17:33 | 1554 | 0
1055 | 2019-03-06 17:34 | 1554 | 0.004962
1056 | 2019-03-06 17:35 | 1554 | 0
1057 | 2019-03-06 17:36 | 1554 | 0
1058 | 2019-03-06 17:37 | 1554 | 0.004962
1059 | 2019-03-06 17:38 | 1554 | 0
1060 | 2019-03-06 17:39 | 1554 | 0.004962
1061 | 2019-03-06 17:40 | 1554 | 0
1062 | 2019-03-06 17:41 | 1554 | 0
1063 | 2019-03-06 17:42 | 1554 | 0
1064 | 2019-03-06 17:43 | 1554 | 0
1065 | 2019-03-06 17:44 | 1554 | 0
1066 | 2019-03-06 17:45 | 1554 | 0
1067 | 2019-03-06 17:46 | 1554 | 0
1068 | 2019-03-06 17:47 | 1554 | 0
1069 | 2019-03-06 17:48 | 1554 | 0
1070 | 2019-03-06 17:49 | 1554 | 0
1071 | 2019-03-06 17:50 | 1554 | 0
1072 | 2019-03-06 17:51 | 1554 | 0
1073 | 2019-03-06 17:52 | 1554 | 0
1074 | 2019-03-06 17:53 | 1554 | 0
1075 | 2019-03-06 17:54 | 1554 | 0
1076 | 2019-03-06 17:55 | 1554 | 0
1077 | 2019-03-06 17:56 | 1554 | 0
1078 | 2019-03-06 17:57 | 1554 | 0
1079 | 2019-03-06 17:58 | 1554 | 0
1080 | 2019-03-06 17:59 | 1554 | 0
1081 | 2019-03-06 18:00 | 1555 | 0
1082 | 2019-03-06 18:01 | 1555 | 0
1083 | 2019-03-06 18:02 | 1555 | 0
1084 | 2019-03-06 18:03 | 1555 | 0
1085 | 2019-03-06 18:04 | 1555 | 0
1086 | 2019-03-06 18:05 | 1555 | 0
1087 | 2019-03-06 18:06 | 1555 | 0
1088 | 2019-03-06 18:07 | 1555 | 0
1089 | 2019-03-06 18:08 | 1555 | 0
1090 | 2019-03-06 18:09 | 1555 | 0
1091 | 2019-03-06 18:10 | 1555 | 0
1092 | 2019-03-06 18:11 | 1555 | 0
1093 | 2019-03-06 18:12 | 1555 | 0
1094 | 2019-03-06 18:13 | 1555 | 0
1095 | 2019-03-06 18:14 | 1555 | 0
1096 | 2019-03-06 18:15 | 1555 | 0
1097 | 2019-03-06 18:16 | 1555 | 0
1098 | 2019-03-06 18:17 | 1555 | 0
1099 | 2019-03-06 18:18 | 1555 | 0
1100 | 2019-03-06 18:19 | 1555 | 0
1101 | 2019-03-06 18:20 | 1555 | 0
1102 | 2019-03-06 18:21 | 1555 | 0
1103 | 2019-03-06 18:22 | 1555 | 0
1104 | 2019-03-06 18:23 | 1555 | 0
1105 | 2019-03-06 18:24 | 1555 | 0
1106 | 2019-03-06 18:25 | 1555 | 0
1107 | 2019-03-06 18:26 | 1555 | 0
1108 | 2019-03-06 18:27 | 1555 | 0
1109 | 2019-03-06 18:28 | 1555 | 0
1110 | 2019-03-06 18:29 | 1555 | 0
1111 | 2019-03-06 18:30 | 1555 | 0
1112 | 2019-03-06 18:31 | 1555 | 0
1113 | 2019-03-06 18:32 | 1555 | 0
1114 | 2019-03-06 18:33 | 1555 | 0
1115 | 2019-03-06 18:34 | 1555 | 0
1116 | 2019-03-06 18:35 | 1555 | 0
1117 | 2019-03-06 18:36 | 1555 | 0
1118 | 2019-03-06 18:37 | 1555 | 0
1119 | 2019-03-06 18:38 | 1555 | 0
1120 | 2019-03-06 18:39 | 1555 | 0
1121 | 2019-03-06 18:40 | 1555 | 0
1122 | 2019-03-06 18:41 | 1555 | 0
1123 | 2019-03-06 18:42 | 1555 | 0
1124 | 2019-03-06 18:43 | 1555 | 0
1125 | 2019-03-06 18:44 | 1555 | 0
1126 | 2019-03-06 18:45 | 1555 | 0
1127 | 2019-03-06 18:46 | 1555 | 0
1128 | 2019-03-06 18:47 | 1555 | 0
1129 | 2019-03-06 18:48 | 1555 | 0
1130 | 2019-03-06 18:49 | 1555 | 0
1131 | 2019-03-06 18:50 | 1555 | 0
1132 | 2019-03-06 18:51 | 1555 | 0
1133 | 2019-03-06 18:52 | 1555 | 0
1134 | 2019-03-06 18:53 | 1555 | 0
1135 | 2019-03-06 18:54 | 1555 | 0
1136 | 2019-03-06 18:55 | 1555 | 0
1137 | 2019-03-06 18:56 | 1555 | 0
1138 | 2019-03-06 18:57 | 1555 | 0
1139 | 2019-03-06 18:58 | 1555 | 0
1140 | 2019-03-06 18:59 | 1555 | 0
1141 | 2019-03-06 19:00 | 1556 | 0
1142 | 2019-03-06 19:01 | 1556 | 0
1143 | 2019-03-06 19:02 | 1556 | 0
1144 | 2019-03-06 19:03 | 1556 | 0
1145 | 2019-03-06 19:04 | 1556 | 0
1146 | 2019-03-06 19:05 | 1556 | 0
1147 | 2019-03-06 19:06 | 1556 | 0
1148 | 2019-03-06 19:07 | 1556 | 0
1149 | 2019-03-06 19:08 | 1556 | 0
1150 | 2019-03-06 19:09 | 1556 | 0
1151 | 2019-03-06 19:10 | 1556 | 0
1152 | 2019-03-06 19:11 | 1556 | 0
1153 | 2019-03-06 19:12 | 1556 | 0
1154 | 2019-03-06 19:13 | 1556 | 0
1155 | 2019-03-06 19:14 | 1556 | 0
1156 | 2019-03-06 19:15 | 1556 | 0
1157 | 2019-03-06 19:16 | 1556 | 0
1158 | 2019-03-06 19:17 | 1556 | 0
1159 | 2019-03-06 19:18 | 1556 | 0
1160 | 2019-03-06 19:19 | 1556 | 0
1161 | 2019-03-06 19:20 | 1556 | 0
1162 | 2019-03-06 19:21 | 1556 | 0
1163 | 2019-03-06 19:22 | 1556 | 0
1164 | 2019-03-06 19:23 | 1556 | 0
1165 | 2019-03-06 19:24 | 1556 | 0
1166 | 2019-03-06 19:25 | 1556 | 0
1167 | 2019-03-06 19:26 | 1556 | 0
1168 | 2019-03-06 19:27 | 1556 | 0
1169 | 2019-03-06 19:28 | 1556 | 0
1170 | 2019-03-06 19:29 | 1556 | 0
1171 | 2019-03-06 19:30 | 1556 | 0
1172 | 2019-03-06 19:31 | 1556 | 0
1173 | 2019-03-06 19:32 | 1556 | 0
1174 | 2019-03-06 19:33 | 1556 | 0
1175 | 2019-03-06 19:34 | 1556 | 0
1176 | 2019-03-06 19:35 | 1556 | 0
1177 | 2019-03-06 19:36 | 1556 | 0
1178 | 2019-03-06 19:37 | 1556 | 0
1179 | 2019-03-06 19:38 | 1556 | 0
1180 | 2019-03-06 19:39 | 1556 | 0
1181 | 2019-03-06 19:40 | 1556 | 0
1182 | 2019-03-06 19:41 | 1556 | 0
1183 | 2019-03-06 19:42 | 1556 | 0
1184 | 2019-03-06 19:43 | 1556 | 0
1185 | 2019-03-06 19:44 | 1556 | 0
1186 | 2019-03-06 19:45 | 1556 | 0
1187 | 2019-03-06 19:46 | 1556 | 0
1188 | 2019-03-06 19:47 | 1556 | 0
1189 | 2019-03-06 19:48 | 1556 | 0
1190 | 2019-03-06 19:49 | 1556 | 0
1191 | 2019-03-06 19:50 | 1556 | 0
1192 | 2019-03-06 19:51 | 1556 | 0
1193 | 2019-03-06 19:52 | 1556 | 0
1194 | 2019-03-06 19:53 | 1556 | 0
1195 | 2019-03-06 19:54 | 1556 | 0
1196 | 2019-03-06 19:55 | 1556 | 0
1197 | 2019-03-06 19:56 | 1556 | 0
1198 | 2019-03-06 19:57 | 1556 | 0
1199 | 2019-03-06 19:58 | 1556 | 0
1200 | 2019-03-06 19:59 | 1556 | 0
1201 | 2019-03-06 20:00 | 1556 | 0
1202 | 2019-03-06 20:01 | 1557 | 0
1203 | 2019-03-06 20:02 | 1557 | 0
1204 | 2019-03-06 20:03 | 1557 | 0
1205 | 2019-03-06 20:04 | 1557 | 0
1206 | 2019-03-06 20:05 | 1557 | 0
1207 | 2019-03-06 20:06 | 1557 | 0
1208 | 2019-03-06 20:07 | 1557 | 0
1209 | 2019-03-06 20:08 | 1557 | 0
1210 | 2019-03-06 20:09 | 1557 | 0
1211 | 2019-03-06 20:10 | 1557 | 0
1212 | 2019-03-06 20:11 | 1557 | 0
1213 | 2019-03-06 20:12 | 1557 | 0
1214 | 2019-03-06 20:13 | 1557 | 0
1215 | 2019-03-06 20:14 | 1557 | 0
1216 | 2019-03-06 20:15 | 1557 | 0
1217 | 2019-03-06 20:16 | 1557 | 0
1218 | 2019-03-06 20:17 | 1557 | 0
1219 | 2019-03-06 20:18 | 1557 | 0
1220 | 2019-03-06 20:19 | 1557 | 0
1221 | 2019-03-06 20:20 | 1557 | 0
1222 | 2019-03-06 20:21 | 1557 | 0
1223 | 2019-03-06 20:22 | 1557 | 0
1224 | 2019-03-06 20:23 | 1557 | 0
1225 | 2019-03-06 20:24 | 1557 | 0
1226 | 2019-03-06 20:25 | 1557 | 0
1227 | 2019-03-06 20:26 | 1557 | 0
1228 | 2019-03-06 20:27 | 1557 | 0
1229 | 2019-03-06 20:28 | 1557 | 0
1230 | 2019-03-06 20:29 | 1557 | 0
1231 | 2019-03-06 20:30 | 1557 | 0
1232 | 2019-03-06 20:31 | 1557 | 0
1233 | 2019-03-06 20:32 | 1557 | 0
1234 | 2019-03-06 20:33 | 1557 | 0
1235 | 2019-03-06 20:34 | 1557 | 0
1236 | 2019-03-06 20:35 | 1557 | 0
1237 | 2019-03-06 20:36 | 1557 | 0
1238 | 2019-03-06 20:37 | 1557 | 0
1239 | 2019-03-06 20:38 | 1557 | 0
1240 | 2019-03-06 20:39 | 1557 | 0
1241 | 2019-03-06 20:40 | 1557 | 0
1242 | 2019-03-06 20:41 | 1557 | 0
1243 | 2019-03-06 20:42 | 1557 | 0
1244 | 2019-03-06 20:43 | 1557 | 0
1245 | 2019-03-06 20:44 | 1557 | 0
1246 | 2019-03-06 20:45 | 1557 | 0
1247 | 2019-03-06 20:46 | 1557 | 0
1248 | 2019-03-06 20:47 | 1557 | 0
1249 | 2019-03-06 20:48 | 1557 | 0
1250 | 2019-03-06 20:49 | 1557 | 0
1251 | 2019-03-06 20:50 | 1557 | 0
1252 | 2019-03-06 20:51 | 1557 | 0
1253 | 2019-03-06 20:52 | 1557 | 0
1254 | 2019-03-06 20:53 | 1557 | 0
1255 | 2019-03-06 20:54 | 1557 | 0
1256 | 2019-03-06 20:55 | 1557 | 0
1257 | 2019-03-06 20:56 | 1557 | 0
1258 | 2019-03-06 20:57 | 1557 | 0
1259 | 2019-03-06 20:58 | 1557 | 0
1260 | 2019-03-06 20:59 | 1557 | 0
1261 | 2019-03-06 21:00 | 1558 | 0
1262 | 2019-03-06 21:01 | 1558 | 0
1263 | 2019-03-06 21:02 | 1558 | 0
1264 | 2019-03-06 21:03 | 1558 | 0
1265 | 2019-03-06 21:04 | 1558 | 0
1266 | 2019-03-06 21:05 | 1558 | 0
1267 | 2019-03-06 21:06 | 1558 | 0
1268 | 2019-03-06 21:07 | 1558 | 0
1269 | 2019-03-06 21:08 | 1558 | 0
1270 | 2019-03-06 21:09 | 1558 | 0
1271 | 2019-03-06 21:10 | 1558 | 0
1272 | 2019-03-06 21:11 | 1558 | 0
1273 | 2019-03-06 21:12 | 1558 | 0
1274 | 2019-03-06 21:13 | 1558 | 0
1275 | 2019-03-06 21:14 | 1558 | 0
1276 | 2019-03-06 21:15 | 1558 | 0
1277 | 2019-03-06 21:16 | 1558 | 0
1278 | 2019-03-06 21:17 | 1558 | 0
1279 | 2019-03-06 21:18 | 1558 | 0
1280 | 2019-03-06 21:19 | 1558 | 0
1281 | 2019-03-06 21:20 | 1558 | 0
1282 | 2019-03-06 21:21 | 1558 | 0
1283 | 2019-03-06 21:22 | 1558 | 0
1284 | 2019-03-06 21:23 | 1558 | 0
1285 | 2019-03-06 21:24 | 1558 | 0
1286 | 2019-03-06 21:25 | 1558 | 0
1287 | 2019-03-06 21:26 | 1558 | 0
1288 | 2019-03-06 21:27 | 1558 | 0
1289 | 2019-03-06 21:28 | 1558 | 0
1290 | 2019-03-06 21:29 | 1558 | 0
1291 | 2019-03-06 21:30 | 1558 | 0
1292 | 2019-03-06 21:31 | 1558 | 0
1293 | 2019-03-06 21:32 | 1558 | 0
1294 | 2019-03-06 21:33 | 1558 | 0
1295 | 2019-03-06 21:34 | 1558 | 0
1296 | 2019-03-06 21:35 | 1558 | 0
1297 | 2019-03-06 21:36 | 1558 | 0
1298 | 2019-03-06 21:37 | 1558 | 0
1299 | 2019-03-06 21:38 | 1558 | 0
1300 | 2019-03-06 21:39 | 1558 | 0
1301 | 2019-03-06 21:40 | 1558 | 0
1302 | 2019-03-06 21:41 | 1558 | 0
1303 | 2019-03-06 21:42 | 1558 | 0
1304 | 2019-03-06 21:43 | 1558 | 0
1305 | 2019-03-06 21:44 | 1558 | 0
1306 | 2019-03-06 21:45 | 1558 | 0
1307 | 2019-03-06 21:46 | 1558 | 0
1308 | 2019-03-06 21:47 | 1558 | 0
1309 | 2019-03-06 21:48 | 1558 | 0
1310 | 2019-03-06 21:49 | 1558 | 0
1311 | 2019-03-06 21:50 | 1558 | 0
1312 | 2019-03-06 21:51 | 1558 | 0
1313 | 2019-03-06 21:52 | 1558 | 0
1314 | 2019-03-06 21:53 | 1558 | 0
1315 | 2019-03-06 21:54 | 1558 | 0
1316 | 2019-03-06 21:55 | 1558 | 0
1317 | 2019-03-06 21:56 | 1558 | 0
1318 | 2019-03-06 21:57 | 1558 | 0
1319 | 2019-03-06 21:58 | 1558 | 0
1320 | 2019-03-06 21:59 | 1558 | 0
1321 | 2019-03-06 22:00 | 1559 | 0
1322 | 2019-03-06 22:01 | 1559 | 0
1323 | 2019-03-06 22:02 | 1559 | 0
1324 | 2019-03-06 22:03 | 1559 | 0
1325 | 2019-03-06 22:04 | 1559 | 0
1326 | 2019-03-06 22:05 | 1559 | 0
1327 | 2019-03-06 22:06 | 1559 | 0
1328 | 2019-03-06 22:07 | 1559 | 0
1329 | 2019-03-06 22:08 | 1559 | 0
1330 | 2019-03-06 22:09 | 1559 | 0
1331 | 2019-03-06 22:10 | 1559 | 0
1332 | 2019-03-06 22:11 | 1559 | 0
1333 | 2019-03-06 22:12 | 1559 | 0
1334 | 2019-03-06 22:13 | 1559 | 0
1335 | 2019-03-06 22:14 | 1559 | 0
1336 | 2019-03-06 22:15 | 1559 | 0
1337 | 2019-03-06 22:16 | 1559 | 0
1338 | 2019-03-06 22:17 | 1559 | 0
1339 | 2019-03-06 22:18 | 1559 | 0
1340 | 2019-03-06 22:19 | 1559 | 0
1341 | 2019-03-06 22:20 | 1559 | 0
1342 | 2019-03-06 22:21 | 1559 | 0
1343 | 2019-03-06 22:22 | 1559 | 0
1344 | 2019-03-06 22:23 | 1559 | 0
1345 | 2019-03-06 22:24 | 1559 | 0
1346 | 2019-03-06 22:25 | 1559 | 0
1347 | 2019-03-06 22:26 | 1559 | 0
1348 | 2019-03-06 22:27 | 1559 | 0
1349 | 2019-03-06 22:28 | 1559 | 0
1350 | 2019-03-06 22:29 | 1559 | 0
1351 | 2019-03-06 22:30 | 1559 | 0
1352 | 2019-03-06 22:31 | 1559 | 0
1353 | 2019-03-06 22:32 | 1559 | 0
1354 | 2019-03-06 22:33 | 1559 | 0
1355 | 2019-03-06 22:34 | 1559 | 0
1356 | 2019-03-06 22:35 | 1559 | 0
1357 | 2019-03-06 22:36 | 1559 | 0
1358 | 2019-03-06 22:37 | 1559 | 0
1359 | 2019-03-06 22:38 | 1559 | 0
1360 | 2019-03-06 22:39 | 1559 | 0
1361 | 2019-03-06 22:40 | 1559 | 0
1362 | 2019-03-06 22:41 | 1559 | 0
1363 | 2019-03-06 22:42 | 1559 | 0
1364 | 2019-03-06 22:43 | 1559 | 0
1365 | 2019-03-06 22:44 | 1559 | 0
1366 | 2019-03-06 22:45 | 1559 | 0
1367 | 2019-03-06 22:46 | 1559 | 0
1368 | 2019-03-06 22:47 | 1559 | 0
1369 | 2019-03-06 22:48 | 1559 | 0
1370 | 2019-03-06 22:49 | 1559 | 0
1371 | 2019-03-06 22:50 | 1559 | 0
1372 | 2019-03-06 22:51 | 1559 | 0
1373 | 2019-03-06 22:52 | 1559 | 0
1374 | 2019-03-06 22:53 | 1559 | 0
1375 | 2019-03-06 22:54 | 1559 | 0
1376 | 2019-03-06 22:55 | 1559 | 0
1377 | 2019-03-06 22:56 | 1559 | 0
1378 | 2019-03-06 22:57 | 1559 | 0
1379 | 2019-03-06 22:58 | 1559 | 0
1380 | 2019-03-06 22:59 | 1559 | 0
1381 | 2019-03-06 23:00 | 1559 | 0
1382 | 2019-03-06 23:01 | 1560 | 0
1383 | 2019-03-06 23:02 | 1560 | 0
1384 | 2019-03-06 23:03 | 1560 | 0
1385 | 2019-03-06 23:04 | 1560 | 0
1386 | 2019-03-06 23:05 | 1560 | 0
1387 | 2019-03-06 23:06 | 1560 | 0
1388 | 2019-03-06 23:07 | 1560 | 0
1389 | 2019-03-06 23:08 | 1560 | 0
1390 | 2019-03-06 23:09 | 1560 | 0
1391 | 2019-03-06 23:10 | 1560 | 0
1392 | 2019-03-06 23:11 | 1560 | 0
1393 | 2019-03-06 23:12 | 1560 | 0
1394 | 2019-03-06 23:13 | 1560 | 0
1395 | 2019-03-06 23:14 | 1560 | 0
1396 | 2019-03-06 23:15 | 1560 | 0
1397 | 2019-03-06 23:16 | 1560 | 0
1398 | 2019-03-06 23:17 | 1560 | 0
1399 | 2019-03-06 23:18 | 1560 | 0
1400 | 2019-03-06 23:19 | 1560 | 0
1401 | 2019-03-06 23:20 | 1560 | 0
1402 | 2019-03-06 23:21 | 1560 | 0
1403 | 2019-03-06 23:22 | 1560 | 0
1404 | 2019-03-06 23:23 | 1560 | 0
1405 | 2019-03-06 23:24 | 1560 | 0
1406 | 2019-03-06 23:25 | 1560 | 0
1407 | 2019-03-06 23:26 | 1560 | 0
1408 | 2019-03-06 23:27 | 1560 | 0
1409 | 2019-03-06 23:28 | 1560 | 0
1410 | 2019-03-06 23:29 | 1560 | 0
1411 | 2019-03-06 23:30 | 1560 | 0
1412 | 2019-03-06 23:31 | 1560 | 0
1413 | 2019-03-06 23:32 | 1560 | 0
1414 | 2019-03-06 23:33 | 1560 | 0
1415 | 2019-03-06 23:34 | 1560 | 0
1416 | 2019-03-06 23:35 | 1560 | 0
1417 | 2019-03-06 23:36 | 1560 | 0
1418 | 2019-03-06 23:37 | 1560 | 0
1419 | 2019-03-06 23:38 | 1560 | 0
1420 | 2019-03-06 23:39 | 1560 | 0
1421 | 2019-03-06 23:40 | 1560 | 0
1422 | 2019-03-06 23:41 | 1560 | 0
1423 | 2019-03-06 23:42 | 1560 | 0
1424 | 2019-03-06 23:43 | 1560 | 0
1425 | 2019-03-06 23:44 | 1560 | 0
1426 | 2019-03-06 23:45 | 1560 | 0
1427 | 2019-03-06 23:46 | 1560 | 0
1428 | 2019-03-06 23:47 | 1560 | 0
1429 | 2019-03-06 23:48 | 1560 | 0
1430 | 2019-03-06 23:49 | 1560 | 0
1431 | 2019-03-06 23:50 | 1560 | 0
1432 | 2019-03-06 23:51 | 1560 | 0
1433 | 2019-03-06 23:52 | 1560 | 0
1434 | 2019-03-06 23:53 | 1560 | 0
1435 | 2019-03-06 23:54 | 1560 | 0
1436 | 2019-03-06 23:55 | 1560 | 0
1437 | 2019-03-06 23:56 | 1560 | 0
1438 | 2019-03-06 23:57 | 1560 | 0
1439 | 2019-03-06 23:58 | 1560 | 0
1440 | 2019-03-06 23:59 | 1560 | 0